## Contents
Residential microgrid EMS: results workbook
Generated 2026-10-14 08:40 from results/*.csv
Sheet | Content | Source CSV
P1 Controllers | Part 1: rule-based vs MILP controller, 24 h at 1.5 min, scenarios S1-S4 | part1_controller_comparison.csv
P3 Forecast metrics | Part 3: day-ahead forecast accuracy on the test period (1 Oct - 31 Dec 2021) | part3_forecast_metrics.csv
P3 MPC | Part 3: realised cost of the forecast-driven MPC vs a perfect-forecast plan | part3_mpc_summary.csv
P4 Siting | Part 4: 60 kWp PV plant at three connection points on the LV feeder, after grid coupling | part4_siting.csv
P4 Coupling iterations | Part 4: optimisation and load-flow iterations until the schedule is network-feasible | part4_coupling_iterations.csv
P5 Test summary | Part 5: closed-loop tests of a battery site controller, checks passed per controller version | part5_test_summary.csv
P5 Test results | Part 5: every check per site, scenario and controller version | part5_test_results.csv
P3 Forecast series | Part 3: measured values and day-ahead forecasts, 15-min, test period | part3_forecasts_test.csv

## P1 Controllers
Part 1: rule-based vs MILP controller, 24 h at 1.5 min, scenarios S1-S4
Scenario | Controller | Gen (kWh) | PV used (kWh) | PV curtailed(kWh) | Total demand(kWh) | True cost (€) | Virtual cost (€) | EV SOC dep (%) | BSS final (%)
S1 | RB | 0 | 26.07 | 0 | 29.83 | 0 | 0.94 | 63.8 | 31
S1 | OPT | 0 | 26.07 | 0 | 29.83 | 0 | 0.94 | 70.6 | 20
S2 | RB | 0 | 29.9 | 22.25 | 24.47 | 0 | -1.36 | 72.4 | 56.5
S2 | OPT | 0 | 29.9 | 22.25 | 24.47 | 0 | -1.36 | 81.1 | 42.4
S3 | RB | 0 | 8.69 | 0 | 16.55 | 0 | 1.96 | 34.7 | 21.7
S3 | OPT | 9.4 | 8.69 | 0 | 16.55 | 2.82 | 4.31 | 50.1 | 20.3
S4 | RB | 0 | 37.96 | 14.19 | 30.95 | 0 | -1.75 | 34.1 | 57.9
S4 | OPT | 0 | 37.96 | 14.19 | 30.95 | 0 | -1.75 | 57.5 | 20

## P3 Forecast metrics
Part 3: day-ahead forecast accuracy on the test period (1 Oct - 31 Dec 2021)
target | model | MAE | RMSE | nMAE_% | MAE_daylight
load | XGBoost | 0.9756 | 1.2679 | 81.2291
load | Persistence | 1.1046 | 1.7412 | 91.9697
load | 7-day profile | 0.972 | 1.3104 | 80.9287
pv | XGBoost | 0.0622 | 0.1185 | 76.8094 | 0.1541
pv | Persistence | 0.0585 | 0.1346 | 72.277 | 0.1465
pv | 7-day profile | 0.0601 | 0.1217 | 74.1887 | 0.1498

## P3 MPC
Part 3: realised cost of the forecast-driven MPC vs a perfect-forecast plan
window | strategy | days | realised_cost_EUR | grid_import_kWh | grid_export_kWh | extra_cost_vs_perfect_%
04 Oct - 17 Oct | perfect | 14 | 174.95 | 440.24 | 38.13 | 0
04 Oct - 17 Oct | xgboost | 14 | 178.09 | 448.49 | 43.43 | 1.8
04 Oct - 17 Oct | persistence | 14 | 194.66 | 493.79 | 95.19 | 11.27
04 Oct - 17 Oct | profile7 | 14 | 192.21 | 485.9 | 71.69 | 9.87
08 Nov - 21 Nov | perfect | 14 | 228.7 | 572.49 | 10.01 | 0
08 Nov - 21 Nov | xgboost | 14 | 239.94 | 602.2 | 31.19 | 4.92
08 Nov - 21 Nov | persistence | 14 | 244.15 | 612.46 | 27.86 | 6.76
08 Nov - 21 Nov | profile7 | 14 | 249.75 | 628.29 | 52.07 | 9.21

## P4 Siting
Part 4: 60 kWp PV plant at three connection points on the LV feeder, after grid coupling
connection_point | bus | short_circuit_mva | max_voltage_before_pu | violating_steps_before | iterations | plant_curtailment_pct | total_curtailed_kwh | total_curtailment_pct | extra_cost_eur | reinforced_max_voltage_pu | reinforced_violating_steps
Next to transformer | 2 | 3.7089 | 1.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0208 | 0
Mid-feeder | 8 | 1.8975 | 1.0592 | 24 | 3 | 0.53177 | 16.6469 | 0.8667 | 0.50408 | 1.0279 | 0
Feeder end | 14 | 1.2049 | 1.0734 | 40 | 4 | 23.8021 | 191.2235 | 9.9558 | 5.7685 | 1.035 | 0

## P4 Coupling iterations
Part 4: optimisation and load-flow iterations until the schedule is network-feasible
case | iteration | violating_steps | max_voltage_pu | min_voltage_pu | max_line_loading_pct | max_trafo_loading_pct | curtailed_kwh | cost_eur
Homes only | 0 | 0 | 1.0391 | 0.99531 | 43.7292 | 51.1253 | 0 | -12.7693
Next to transformer | 0 | 0 | 1.0447 | 0.99531 | 67.6854 | 79.1333 | 0 | -31.9781
Mid-feeder | 0 | 24 | 1.0592 | 0.99531 | 66.4237 | 77.6583 | 0 | -31.9781
Mid-feeder | 1 | 14 | 1.0521 | 0.99473 | 61.246 | 71.6048 | 13.2011 | -31.5821
Mid-feeder | 2 | 2 | 1.051 | 0.99537 | 59.6287 | 69.714 | 16.2721 | -31.4859
Mid-feeder | 3 | 0 | 1.05 | 0.99537 | 59.2773 | 69.3031 | 16.6469 | -31.474
Feeder end | 0 | 40 | 1.0734 | 0.99531 | 65.8207 | 76.9533 | 0 | -31.9781
Feeder end | 1 | 39 | 1.0644 | 0.99502 | 59.1269 | 69.1272 | 78.6308 | -29.6085
Feeder end | 2 | 31 | 1.0563 | 0.99343 | 53.1009 | 62.0821 | 145.4118 | -27.587
Feeder end | 3 | 3 | 1.0523 | 0.99408 | 50.9656 | 59.5856 | 187.7233 | -26.3147
Feeder end | 4 | 0 | 1.0499 | 0.99408 | 49.3203 | 57.6621 | 191.2235 | -26.2097

## P5 Test summary
Part 5: closed-loop tests of a battery site controller, checks passed per controller version
controller | checks | passed | failed
Controller v1 | 36 | 33 | 3
Controller v2 | 36 | 36 | 0
v2 + fault: FCR sign error | 36 | 14 | 22
v2 + fault: filtered FCR (60 s) | 36 | 14 | 22
v2 + fault: connection limit ignored | 36 | 34 | 2

## P5 Test results
Part 5: every check per site, scenario and controller version
site | scenario | controller | check | value | limit | unit | passed
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v1 | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v1 | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v1 | Lowest SOC | 49.805 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v2 | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v2 | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | Controller v2 | Lowest SOC | 49.805 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: FCR sign error | FCR tracking error (RMS) | 20.477 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: FCR sign error | FCR response direction (correlation) | -0.984 | >= 0.9 | - | FALSE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: FCR sign error | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 8.576 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | FCR response direction (correlation) | 0.552 | >= 0.9 | - | FALSE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | Lowest SOC | 49.826 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | Lowest SOC | 49.805 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | Lowest SOC | 40.843 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | Lowest SOC | 40.843 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | FCR sustained within 2% (15 min) | 0 | >= 99 | % of time | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR sustained within 2% (15 min) | 77.516 | >= 99 | % of time | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | Lowest SOC | 41.425 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | Lowest SOC | 40.843 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | FCR sustained within 2% (15 min) | 0 | >= 99 | % of time | FALSE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | Lowest SOC | 40.843 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR sustained within 2% (15 min) | 77.516 | >= 99 | % of time | FALSE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 30 MWh (2 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | Controller v1 | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | Controller v1 | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | Controller v2 | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | Controller v2 | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: FCR sign error | FCR tracking error (RMS) | 122.378 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: FCR sign error | FCR response direction (correlation) | -1 | >= 0.9 | - | FALSE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 20.454 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: filtered FCR (60 s) | FCR response direction (correlation) | 0.891 | >= 0.9 | - | FALSE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Frequency ramp to 49.85 Hz | v2 + fault: connection limit ignored | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | Controller v1 | Lowest SOC | 8.093 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | Controller v2 | Lowest SOC | 9.842 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: FCR sign error | Lowest SOC | 12 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: filtered FCR (60 s) | Lowest SOC | 10.42 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Under-frequency step at low SOC | v2 + fault: connection limit ignored | Lowest SOC | 9.842 | >= 5 | % | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | Controller v1 | FCR tracking error (RMS) | 9.033 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | Controller v1 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | Controller v2 | FCR tracking error (RMS) | 1.873 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | Controller v2 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: FCR sign error | FCR tracking error (RMS) | 21.362 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: FCR sign error | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 8.768 | <= 5 | % of FCR | FALSE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: filtered FCR (60 s) | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 1.873 | <= 5 | % of FCR | TRUE
15 MW / 30 MWh (2 h) | Wind surge at the connection limit | v2 + fault: connection limit ignored | Time above connection limit | 299.6 | <= 1 | s | FALSE
15 MW / 30 MWh (2 h) | Step with 1 s communication delay | Controller v1 | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Step with 1 s communication delay | Controller v2 | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Step with 1 s communication delay | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Step with 1 s communication delay | v2 + fault: filtered FCR (60 s) | FCR full activation time | 235.4 | <= 30 | s | FALSE
15 MW / 30 MWh (2 h) | Step with 1 s communication delay | v2 + fault: connection limit ignored | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | Controller v1 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | Controller v1 | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | Controller v2 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | Controller v2 | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: FCR sign error | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: FCR sign error | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: filtered FCR (60 s) | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: filtered FCR (60 s) | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: connection limit ignored | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 30 MWh (2 h) | Schedule step to full discharge | v2 + fault: connection limit ignored | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v1 | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v1 | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v1 | Lowest SOC | 49.61 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v2 | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v2 | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | Controller v2 | Lowest SOC | 49.61 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: FCR sign error | FCR tracking error (RMS) | 20.477 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: FCR sign error | FCR response direction (correlation) | -0.984 | >= 0.9 | - | FALSE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: FCR sign error | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 8.576 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | FCR response direction (correlation) | 0.552 | >= 0.9 | - | FALSE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: filtered FCR (60 s) | Lowest SOC | 49.651 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 1.849 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | FCR response direction (correlation) | 0.984 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Normal frequency (noise) | v2 + fault: connection limit ignored | Lowest SOC | 49.61 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v1 | Lowest SOC | 31.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | Controller v2 | Lowest SOC | 31.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | FCR sustained within 2% (15 min) | 0 | >= 99 | % of time | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: FCR sign error | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR sustained within 2% (15 min) | 77.516 | >= 99 | % of time | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | Lowest SOC | 32.85 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step -200 mHz, 15 min | v2 + fault: connection limit ignored | Lowest SOC | 31.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v1 | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | Controller v2 | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | FCR sustained within 2% (15 min) | 0 | >= 99 | % of time | FALSE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: FCR sign error | Lowest SOC | 31.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | FCR sustained within 2% (15 min) | 77.516 | >= 99 | % of time | FALSE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: filtered FCR (60 s) | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | FCR sustained within 2% (15 min) | 100 | >= 99 | % of time | TRUE
15 MW / 15 MWh (1 h) | Over-frequency step +200 mHz, 15 min | v2 + fault: connection limit ignored | Lowest SOC | 50 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | Controller v1 | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | Controller v1 | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | Controller v2 | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | Controller v2 | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: FCR sign error | FCR tracking error (RMS) | 122.378 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: FCR sign error | FCR response direction (correlation) | -1 | >= 0.9 | - | FALSE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 20.454 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: filtered FCR (60 s) | FCR response direction (correlation) | 0.891 | >= 0.9 | - | FALSE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 0.276 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Frequency ramp to 49.85 Hz | v2 + fault: connection limit ignored | FCR response direction (correlation) | 1 | >= 0.9 | - | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | Controller v1 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | Controller v1 | Lowest SOC | 4.647 | >= 5 | % | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | Controller v2 | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | Controller v2 | Lowest SOC | 7.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: FCR sign error | Lowest SOC | 12.001 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: filtered FCR (60 s) | FCR full activation time | 234.6 | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: filtered FCR (60 s) | Lowest SOC | 8.84 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: connection limit ignored | FCR full activation time | 1.4 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Under-frequency step at low SOC | v2 + fault: connection limit ignored | Lowest SOC | 7.685 | >= 5 | % | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | Controller v1 | FCR tracking error (RMS) | 9.033 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | Controller v1 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | Controller v2 | FCR tracking error (RMS) | 1.873 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | Controller v2 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: FCR sign error | FCR tracking error (RMS) | 21.362 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: FCR sign error | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: filtered FCR (60 s) | FCR tracking error (RMS) | 8.768 | <= 5 | % of FCR | FALSE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: filtered FCR (60 s) | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: connection limit ignored | FCR tracking error (RMS) | 1.873 | <= 5 | % of FCR | TRUE
15 MW / 15 MWh (1 h) | Wind surge at the connection limit | v2 + fault: connection limit ignored | Time above connection limit | 299.6 | <= 1 | s | FALSE
15 MW / 15 MWh (1 h) | Step with 1 s communication delay | Controller v1 | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Step with 1 s communication delay | Controller v2 | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Step with 1 s communication delay | v2 + fault: FCR sign error | FCR full activation time | inf | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Step with 1 s communication delay | v2 + fault: filtered FCR (60 s) | FCR full activation time | 235.4 | <= 30 | s | FALSE
15 MW / 15 MWh (1 h) | Step with 1 s communication delay | v2 + fault: connection limit ignored | FCR full activation time | 2.2 | <= 30 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | Controller v1 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | Controller v1 | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | Controller v2 | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | Controller v2 | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: FCR sign error | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: FCR sign error | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: filtered FCR (60 s) | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: filtered FCR (60 s) | Schedule settling time (2%) | 1 | <= 2 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: connection limit ignored | Time above connection limit | 0 | <= 1 | s | TRUE
15 MW / 15 MWh (1 h) | Schedule step to full discharge | v2 + fault: connection limit ignored | Schedule settling time (2%) | 1 | <= 2 | s | TRUE

## P3 Forecast series
Part 3: measured values and day-ahead forecasts, 15-min, test period
DateTime | load_actual | load_xgb | load_persist | load_profile7 | pv_actual | pv_xgb | pv_persist | pv_profile7
2021-10-01 | 3.3996 | 2.1547 | 0.32669 | 1.6216 | 0 | 0 | 0 | 0
2021-10-01 00:15 | 3.3077 | 2.1191 | 0.32567 | 1.6705 | 0 | 0 | 0 | 0
2021-10-01 00:30 | 3.3281 | 2.1191 | 0.32158 | 1.7481 | 0 | 0 | 0 | 0
2021-10-01 00:45 | 3.2975 | 2.2154 | 0.31954 | 2.0758 | 0 | 0 | 0 | 0
2021-10-01 01:00 | 3.3077 | 2.251 | 0.32158 | 2.0635 | 0 | 0 | 0 | 0
2021-10-01 01:15 | 3.42 | 2.251 | 0.3226 | 2.0618 | 0 | 0 | 0 | 0
2021-10-01 01:30 | 3.3281 | 2.251 | 0.3175 | 2.0667 | 0 | 0 | 0 | 0
2021-10-01 01:45 | 3.3077 | 2.2011 | 0.31648 | 2.0647 | 0 | 0 | 0 | 0
2021-10-01 02:00 | 3.3077 | 2.1395 | 0.31648 | 2.079 | 0 | 0 | 0 | 0
2021-10-01 02:15 | 3.369 | 2.1395 | 0.31852 | 2.0731 | 0 | 0 | 0 | 0
2021-10-01 02:30 | 3.4302 | 2.1395 | 0.3175 | 2.071 | 0 | 0 | 0 | 0
2021-10-01 02:45 | 3.3894 | 2.1395 | 0.31648 | 2.064 | 0 | 0 | 0 | 0
2021-10-01 03:00 | 3.3281 | 2.1395 | 0.31648 | 2.0632 | 0 | 0 | 0 | 0
2021-10-01 03:15 | 3.2975 | 2.1395 | 0.31444 | 2.0647 | 0 | 0 | 0 | 0
2021-10-01 03:30 | 3.3077 | 2.2162 | 0.31852 | 1.9693 | 0 | 0 | 0 | 0
2021-10-01 03:45 | 3.3587 | 2.1715 | 0.31648 | 1.7812 | 0 | 0 | 0 | 0
2021-10-01 04:00 | 2.2358 | 2.0751 | 0.31648 | 1.6689 | 0 | 0 | 0 | 0
2021-10-01 04:15 | 0.94331 | 2.0243 | 0.31444 | 1.6638 | 0 | 0 | 0 | 0
2021-10-01 04:30 | 0.75546 | 2.0682 | 0.31239 | 1.6251 | 0 | 0 | 0 | 0
2021-10-01 04:45 | 0.38794 | 1.9892 | 0.31648 | 1.6336 | 0 | 0 | 0 | 0
2021-10-01 05:00 | 0.28993 | 2.012 | 0.31954 | 1.6024 | 0 | 0 | 0 | 0
2021-10-01 05:15 | 0.21235 | 1.9634 | 0.31137 | 1.6006 | 0 | 0 | 0 | 0
2021-10-01 05:30 | 0.21745 | 2.0481 | 0.31444 | 1.6048 | 0 | 0 | 0 | 0
2021-10-01 05:45 | 0.31954 | 1.452 | 0.31648 | 1.5469 | 0.041928 | 0.030583 | 0.052585 | 0.029219
2021-10-01 06:00 | 0.31546 | 0.49637 | 0.32056 | 0.3315 | 0.097521 | 0.078037 | 0.12156 | 0.066178
2021-10-01 06:15 | 0.20418 | 0.51507 | 0.31546 | 0.26193 | 0.15311 | 0.12391 | 0.19053 | 0.10314
2021-10-01 06:30 | 1.2965 | 0.82837 | 1.562 | 0.87345 | 0.20871 | 0.1737 | 0.2595 | 0.14009
2021-10-01 06:45 | 2.7564 | 1.2887 | 2.7462 | 1.2149 | 0.2626 | 0.21962 | 0.32981 | 0.19247
2021-10-01 07:00 | 1.3884 | 1.6355 | 1.1128 | 2.2711 | 0.31594 | 0.24332 | 0.40054 | 0.24919
2021-10-01 07:15 | 0.64521 | 1.5836 | 0.91881 | 2.0943 | 0.36928 | 0.28463 | 0.47127 | 0.30591
2021-10-01 07:30 | 0.44919 | 1.501 | 0.7963 | 1.9059 | 0.42262 | 0.32994 | 0.54201 | 0.36263
2021-10-01 07:45 | 0.52678 | 1.3456 | 0.60845 | 1.9622 | 0.47528 | 0.34424 | 0.57165 | 0.37839
2021-10-01 08:00 | 0.54312 | 1.6719 | 0.66562 | 1.954 | 0.52772 | 0.35828 | 0.58843 | 0.38306
2021-10-01 08:15 | 0.58395 | 1.6702 | 0.66154 | 2.2399 | 0.58017 | 0.37747 | 0.60522 | 0.38773
2021-10-01 08:30 | 0.51045 | 1.5045 | 0.45736 | 2.0173 | 0.63261 | 0.40498 | 0.62201 | 0.39239
2021-10-01 08:45 | 2.3379 | 1.4839 | 0.51045 | 2.246 | 0.64493 | 0.41618 | 0.63979 | 0.40087
2021-10-01 09:00 | 0.60845 | 1.4668 | 0.57578 | 2.1609 | 0.64411 | 0.42084 | 0.65788 | 0.41012
2021-10-01 09:15 | 0.54312 | 1.3863 | 0.51453 | 1.6454 | 0.64329 | 0.4256 | 0.67598 | 0.41936
2021-10-01 09:30 | 0.53087 | 1.2755 | 0.5717 | 1.3684 | 0.64247 | 0.42536 | 0.69408 | 0.42861
2021-10-01 09:45 | 0.44103 | 1.1673 | 0.51862 | 0.65279 | 0.65399 | 0.3986 | 0.69953 | 0.43164
2021-10-01 10:00 | 0.42469 | 1.1181 | 0.51453 | 0.82634 | 0.66955 | 0.41483 | 0.70101 | 0.43325
2021-10-01 10:15 | 0.58804 | 1.1845 | 0.59212 | 0.44555 | 0.68511 | 0.41829 | 0.70249 | 0.43486
2021-10-01 10:30 | 0.33894 | 1.2008 | 0.55537 | 0.39275 | 0.70067 | 0.39443 | 0.70397 | 0.43648
2021-10-01 10:45 | 0.34098 | 1.3789 | 0.42469 | 0.37423 | 0.70336 | 0.41789 | 0.68441 | 0.44504
2021-10-01 11:00 | 0.38386 | 1.3916 | 0.42469 | 0.42236 | 0.70183 | 0.40352 | 0.65825 | 0.45534
2021-10-01 11:15 | 0.34608 | 1.0102 | 0.42878 | 0.81249 | 0.70029 | 0.40658 | 0.63208 | 0.46564
2021-10-01 11:30 | 0.44511 | 1.1338 | 0.23072 | 0.79528 | 0.69875 | 0.39647 | 0.60591 | 0.47594
2021-10-01 11:45 | 0.40836 | 1.4666 | 0.17866 | 1.2734 | 0.69738 | 0.41053 | 0.59163 | 0.48463
2021-10-01 12:00 | 0.32465 | 1.2682 | 0.19091 | 1.3868 | 0.69606 | 0.40359 | 0.58109 | 0.4934
2021-10-01 12:15 | 0.26543 | 1.3172 | 0.29606 | 1.2787 | 0.69474 | 0.39995 | 0.57056 | 0.50217
2021-10-01 12:30 | 1.1128 | 1.4124 | 0.28585 | 1.6885 | 0.69343 | 0.3968 | 0.56002 | 0.51094
2021-10-01 12:45 | 0.3369 | 1.4 | 0.28279 | 1.8921 | 0.66238 | 0.39266 | 0.58498 | 0.49734
2021-10-01 13:00 | 0.36752 | 1.3174 | 0.27156 | 1.6407 | 0.62152 | 0.39783 | 0.62116 | 0.47708
2021-10-01 13:15 | 0.30218 | 1.2319 | 0.18274 | 1.5497 | 0.58065 | 0.40343 | 0.65734 | 0.45681
2021-10-01 13:30 | 0.3226 | 1.567 | 0.18274 | 1.694 | 0.53979 | 0.41741 | 0.69352 | 0.43655
2021-10-01 13:45 | 0.31444 | 1.1937 | 0.1807 | 1.1266 | 0.50506 | 0.41675 | 0.69996 | 0.42708
2021-10-01 14:00 | 0.27768 | 1.1034 | 0.17866 | 0.78026 | 0.47237 | 0.42006 | 0.69699 | 0.42117
2021-10-01 14:15 | 0.35119 | 1.195 | 0.17968 | 0.75167 | 0.43967 | 0.41395 | 0.69403 | 0.41526
2021-10-01 14:30 | 0.49411 | 1.1034 | 0.18376 | 0.74832 | 0.40698 | 0.41014 | 0.69106 | 0.40935
2021-10-01 14:45 | 0.39611 | 1.1129 | 0.25625 | 0.50797 | 0.37822 | 0.39473 | 0.67699 | 0.4137
2021-10-01 15:00 | 0.36752 | 1.2327 | 0.28381 | 0.98239 | 0.35078 | 0.38426 | 0.6594 | 0.42001
2021-10-01 15:15 | 0.32465 | 1.1332 | 0.27973 | 0.963 | 0.32333 | 0.3781 | 0.64181 | 0.42633
2021-10-01 15:30 | 0.45736 | 1.0497 | 0.25216 | 0.54253 | 0.29588 | 0.36879 | 0.62422 | 0.43264
2021-10-01 15:45 | 0.56354 | 1.0577 | 0.21235 | 0.4963 | 0.24754 | 0.33207 | 0.56751 | 0.38753
2021-10-01 16:00 | 0.34608 | 1.037 | 0.21235 | 0.44642 | 0.19227 | 0.30148 | 0.49837 | 0.32872
2021-10-01 16:15 | 0.8453 | 0.8316 | 0.20724 | 0.43928 | 0.137 | 0.29445 | 0.42924 | 0.26992
2021-10-01 16:30 | 0.90247 | 0.74833 | 0.2103 | 0.38838 | 0.081725 | 0.28963 | 0.36011 | 0.21111
2021-10-01 16:45 | 0.82897 | 0.87405 | 0.21235 | 0.4473 | 0.055187 | 0.22705 | 0.27829 | 0.16053
2021-10-01 17:00 | 1.0719 | 0.92153 | 0.32771 | 0.43534 | 0.038206 | 0.19648 | 0.19244 | 0.11231
2021-10-01 17:15 | 1.1128 | 0.84579 | 0.30933 | 0.37204 | 0.021225 | 0.1449 | 0.1066 | 0.064094
2021-10-01 17:30 | 1.3476 | 0.87646 | 0.31137 | 0.44715 | 0.004244 | 0.097479 | 0.020749 | 0.015876
2021-10-01 17:45 | 1.1842 | 0.92815 | 0.2297 | 0.60554 | 0 | 0.004047 | 0 | 0.004423
2021-10-01 18:00 | 0.79222 | 1.6065 | 2.6033 | 1.6859 | 0 | 0.002952 | 0 | 0.003037
2021-10-01 18:15 | 0.53087 | 1.5863 | 2.736 | 1.9556 | 0 | 0.002093 | 0 | 0.001652
2021-10-01 18:30 | 0.53495 | 1.321 | 2.736 | 2.0579 | 0 | 0.000384 | 0 | 0.000267
2021-10-01 18:45 | 3.8488 | 1.2776 | 2.736 | 1.5131 | 0 | 0 | 0 | 0
2021-10-01 19:00 | 1.7151 | 1.0476 | 0.46144 | 0.98458 | 0 | 0 | 0 | 0
2021-10-01 19:15 | 0.32465 | 0.8152 | 0.30933 | 0.9506 | 0 | 0 | 0 | 0
2021-10-01 19:30 | 0.4737 | 0.85502 | 0.31648 | 0.77734 | 0 | 0 | 0 | 0
2021-10-01 19:45 | 0.5962 | 0.8909 | 0.22358 | 0.84166 | 0 | 0 | 0 | 0
2021-10-01 20:00 | 0.62479 | 0.8907 | 0.17049 | 0.7874 | 0 | 0 | 0 | 0
2021-10-01 20:15 | 0.51862 | 0.87627 | 0.17253 | 0.83961 | 0 | 0 | 0 | 0
2021-10-01 20:30 | 0.52678 | 0.87627 | 0.17355 | 0.79776 | 0 | 0 | 0 | 0
2021-10-01 20:45 | 0.53087 | 0.87547 | 0.28381 | 0.72192 | 0 | 0 | 0 | 0
2021-10-01 21:00 | 0.52678 | 0.84135 | 0.56354 | 0.62012 | 0 | 0 | 0 | 0
2021-10-01 21:15 | 0.45328 | 0.68576 | 0.33179 | 0.51847 | 0 | 0 | 0 | 0
2021-10-01 21:30 | 0.41244 | 0.59213 | 0.44919 | 0.46684 | 0 | 0 | 0 | 0
2021-10-01 21:45 | 0.41244 | 0.58062 | 0.3369 | 0.41959 | 0 | 0 | 0 | 0
2021-10-01 22:00 | 3.3894 | 1.1268 | 3.2362 | 1.7545 | 0 | 0 | 0 | 0
2021-10-01 22:15 | 3.471 | 1.1984 | 3.42 | 1.7096 | 0 | 0 | 0 | 0
2021-10-01 22:30 | 3.3485 | 1.0326 | 3.4098 | 1.6731 | 0 | 0 | 0 | 0
2021-10-01 22:45 | 3.3077 | 1.1066 | 3.3179 | 1.6905 | 0 | 0 | 0 | 0
2021-10-01 23:00 | 3.3485 | 1.1335 | 3.2873 | 1.7134 | 0 | 0 | 0 | 0
2021-10-01 23:15 | 3.4915 | 1.1815 | 3.2975 | 1.6753 | 0 | 0 | 0 | 0
2021-10-01 23:30 | 3.3996 | 1.0326 | 3.2975 | 1.6463 | 0 | 0 | 0 | 0
2021-10-01 23:45 | 3.369 | 1.2548 | 3.4098 | 1.6451 | 0 | 0 | 0 | 0
2021-10-02 | 3.4506 | 0.92008 | 3.3996 | 1.6245 | 0 | 0 | 0 | 0
2021-10-02 00:15 | 3.3996 | 0.93198 | 3.3077 | 1.6515 | 0 | 0 | 0 | 0
2021-10-02 00:30 | 3.4098 | 1.0298 | 3.3281 | 1.7451 | 0 | 0 | 0 | 0
2021-10-02 00:45 | 3.4506 | 1.5717 | 3.2975 | 2.067 | 0 | 0 | 0 | 0
2021-10-02 01:00 | 3.3587 | 1.6133 | 3.3077 | 2.0519 | 0 | 0 | 0 | 0
2021-10-02 01:15 | 3.471 | 1.6266 | 3.42 | 2.053 | 0 | 0 | 0 | 0
2021-10-02 01:30 | 3.369 | 1.6133 | 3.3281 | 2.0565 | 0 | 0 | 0 | 0
2021-10-02 01:45 | 3.4302 | 1.5828 | 3.3077 | 2.0559 | 0 | 0 | 0 | 0
2021-10-02 02:00 | 3.4915 | 1.4552 | 3.3077 | 2.0702 | 0 | 0 | 0 | 0
2021-10-02 02:15 | 3.369 | 1.5021 | 3.369 | 2.0586 | 0 | 0 | 0 | 0
2021-10-02 02:30 | 3.4302 | 1.4606 | 3.4302 | 2.0695 | 0 | 0 | 0 | 0
2021-10-02 02:45 | 3.2669 | 1.4904 | 3.3894 | 2.0669 | 0 | 0 | 0 | 0
2021-10-02 03:00 | 1.6539 | 1.5021 | 3.3281 | 2.0559 | 0 | 0 | 0 | 0
2021-10-02 03:15 | 0.95556 | 1.5021 | 3.2975 | 2.0501 | 0 | 0 | 0 | 0
2021-10-02 03:30 | 0.62479 | 1.6209 | 3.3077 | 1.9445 | 0 | 0 | 0 | 0
2021-10-02 03:45 | 0.3665 | 1.4965 | 3.3587 | 1.7797 | 0 | 0 | 0 | 0
2021-10-02 04:00 | 0.25318 | 1.4502 | 2.2358 | 1.5099 | 0 | 0 | 0 | 0
2021-10-02 04:15 | 0.36446 | 1.511 | 0.94331 | 1.3158 | 0 | 0 | 0 | 0
2021-10-02 04:30 | 0.25727 | 1.3794 | 0.75546 | 1.2343 | 0 | 0 | 0 | 0
2021-10-02 04:45 | 0.30729 | 1.2797 | 0.38794 | 1.2048 | 0 | 0 | 0 | 0
2021-10-02 05:00 | 0.40223 | 1.1844 | 0.28993 | 1.1625 | 0 | 0 | 0 | 0
2021-10-02 05:15 | 0.27564 | 1.3169 | 0.21235 | 1.1497 | 0 | 0 | 0 | 0
2021-10-02 05:30 | 0.26543 | 1.1812 | 0.21745 | 1.1371 | 0 | 0 | 0 | 0
2021-10-02 05:45 | 0.36242 | 1.1844 | 0.31954 | 1.1667 | 0.039602 | 0.031137 | 0.041928 | 0.026021
2021-10-02 06:00 | 0.26237 | 0.58893 | 0.31546 | 0.32917 | 0.09269 | 0.08289 | 0.097521 | 0.059602
2021-10-02 06:15 | 0.27666 | 0.85576 | 0.20418 | 0.26004 | 0.14578 | 0.14444 | 0.15311 | 0.093183
2021-10-02 06:30 | 1.5518 | 0.99242 | 1.2965 | 0.9525 | 0.19887 | 0.19423 | 0.20871 | 0.12676
2021-10-02 06:45 | 2.1643 | 1.1749 | 2.7564 | 1.1886 | 0.24401 | 0.23913 | 0.2626 | 0.17731
2021-10-02 07:00 | 1.1434 | 1.5076 | 1.3884 | 2.1646 | 0.28645 | 0.28841 | 0.31594 | 0.23253
2021-10-02 07:15 | 0.64929 | 1.5033 | 0.64521 | 2.01 | 0.32888 | 0.33659 | 0.36928 | 0.28774
2021-10-02 07:30 | 0.75955 | 1.5407 | 0.44919 | 1.8405 | 0.37132 | 0.38877 | 0.42262 | 0.34296
2021-10-02 07:45 | 0.64112 | 1.4943 | 0.52678 | 1.9505 | 0.33971 | 0.41704 | 0.47528 | 0.36175
2021-10-02 08:00 | 0.64521 | 1.5191 | 0.54312 | 1.6203 | 0.2828 | 0.43222 | 0.52772 | 0.37047
2021-10-02 08:15 | 0.51862 | 1.517 | 0.58395 | 1.8974 | 0.22588 | 0.44822 | 0.58017 | 0.3792
2021-10-02 08:30 | 0.46961 | 1.3305 | 0.51045 | 1.9093 | 0.16897 | 0.48605 | 0.63261 | 0.38793
2021-10-02 08:45 | 0.48595 | 1.3377 | 2.3379 | 2.2679 | 0.1795 | 0.48362 | 0.64493 | 0.39657
2021-10-02 09:00 | 0.49411 | 1.3733 | 0.60845 | 1.9415 | 0.21313 | 0.48647 | 0.64411 | 0.40454
2021-10-02 09:15 | 0.5472 | 1.3178 | 0.54312 | 1.6535 | 0.24676 | 0.4918 | 0.64329 | 0.41251
2021-10-02 09:30 | 0.63296 | 1.2755 | 0.53087 | 1.3938 | 0.28039 | 0.51295 | 0.64247 | 0.42047
2021-10-02 09:45 | 0.5717 | 1.2885 | 0.44103 | 0.65396 | 0.29625 | 0.51602 | 0.65399 | 0.42443
2021-10-02 10:00 | 0.55128 | 1.1988 | 0.42469 | 0.83043 | 0.30601 | 0.51544 | 0.66955 | 0.42764
2021-10-02 10:15 | 3.1035 | 1.1565 | 0.58804 | 0.48099 | 0.31577 | 0.50539 | 0.68511 | 0.43086
2021-10-02 10:30 | 0.57987 | 1.4274 | 0.33894 | 0.39523 | 0.32552 | 0.50652 | 0.70067 | 0.43408
2021-10-02 10:45 | 0.55945 | 1.3351 | 0.34098 | 0.37832 | 0.37839 | 0.50491 | 0.70336 | 0.44301
2021-10-02 11:00 | 0.44919 | 1.3452 | 0.38386 | 0.43023 | 0.44606 | 0.49928 | 0.70183 | 0.45323
2021-10-02 11:15 | 0.44511 | 1.2807 | 0.34608 | 0.8119 | 0.51374 | 0.5021 | 0.70029 | 0.46344
2021-10-02 11:30 | 0.43694 | 1.2249 | 0.44511 | 0.79178 | 0.58141 | 0.52468 | 0.69875 | 0.47365
2021-10-02 11:45 | 2.6543 | 1.2705 | 0.40836 | 1.2606 | 0.59661 | 0.48095 | 0.69738 | 0.4827
2021-10-02 12:00 | 1.7049 | 1.4201 | 0.32465 | 1.3836 | 0.59375 | 0.48873 | 0.69606 | 0.49194
2021-10-02 12:15 | 0.37365 | 1.3328 | 0.26543 | 1.2717 | 0.59089 | 0.48432 | 0.69474 | 0.50118
2021-10-02 12:30 | 1.0924 | 1.2579 | 1.1128 | 1.7594 | 0.58802 | 0.4805 | 0.69343 | 0.51042
2021-10-02 12:45 | 0.67379 | 1.4847 | 0.3369 | 1.8627 | 0.58955 | 0.47219 | 0.66238 | 0.49182
2021-10-02 13:00 | 0.42878 | 1.4873 | 0.36752 | 1.6441 | 0.59259 | 0.47006 | 0.62152 | 0.46487
2021-10-02 13:15 | 0.4737 | 1.2827 | 0.30218 | 1.5446 | 0.59562 | 0.48799 | 0.58065 | 0.43791
2021-10-02 13:30 | 0.47778 | 1.229 | 0.3226 | 1.6913 | 0.59866 | 0.52158 | 0.53979 | 0.41096
2021-10-02 13:45 | 0.47778 | 1.1131 | 0.31444 | 1.1368 | 0.53554 | 0.51927 | 0.50506 | 0.39711
2021-10-02 14:00 | 0.46961 | 1.1568 | 0.27768 | 0.77267 | 0.44956 | 0.4964 | 0.47237 | 0.38745
2021-10-02 14:15 | 0.45736 | 1.2476 | 0.35119 | 0.75459 | 0.36358 | 0.49522 | 0.43967 | 0.37778
2021-10-02 14:30 | 0.35119 | 1.2415 | 0.49411 | 0.7718 | 0.2776 | 0.48789 | 0.40698 | 0.36812
2021-10-02 14:45 | 0.35119 | 1.0086 | 0.39611 | 0.51468 | 0.30948 | 0.46875 | 0.37822 | 0.37004
2021-10-02 15:00 | 0.3859 | 1.292 | 0.36752 | 0.96956 | 0.38217 | 0.4585 | 0.35078 | 0.37429
2021-10-02 15:15 | 0.46144 | 1.2307 | 0.32465 | 0.84166 | 0.45485 | 0.45258 | 0.32333 | 0.37854
2021-10-02 15:30 | 0.35629 | 0.99766 | 0.45736 | 0.5122 | 0.52753 | 0.43635 | 0.29588 | 0.38279
2021-10-02 15:45 | 0.38692 | 1.008 | 0.56354 | 0.49689 | 0.45448 | 0.39442 | 0.24754 | 0.33598
2021-10-02 16:00 | 0.50636 | 0.98364 | 0.34608 | 0.32669 | 0.33091 | 0.37337 | 0.19227 | 0.27528
2021-10-02 16:15 | 0.39407 | 0.99125 | 0.8453 | 0.40982 | 0.20733 | 0.3482 | 0.137 | 0.21458
2021-10-02 16:30 | 0.37569 | 0.94158 | 0.90247 | 0.40413 | 0.083756 | 0.31755 | 0.081725 | 0.15388
2021-10-02 16:45 | 0.42469 | 0.91543 | 0.82897 | 0.41551 | 0.042271 | 0.23997 | 0.055187 | 0.11323
2021-10-02 17:00 | 0.61254 | 0.93164 | 1.0719 | 0.52314 | 0.029297 | 0.19208 | 0.038206 | 0.078136
2021-10-02 17:15 | 0.40836 | 0.91978 | 1.1128 | 0.47618 | 0.016323 | 0.10985 | 0.021225 | 0.043042
2021-10-02 17:30 | 0.27156 | 1.0922 | 1.3476 | 0.58016 | 0.003349 | 0.070397 | 0.004244 | 0.007949
2021-10-02 17:45 | 0.38998 | 1.1143 | 1.1842 | 0.71229 | 0 | 0.00252 | 0 | 0
2021-10-02 18:00 | 2.6135 | 1.3786 | 0.79222 | 1.3382 | 0 | 0.001655 | 0 | 0
2021-10-02 18:15 | 2.7666 | 1.4827 | 0.53087 | 1.6829 | 0 | 0.000456 | 0 | 0
2021-10-02 18:30 | 2.7768 | 1.4143 | 0.53495 | 2.069 | 0 | 0.00011 | 0 | 0
2021-10-02 18:45 | 2.9708 | 1.5056 | 3.8488 | 2.0005 | 0 | 0 | 0 | 0
2021-10-02 19:00 | 0.78813 | 1.1488 | 1.7151 | 1.1456 | 0 | 0 | 0 | 0
2021-10-02 19:15 | 0.55537 | 1.1056 | 0.32465 | 0.95527 | 0 | 0 | 0 | 0
2021-10-02 19:30 | 0.62479 | 0.96201 | 0.4737 | 0.78726 | 0 | 0 | 0 | 0
2021-10-02 19:45 | 0.65337 | 0.90786 | 0.5962 | 0.85916 | 0 | 0 | 0 | 0
2021-10-02 20:00 | 0.8208 | 0.86279 | 0.62479 | 0.8084 | 0 | 0 | 0 | 0
2021-10-02 20:15 | 0.92289 | 0.87793 | 0.51862 | 0.83903 | 0 | 0 | 0 | 0
2021-10-02 20:30 | 0.57578 | 0.9136 | 0.52678 | 0.79367 | 0 | 0 | 0 | 0
2021-10-02 20:45 | 0.32158 | 0.85359 | 0.53087 | 0.71959 | 0 | 0 | 0 | 0
2021-10-02 21:00 | 0.34404 | 0.82246 | 0.52678 | 0.60787 | 0 | 0 | 0 | 0
2021-10-02 21:15 | 0.42878 | 0.61926 | 0.45328 | 0.48638 | 0 | 0 | 0 | 0
2021-10-02 21:30 | 0.46553 | 0.61089 | 0.41244 | 0.45109 | 0 | 0 | 0 | 0
2021-10-02 21:45 | 0.46144 | 0.627 | 0.41244 | 0.41959 | 0 | 0 | 0 | 0
2021-10-02 22:00 | 3.3485 | 1.2588 | 3.3894 | 2.1774 | 0 | 0 | 0 | 0
2021-10-02 22:15 | 3.5119 | 1.2588 | 3.471 | 2.1465 | 0 | 0 | 0 | 0
2021-10-02 22:30 | 3.471 | 1.1993 | 3.3485 | 2.0925 | 0 | 0 | 0 | 0
2021-10-02 22:45 | 3.5731 | 1.1993 | 3.3077 | 2.0871 | 0 | 0 | 0 | 0
2021-10-02 23:00 | 3.3077 | 1.2588 | 3.3485 | 2.1153 | 0 | 0 | 0 | 0
2021-10-02 23:15 | 3.3179 | 1.2588 | 3.4915 | 2.1134 | 0 | 0 | 0 | 0
2021-10-02 23:30 | 3.3894 | 1.1993 | 3.3996 | 2.073 | 0 | 0 | 0 | 0
2021-10-02 23:45 | 3.3077 | 1.1993 | 3.369 | 2.0675 | 0 | 0 | 0 | 0
2021-10-03 | 3.3485 | 1.1275 | 3.4506 | 2.0586 | 0 | 0 | 0 | 0
2021-10-03 00:15 | 3.3383 | 1.1275 | 3.3996 | 2.066 | 0 | 0 | 0 | 0
2021-10-03 00:30 | 3.2873 | 1.1275 | 3.4098 | 2.0675 | 0 | 0 | 0 | 0
2021-10-03 00:45 | 3.369 | 1.1275 | 3.4506 | 2.0641 | 0 | 0 | 0 | 0
2021-10-03 01:00 | 3.3077 | 1.1275 | 3.3587 | 2.0489 | 0 | 0 | 0 | 0
2021-10-03 01:15 | 3.3894 | 1.1275 | 3.471 | 2.0647 | 0 | 0 | 0 | 0
2021-10-03 01:30 | 3.3077 | 1.1275 | 3.369 | 2.0536 | 0 | 0 | 0 | 0
2021-10-03 01:45 | 3.3587 | 1.226 | 3.4302 | 2.053 | 0 | 0 | 0 | 0
2021-10-03 02:00 | 3.5323 | 1.0877 | 3.4915 | 2.0673 | 0 | 0 | 0 | 0
2021-10-03 02:15 | 3.6548 | 1.0877 | 3.369 | 2.0498 | 0 | 0 | 0 | 0
2021-10-03 02:30 | 3.369 | 1.0877 | 3.4302 | 2.0724 | 0 | 0 | 0 | 0
2021-10-03 02:45 | 3.42 | 1.1171 | 3.2669 | 2.0508 | 0 | 0 | 0 | 0
2021-10-03 03:00 | 3.4302 | 1.1171 | 1.6539 | 1.8138 | 0 | 0 | 0 | 0
2021-10-03 03:15 | 3.4302 | 1.1232 | 0.95556 | 1.6951 | 0 | 0 | 0 | 0
2021-10-03 03:30 | 3.369 | 1.141 | 0.62479 | 1.5379 | 0 | 0 | 0 | 0
2021-10-03 03:45 | 3.3281 | 1.1877 | 0.3665 | 1.3522 | 0 | 0 | 0 | 0
2021-10-03 04:00 | 3.4302 | 0.86247 | 0.25318 | 1.0677 | 0 | 0 | 0 | 0
2021-10-03 04:15 | 3.3485 | 0.80032 | 0.36446 | 0.88658 | 0 | 0 | 0 | 0
2021-10-03 04:30 | 3.3792 | 0.7994 | 0.25727 | 0.78244 | 0 | 0 | 0 | 0
2021-10-03 04:45 | 3.4608 | 0.7994 | 0.30729 | 0.747 | 0 | 0 | 0 | 0
2021-10-03 05:00 | 3.3485 | 0.76975 | 0.40223 | 0.72702 | 0 | 0 | 0 | 0
2021-10-03 05:15 | 3.4506 | 0.81389 | 0.27564 | 0.70486 | 0 | 0 | 0 | 0
2021-10-03 05:30 | 3.1546 | 0.81297 | 0.26543 | 0.69085 | 0 | 0 | 0 | 0
2021-10-03 05:45 | 1.6947 | 0.81389 | 0.36242 | 0.73869 | 0.002335 | 0.026895 | 0.039602 | 0.024534
2021-10-03 06:00 | 0.36956 | 0.5525 | 0.26237 | 0.28556 | 0.0055 | 0.077508 | 0.09269 | 0.056808
2021-10-03 06:15 | 0.2103 | 0.61739 | 0.27666 | 0.25799 | 0.008664 | 0.14142 | 0.14578 | 0.089083
2021-10-03 06:30 | 0.3226 | 0.80021 | 1.5518 | 0.84749 | 0.011829 | 0.17288 | 0.19887 | 0.12136
2021-10-03 06:45 | 0.28075 | 1.2398 | 2.1643 | 1.2936 | 0.011296 | 0.21597 | 0.24401 | 0.16834
2021-10-03 07:00 | 1.419 | 1.9084 | 1.1434 | 1.7854 | 0.009446 | 0.25365 | 0.28645 | 0.21932
2021-10-03 07:15 | 0.73913 | 2.1293 | 0.64929 | 1.5544 | 0.007596 | 0.27106 | 0.32888 | 0.27031
2021-10-03 07:30 | 1.1842 | 1.9451 | 0.75955 | 1.4313 | 0.005746 | 0.30251 | 0.37132 | 0.3213
2021-10-03 07:45 | 0.76363 | 1.9451 | 0.64112 | 1.4966 | 0.012566 | 0.31909 | 0.33971 | 0.33046
2021-10-03 08:00 | 0.5962 | 1.9968 | 0.64521 | 1.4689 | 0.022477 | 0.34378 | 0.2828 | 0.32721
2021-10-03 08:15 | 0.58395 | 2.2176 | 0.51862 | 1.6842 | 0.032389 | 0.36322 | 0.22588 | 0.32396
2021-10-03 08:30 | 0.5962 | 2.3065 | 0.46961 | 1.6541 | 0.042301 | 0.38821 | 0.16897 | 0.32071
2021-10-03 08:45 | 0.97189 | 2.3 | 0.48595 | 2.2055 | 0.066929 | 0.39402 | 0.1795 | 0.3295
2021-10-03 09:00 | 2.7666 | 2.2602 | 0.49411 | 1.9275 | 0.096816 | 0.40895 | 0.21313 | 0.34152
2021-10-03 09:15 | 1.6947 | 2.2663 | 0.5472 | 1.6273 | 0.1267 | 0.41343 | 0.24676 | 0.35354
2021-10-03 09:30 | 0.49411 | 1.9009 | 0.63296 | 1.3833 | 0.15659 | 0.41791 | 0.28039 | 0.36556
2021-10-03 09:45 | 0.26441 | 1.1888 | 0.5717 | 0.66212 | 0.17009 | 0.42344 | 0.29625 | 0.37138
2021-10-03 10:00 | 0.27054 | 1.373 | 0.55128 | 0.84793 | 0.17773 | 0.44692 | 0.30601 | 0.37566
2021-10-03 10:15 | 0.31444 | 1.2224 | 3.1035 | 0.85843 | 0.18536 | 0.44758 | 0.31577 | 0.37995
2021-10-03 10:30 | 0.25829 | 1.7372 | 0.57987 | 0.42498 | 0.19299 | 0.44025 | 0.32552 | 0.38424
2021-10-03 10:45 | 0.37161 | 1.6069 | 0.55945 | 0.4018 | 0.17258 | 0.44378 | 0.37839 | 0.40072
2021-10-03 11:00 | 0.44511 | 1.4931 | 0.44919 | 0.43257 | 0.1421 | 0.45389 | 0.44606 | 0.42066
2021-10-03 11:15 | 0.18785 | 1.7042 | 0.44511 | 0.82197 | 0.11163 | 0.45106 | 0.51374 | 0.4406
2021-10-03 11:30 | 0.18172 | 1.6867 | 0.43694 | 0.8087 | 0.081155 | 0.42236 | 0.58141 | 0.46054
2021-10-03 11:45 | 0.18172 | 1.9912 | 2.6543 | 1.5945 | 0.070932 | 0.41119 | 0.59661 | 0.47193
2021-10-03 12:00 | 1.2455 | 1.8935 | 1.7049 | 1.5808 | 0.067984 | 0.40719 | 0.59375 | 0.48096
2021-10-03 12:15 | 1.7457 | 1.8866 | 0.37365 | 1.2703 | 0.065037 | 0.40351 | 0.59089 | 0.48997
2021-10-03 12:30 | 1.858 | 2.0979 | 1.0924 | 1.8379 | 0.06209 | 0.40032 | 0.58802 | 0.499
2021-10-03 12:45 | 1.9193 | 2.0323 | 0.67379 | 1.8172 | 0.064082 | 0.40801 | 0.58955 | 0.48715
2021-10-03 13:00 | 1.807 | 1.9018 | 0.42878 | 1.4209 | 0.067852 | 0.41339 | 0.59259 | 0.46875
2021-10-03 13:15 | 0.99639 | 1.7585 | 0.4737 | 1.3483 | 0.071621 | 0.41877 | 0.59562 | 0.45034
2021-10-03 13:30 | 0.46553 | 1.3872 | 0.47778 | 1.4868 | 0.075391 | 0.42415 | 0.59866 | 0.43194
2021-10-03 13:45 | 0.31239 | 1.1845 | 0.47778 | 0.94258 | 0.0753 | 0.42228 | 0.53554 | 0.42163
2021-10-03 14:00 | 0.24093 | 1.1845 | 0.46961 | 0.76684 | 0.073818 | 0.41515 | 0.44956 | 0.41334
2021-10-03 14:15 | 0.17764 | 1.1821 | 0.45736 | 0.76348 | 0.072336 | 0.40833 | 0.36358 | 0.40506
2021-10-03 14:30 | 0.17661 | 1.2007 | 0.35119 | 0.77063 | 0.070853 | 0.40652 | 0.2776 | 0.39677
2021-10-03 14:45 | 0.18376 | 1.0867 | 0.35119 | 0.52868 | 0.059588 | 0.40072 | 0.30948 | 0.3938
2021-10-03 15:00 | 0.18274 | 1.2161 | 0.3859 | 0.98867 | 0.044789 | 0.39604 | 0.38217 | 0.39323
2021-10-03 15:15 | 0.21847 | 1.1303 | 0.46144 | 0.87126 | 0.02999 | 0.38969 | 0.45485 | 0.39265
2021-10-03 15:30 | 0.29606 | 0.95185 | 0.35629 | 0.52605 | 0.015192 | 0.38334 | 0.52753 | 0.39208
2021-10-03 15:45 | 0.27564 | 0.9876 | 0.38692 | 0.49513 | 0.009981 | 0.3427 | 0.45448 | 0.34237
2021-10-03 16:00 | 0.1807 | 0.9361 | 0.50636 | 0.34798 | 0.008238 | 0.30898 | 0.33091 | 0.27723
2021-10-03 16:15 | 0.17764 | 0.88562 | 0.39407 | 0.42542 | 0.006496 | 0.29305 | 0.20733 | 0.21209
2021-10-03 16:30 | 0.18172 | 0.86703 | 0.37569 | 0.41696 | 0.004753 | 0.26049 | 0.083756 | 0.14695
2021-10-03 16:45 | 2.8585 | 0.87695 | 0.42469 | 0.43563 | 0.003503 | 0.18148 | 0.042271 | 0.10627
2021-10-03 17:00 | 3.5119 | 0.92766 | 0.61254 | 0.54647 | 0.00243 | 0.1334 | 0.029297 | 0.073382
2021-10-03 17:15 | 3.2567 | 0.87832 | 0.40836 | 0.48288 | 0.001358 | 0.08122 | 0.016323 | 0.040497
2021-10-03 17:30 | 0.33077 | 0.98976 | 0.27156 | 0.57841 | 0.000286 | 0.04517 | 0.003349 | 0.007612
2021-10-03 17:45 | 0.53495 | 1.0091 | 0.38998 | 0.71521 | 0 | 0.002424 | 0 | 0
2021-10-03 18:00 | 2.3072 | 1.2295 | 2.6135 | 1.3207 | 0 | 0.001594 | 0 | 0
2021-10-03 18:15 | 1.0617 | 1.2309 | 2.7666 | 1.6537 | 0 | 0.000643 | 0 | 0
2021-10-03 18:30 | 0.2981 | 1.3162 | 2.7768 | 2.2251 | 0 | 0.000303 | 0 | 0
2021-10-03 18:45 | 0.32056 | 1.4037 | 2.9708 | 2.3642 | 0 | 0 | 0 | 0
2021-10-03 19:00 | 0.39509 | 0.9775 | 0.78813 | 1.1829 | 0 | 0 | 0 | 0
2021-10-03 19:15 | 0.36956 | 0.90707 | 0.55537 | 0.90568 | 0 | 0 | 0 | 0
2021-10-03 19:30 | 1.7151 | 0.81889 | 0.62479 | 0.74759 | 0 | 0 | 0 | 0
2021-10-03 19:45 | 2.5727 | 0.98839 | 0.65337 | 0.78332 | 0 | 0 | 0 | 0
2021-10-03 20:00 | 0.33485 | 0.8938 | 0.8208 | 0.84574 | 0 | 0 | 0 | 0
2021-10-03 20:15 | 0.23276 | 0.95326 | 0.92289 | 0.89037 | 0 | 0 | 0 | 0
2021-10-03 20:30 | 0.17661 | 0.9316 | 0.57578 | 0.77092 | 0 | 0 | 0 | 0
2021-10-03 20:45 | 0.17559 | 0.91664 | 0.32158 | 0.68444 | 0 | 0 | 0 | 0
2021-10-03 21:00 | 0.18989 | 0.8735 | 0.34404 | 0.59868 | 0 | 0 | 0 | 0
2021-10-03 21:15 | 0.30525 | 0.65137 | 0.42878 | 0.48113 | 0 | 0 | 0 | 0
2021-10-03 21:30 | 0.27258 | 0.57948 | 0.46553 | 0.45459 | 0 | 0 | 0 | 0
2021-10-03 21:45 | 0.17559 | 0.63512 | 0.46144 | 0.43519 | 0 | 0 | 0 | 0
2021-10-03 22:00 | 0.17764 | 2.1491 | 3.3485 | 2.6011 | 0 | 0 | 0 | 0
2021-10-03 22:15 | 0.17866 | 2.0482 | 3.5119 | 2.6017 | 0 | 0 | 0 | 0
2021-10-03 22:30 | 0.27564 | 2.0432 | 3.471 | 2.5489 | 0 | 0 | 0 | 0
2021-10-03 22:45 | 0.28177 | 2.0432 | 3.5731 | 2.5452 | 0 | 0 | 0 | 0
2021-10-03 23:00 | 0.17559 | 2.1881 | 3.3077 | 2.5355 | 0 | 0 | 0 | 0
2021-10-03 23:15 | 0.17661 | 2.0998 | 3.3179 | 2.549 | 0 | 0 | 0 | 0
2021-10-03 23:30 | 0.24399 | 2.1727 | 3.3894 | 2.5216 | 0 | 0 | 0 | 0
2021-10-03 23:45 | 3.2362 | 2.1071 | 3.3077 | 2.5041 | 0 | 0 | 0 | 0
2021-10-04 | 3.3383 | 2.1523 | 3.3485 | 2.5012 | 0 | 0 | 0 | 0
2021-10-04 00:15 | 3.2873 | 2.173 | 3.3383 | 2.4923 | 0 | 0 | 0 | 0
2021-10-04 00:30 | 3.3894 | 2.2037 | 3.2873 | 2.4898 | 0 | 0 | 0 | 0
2021-10-04 00:45 | 3.2873 | 2.1523 | 3.369 | 2.5101 | 0 | 0 | 0 | 0
2021-10-04 01:00 | 3.3383 | 2.1523 | 3.3077 | 2.4868 | 0 | 0 | 0 | 0
2021-10-04 01:15 | 3.4302 | 2.2037 | 3.3894 | 2.5086 | 0 | 0 | 0 | 0
2021-10-04 01:30 | 3.3485 | 2.173 | 3.3077 | 2.4744 | 0 | 0 | 0 | 0
2021-10-04 01:45 | 3.2975 | 2.1582 | 3.3587 | 2.4935 | 0 | 0 | 0 | 0
2021-10-04 02:00 | 3.2975 | 2.0867 | 3.5323 | 2.5366 | 0 | 0 | 0 | 0
2021-10-04 02:15 | 3.3894 | 2.1073 | 3.6548 | 2.5371 | 0 | 0 | 0 | 0
2021-10-04 02:30 | 3.3587 | 2.1425 | 3.369 | 2.5123 | 0 | 0 | 0 | 0
2021-10-04 02:45 | 3.369 | 2.0835 | 3.42 | 2.4873 | 0 | 0 | 0 | 0
2021-10-04 03:00 | 3.5119 | 2.1227 | 3.4302 | 2.2611 | 0 | 0 | 0 | 0
2021-10-04 03:15 | 3.4302 | 2.1227 | 3.4302 | 2.15 | 0 | 0 | 0 | 0
2021-10-04 03:30 | 3.3587 | 2.0706 | 3.369 | 1.9846 | 0 | 0 | 0 | 0
2021-10-04 03:45 | 3.369 | 2.0281 | 3.3281 | 1.7931 | 0 | 0 | 0 | 0
2021-10-04 04:00 | 3.4098 | 1.8152 | 3.4302 | 1.5096 | 0 | 0 | 0 | 0
2021-10-04 04:15 | 3.4506 | 1.7732 | 3.3485 | 1.3164 | 0 | 0 | 0 | 0
2021-10-04 04:30 | 3.3587 | 1.9598 | 3.3792 | 1.2303 | 0 | 0 | 0 | 0
2021-10-04 04:45 | 3.3485 | 1.9434 | 3.4608 | 1.2067 | 0 | 0 | 0 | 0
2021-10-04 05:00 | 3.4098 | 1.6872 | 3.3485 | 1.1682 | 0 | 0 | 0 | 0
2021-10-04 05:15 | 3.42 | 1.7757 | 3.4506 | 1.1456 | 0 | 0 | 0 | 0
2021-10-04 05:30 | 3.3383 | 1.7483 | 3.1546 | 1.1048 | 0 | 0 | 0 | 0
2021-10-04 05:45 | 3.3383 | 1.6665 | 1.6947 | 0.94579 | 0 | 0.039311 | 0.002335 | 0.024429
2021-10-04 06:00 | 0.51453 | 0.5402 | 0.36956 | 0.3035 | 0 | 0.082333 | 0.0055 | 0.056605
2021-10-04 06:15 | 0.30218 | 0.57984 | 0.2103 | 0.23874 | 0 | 0.12086 | 0.008664 | 0.08878
2021-10-04 06:30 | 0.38182 | 0.89182 | 0.3226 | 0.84136 | 0 | 0.17644 | 0.011829 | 0.12096
2021-10-04 06:45 | 0.17866 | 1.2247 | 0.28075 | 1.2929 | 0.004896 | 0.21324 | 0.011296 | 0.16768
2021-10-04 07:00 | 3.1648 | 1.7057 | 1.419 | 1.5258 | 0.011611 | 0.24698 | 0.009446 | 0.21832
2021-10-04 07:15 | 3.4608 | 1.504 | 0.73913 | 1.1583 | 0.018325 | 0.26789 | 0.007596 | 0.26896
2021-10-04 07:30 | 3.4098 | 1.504 | 1.1842 | 1.1104 | 0.025039 | 0.30408 | 0.005746 | 0.3196
2021-10-04 07:45 | 3.3179 | 1.504 | 0.76363 | 1.053 | 0.027888 | 0.31495 | 0.012566 | 0.32948
2021-10-04 08:00 | 3.3383 | 1.4877 | 0.5962 | 1.0291 | 0.029297 | 0.32701 | 0.022477 | 0.32736
2021-10-04 08:15 | 3.9611 | 1.5414 | 0.58395 | 1.0521 | 0.030707 | 0.36623 | 0.032389 | 0.32524
2021-10-04 08:30 | 3.5017 | 1.5545 | 0.5962 | 0.97423 | 0.032117 | 0.37348 | 0.042301 | 0.32312
2021-10-04 08:45 | 3.5527 | 1.6107 | 0.97189 | 1.7755 | 0.039225 | 0.385 | 0.066929 | 0.33355
2021-10-04 09:00 | 3.6242 | 1.6499 | 2.7666 | 1.7554 | 0.048457 | 0.34413 | 0.096816 | 0.34755
2021-10-04 09:15 | 3.7161 | 1.518 | 1.6947 | 1.3006 | 0.057689 | 0.31198 | 0.1267 | 0.36155
2021-10-04 09:30 | 3.5833 | 1.4245 | 0.49411 | 0.90262 | 0.066921 | 0.31536 | 0.15659 | 0.37555
2021-10-04 09:45 | 3.6242 | 1.082 | 0.26441 | 0.5103 | 0.12807 | 0.31926 | 0.17009 | 0.379
2021-10-04 10:00 | 3.5221 | 1.1317 | 0.27054 | 0.47384 | 0.2086 | 0.3189 | 0.17773 | 0.37959
2021-10-04 10:15 | 5.7556 | 1.5332 | 0.31444 | 0.85172 | 0.28912 | 0.35392 | 0.18536 | 0.38017
2021-10-04 10:30 | 4.7791 | 1.2324 | 0.25829 | 0.41273 | 0.36965 | 0.3548 | 0.19299 | 0.38076
2021-10-04 10:45 | 2.1439 | 1.2218 | 0.37161 | 0.39946 | 0.37594 | 0.35358 | 0.17258 | 0.38964
2021-10-04 11:00 | 0.24502 | 1.2324 | 0.44511 | 0.4104 | 0.35448 | 0.35374 | 0.1421 | 0.40058
2021-10-04 11:15 | 0.22766 | 1.2981 | 0.18785 | 0.3369 | 0.33301 | 0.34715 | 0.11163 | 0.41152
2021-10-04 11:30 | 0.37467 | 1.4197 | 0.18172 | 0.30233 | 0.31154 | 0.34731 | 0.081155 | 0.42247
2021-10-04 11:45 | 0.46553 | 1.6246 | 0.18172 | 0.94885 | 0.30829 | 0.3425 | 0.070932 | 0.43163
2021-10-04 12:00 | 2.3889 | 1.5545 | 1.2455 | 1.2249 | 0.31187 | 0.37737 | 0.067984 | 0.44048
2021-10-04 12:15 | 1.613 | 1.6464 | 1.7457 | 0.95527 | 0.31544 | 0.37396 | 0.065037 | 0.44932
2021-10-04 12:30 | 0.29096 | 1.5272 | 1.858 | 1.489 | 0.31901 | 0.37101 | 0.06209 | 0.45817
2021-10-04 12:45 | 0.25931 | 1.5489 | 1.9193 | 1.4611 | 0.35438 | 0.37451 | 0.064082 | 0.44318
2021-10-04 13:00 | 0.28483 | 1.4485 | 1.807 | 1.1322 | 0.40169 | 0.36202 | 0.067852 | 0.42092
2021-10-04 13:15 | 1.0821 | 1.5491 | 0.99639 | 1.0094 | 0.44899 | 0.36788 | 0.071621 | 0.39867
2021-10-04 13:30 | 0.77997 | 1.3817 | 0.46553 | 1.5052 | 0.49629 | 0.37261 | 0.075391 | 0.37641
2021-10-04 13:45 | 0.4982 | 1.3156 | 0.31239 | 0.956 | 0.52717 | 0.37096 | 0.0753 | 0.37014
2021-10-04 14:00 | 0.44103 | 1.3556 | 0.24093 | 0.76961 | 0.55188 | 0.37584 | 0.073818 | 0.36789
2021-10-04 14:15 | 0.30831 | 1.4753 | 0.17764 | 0.75678 | 0.5766 | 0.34875 | 0.072336 | 0.36565
2021-10-04 14:30 | 0.28381 | 1.6395 | 0.17661 | 0.76363 | 0.60131 | 0.34581 | 0.070853 | 0.36341
2021-10-04 14:45 | 0.26339 | 1.1066 | 0.18376 | 0.52285 | 0.56149 | 0.33976 | 0.059588 | 0.35339
2021-10-04 15:00 | 0.35323 | 1.3163 | 0.18274 | 0.97379 | 0.49738 | 0.36173 | 0.044789 | 0.34219
2021-10-04 15:15 | 0.38896 | 1.1319 | 0.21847 | 0.85434 | 0.43326 | 0.35593 | 0.02999 | 0.33099
2021-10-04 15:30 | 0.35527 | 1.0726 | 0.29606 | 0.52445 | 0.36914 | 0.34279 | 0.015192 | 0.31979
2021-10-04 15:45 | 1.9091 | 1.1925 | 0.27564 | 0.50272 | 0.31898 | 0.33804 | 0.009981 | 0.2772
2021-10-04 16:00 | 1.8887 | 1.2235 | 0.1807 | 0.34244 | 0.27408 | 0.30957 | 0.008238 | 0.22398
2021-10-04 16:15 | 1.7253 | 1.1871 | 0.17764 | 0.4193 | 0.22919 | 0.29425 | 0.006496 | 0.17077
2021-10-04 16:30 | 1.9601 | 1.0958 | 0.18172 | 0.41128 | 0.18429 | 0.26209 | 0.004753 | 0.11755
2021-10-04 16:45 | 1.8376 | 1.1736 | 2.8585 | 0.79717 | 0.14078 | 0.22324 | 0.003503 | 0.084673
2021-10-04 17:00 | 0.94331 | 1.2371 | 3.5119 | 0.99683 | 0.097787 | 0.16185 | 0.00243 | 0.05852
2021-10-04 17:15 | 3.0219 | 1.1039 | 3.2567 | 0.91137 | 0.054796 | 0.11108 | 0.001358 | 0.032368
2021-10-04 17:30 | 3.5425 | 1.098 | 0.33077 | 0.58876 | 0.011804 | 0.066833 | 0.000286 | 0.006215
2021-10-04 17:45 | 3.7875 | 1.0316 | 0.53495 | 0.75444 | 0 | 0.000647 | 0 | 0
2021-10-04 18:00 | 4.0019 | 1.3345 | 2.3072 | 1.6002 | 0 | 0.00039 | 0 | 0
2021-10-04 18:15 | 3.91 | 1.4527 | 1.0617 | 1.7635 | 0 | 0.00025 | 0 | 0
2021-10-04 18:30 | 3.7365 | 1.5192 | 0.2981 | 2.231 | 0 | 3.7e-05 | 0 | 0
2021-10-04 18:45 | 4.4099 | 1.6109 | 0.32056 | 2.3745 | 0 | 0 | 0 | 0
2021-10-04 19:00 | 1.2353 | 1.2621 | 0.39509 | 1.1902 | 0 | 0 | 0 | 0
2021-10-04 19:15 | 0.40223 | 1.0812 | 0.36956 | 0.91108 | 0 | 0 | 0 | 0
2021-10-04 19:30 | 0.50228 | 1.1127 | 1.7151 | 0.92435 | 0 | 0 | 0 | 0
2021-10-04 19:45 | 1.1842 | 0.96285 | 2.5727 | 0.90874 | 0 | 0 | 0 | 0
2021-10-04 20:00 | 0.67379 | 0.84436 | 0.33485 | 0.63835 | 0 | 0 | 0 | 0
2021-10-04 20:15 | 0.46144 | 0.82558 | 0.23276 | 0.71652 | 0 | 0 | 0 | 0
2021-10-04 20:30 | 0.47778 | 0.91221 | 0.17661 | 0.66956 | 0 | 0 | 0 | 0
2021-10-04 20:45 | 0.50228 | 0.87527 | 0.17559 | 0.59985 | 0 | 0 | 0 | 0
2021-10-04 21:00 | 0.38794 | 0.76553 | 0.18989 | 0.52314 | 0 | 0 | 0 | 0
2021-10-04 21:15 | 0.31546 | 0.6439 | 0.30525 | 0.43023 | 0 | 0 | 0 | 0
2021-10-04 21:30 | 0.25216 | 0.6439 | 0.27258 | 0.41128 | 0 | 0 | 0 | 0
2021-10-04 21:45 | 0.23685 | 0.75767 | 0.17559 | 0.36344 | 0 | 0 | 0 | 0
2021-10-04 22:00 | 3.1546 | 1.2547 | 0.17764 | 2.1102 | 0 | 0 | 0 | 0
2021-10-04 22:15 | 3.3077 | 1.2287 | 0.17866 | 2.1255 | 0 | 0 | 0 | 0
2021-10-04 22:30 | 3.3383 | 1.1935 | 0.27564 | 2.0764 | 0 | 0 | 0 | 0
2021-10-04 22:45 | 3.3281 | 1.1935 | 0.28177 | 2.0794 | 0 | 0 | 0 | 0
2021-10-04 23:00 | 3.3996 | 1.1015 | 0.17559 | 2.0516 | 0 | 0 | 0 | 0
2021-10-04 23:15 | 3.4608 | 1.0646 | 0.17661 | 2.0799 | 0 | 0 | 0 | 0
2021-10-04 23:30 | 3.4608 | 1.3049 | 0.24399 | 2.0781 | 0 | 0 | 0 | 0
2021-10-04 23:45 | 3.1137 | 1.2096 | 3.2362 | 2.4735 | 0 | 0 | 0 | 0
2021-10-05 | 1.5722 | 0.93922 | 3.3383 | 2.4954 | 0 | 0 | 0 | 0
2021-10-05 00:15 | 0.64112 | 0.93922 | 3.2873 | 2.4879 | 0 | 0 | 0 | 0
2021-10-05 00:30 | 0.73913 | 0.93922 | 3.3894 | 2.5015 | 0 | 0 | 0 | 0
2021-10-05 00:45 | 0.27564 | 0.93922 | 3.2873 | 2.4999 | 0 | 0 | 0 | 0
2021-10-05 01:00 | 0.30218 | 0.93922 | 3.3383 | 2.4824 | 0 | 0 | 0 | 0
2021-10-05 01:15 | 0.38998 | 0.93922 | 3.4302 | 2.5261 | 0 | 0 | 0 | 0
2021-10-05 01:30 | 0.40223 | 0.93922 | 3.3485 | 2.4787 | 0 | 0 | 0 | 0
2021-10-05 01:45 | 0.65746 | 0.93922 | 3.2975 | 2.4891 | 0 | 0 | 0 | 0
2021-10-05 02:00 | 0.39611 | 0.95669 | 3.2975 | 2.5148 | 0 | 0 | 0 | 0
2021-10-05 02:15 | 0.27156 | 0.98269 | 3.3894 | 2.5473 | 0 | 0 | 0 | 0
2021-10-05 02:30 | 0.26645 | 0.85849 | 3.3587 | 2.5167 | 0 | 0 | 0 | 0
2021-10-05 02:45 | 0.34302 | 0.90562 | 3.369 | 2.4888 | 0 | 0 | 0 | 0
2021-10-05 03:00 | 0.40019 | 0.95981 | 3.5119 | 2.2743 | 0 | 0 | 0 | 0
2021-10-05 03:15 | 0.40325 | 0.95981 | 3.4302 | 2.1617 | 0 | 0 | 0 | 0
2021-10-05 03:30 | 0.40121 | 0.89099 | 3.3587 | 1.989 | 0 | 0 | 0 | 0
2021-10-05 03:45 | 0.35527 | 0.87791 | 3.369 | 1.7698 | 0 | 0 | 0 | 0
2021-10-05 04:00 | 0.28687 | 0.91124 | 3.4098 | 1.5184 | 0 | 0 | 0 | 0
2021-10-05 04:15 | 0.28177 | 1.0569 | 3.4506 | 1.3324 | 0 | 0 | 0 | 0
2021-10-05 04:30 | 0.342 | 0.74074 | 3.3587 | 1.223 | 0 | 0 | 0 | 0
2021-10-05 04:45 | 0.39611 | 0.78755 | 3.3485 | 1.2052 | 0 | 0 | 0 | 0
2021-10-05 05:00 | 0.27156 | 0.8293 | 3.4098 | 1.1857 | 0 | 0 | 0 | 0
2021-10-05 05:15 | 0.27462 | 1.0228 | 3.42 | 1.1646 | 0 | 0 | 0 | 0
2021-10-05 05:30 | 0.29096 | 0.98106 | 3.3383 | 1.1106 | 0 | 0 | 0 | 0
2021-10-05 05:45 | 0.39611 | 0.70939 | 3.3383 | 0.94141 | 0.025653 | 0.019698 | 0 | 0.022225
2021-10-05 06:00 | 0.27973 | 0.75003 | 0.51453 | 0.32377 | 0.061218 | 0.04141 | 0 | 0.051599
2021-10-05 06:15 | 0.2685 | 0.73862 | 0.30218 | 0.25741 | 0.096782 | 0.075075 | 0 | 0.080973
2021-10-05 06:30 | 2.8279 | 0.75187 | 0.38182 | 0.85026 | 0.13235 | 0.092854 | 0 | 0.11035
2021-10-05 06:45 | 1.9193 | 0.78393 | 0.17866 | 1.2878 | 0.15952 | 0.131 | 0.004896 | 0.14453
2021-10-05 07:00 | 1.4599 | 1.1582 | 3.1648 | 1.52 | 0.18344 | 0.15556 | 0.011611 | 0.18006
2021-10-05 07:15 | 0.71054 | 0.88532 | 3.4608 | 1.1612 | 0.20736 | 0.17519 | 0.018325 | 0.21559
2021-10-05 07:30 | 0.5962 | 0.9485 | 3.4098 | 1.1207 | 0.23128 | 0.22655 | 0.025039 | 0.25112
2021-10-05 07:45 | 0.56354 | 0.92693 | 3.3179 | 1.0486 | 0.30568 | 0.23897 | 0.027888 | 0.26599
2021-10-05 08:00 | 0.42061 | 0.91951 | 3.3383 | 0.99844 | 0.39965 | 0.24496 | 0.029297 | 0.27425
2021-10-05 08:15 | 0.46144 | 0.9598 | 3.9611 | 1.0623 | 0.49362 | 0.25687 | 0.030707 | 0.28252
2021-10-05 08:30 | 0.42878 | 0.87899 | 3.5017 | 0.95235 | 0.58759 | 0.28815 | 0.032117 | 0.29078
2021-10-05 08:45 | 0.35731 | 0.9203 | 3.5527 | 1.5433 | 0.60367 | 0.32871 | 0.039225 | 0.29395
2021-10-05 09:00 | 0.3665 | 0.91678 | 3.6242 | 1.6837 | 0.58948 | 0.34142 | 0.048457 | 0.29597
2021-10-05 09:15 | 0.3859 | 0.99465 | 3.7161 | 1.2478 | 0.5753 | 0.35775 | 0.057689 | 0.29799
2021-10-05 09:30 | 0.39509 | 0.91612 | 3.5833 | 1.0062 | 0.56112 | 0.36506 | 0.066921 | 0.30001
2021-10-05 09:45 | 0.41653 | 0.85999 | 3.6242 | 0.92245 | 0.5761 | 0.36905 | 0.12807 | 0.32137
2021-10-05 10:00 | 0.39202 | 0.85999 | 3.5221 | 0.90466 | 0.60242 | 0.36863 | 0.2086 | 0.34874
2021-10-05 10:15 | 0.33485 | 0.82193 | 5.7556 | 1.6255 | 0.62874 | 0.3395 | 0.28912 | 0.37612
2021-10-05 10:30 | 0.23481 | 0.79139 | 4.7791 | 1.0664 | 0.65506 | 0.33529 | 0.36965 | 0.40349
2021-10-05 10:45 | 0.22664 | 0.87844 | 2.1439 | 0.67715 | 0.6508 | 0.33917 | 0.37594 | 0.40942
2021-10-05 11:00 | 0.22562 | 0.8026 | 0.24502 | 0.41594 | 0.63462 | 0.33933 | 0.35448 | 0.40822
2021-10-05 11:15 | 0.22562 | 0.77938 | 0.22766 | 0.34069 | 0.61843 | 0.33948 | 0.33301 | 0.40701
2021-10-05 11:30 | 0.28993 | 0.80879 | 0.37467 | 0.32829 | 0.60225 | 0.31957 | 0.31154 | 0.4058
2021-10-05 11:45 | 0.34098 | 0.80056 | 0.46553 | 0.98779 | 0.50638 | 0.33865 | 0.30829 | 0.41931
2021-10-05 12:00 | 0.22562 | 1.0058 | 2.3889 | 1.1578 | 0.3794 | 0.33293 | 0.31187 | 0.43728
2021-10-05 12:15 | 0.22766 | 0.86109 | 1.613 | 0.69567 | 0.25243 | 0.3127 | 0.31544 | 0.45524
2021-10-05 12:30 | 0.22868 | 0.81488 | 0.29096 | 1.0348 | 0.12545 | 0.31023 | 0.31901 | 0.47321
2021-10-05 12:45 | 0.27258 | 0.87853 | 0.25931 | 0.85128 | 0.10125 | 0.31316 | 0.35438 | 0.46595
2021-10-05 13:00 | 0.34098 | 0.89902 | 0.28483 | 0.61866 | 0.11723 | 0.33477 | 0.40169 | 0.4515
2021-10-05 13:15 | 0.24093 | 1.0139 | 1.0821 | 0.5103 | 0.13321 | 0.34181 | 0.44899 | 0.43705
2021-10-05 13:30 | 0.22766 | 0.91058 | 0.77997 | 0.74088 | 0.14919 | 0.3462 | 0.49629 | 0.4226
2021-10-05 13:45 | 0.22664 | 1.0402 | 0.4982 | 0.52693 | 0.13182 | 0.32093 | 0.52717 | 0.41244
2021-10-05 14:00 | 0.24706 | 1.0012 | 0.44103 | 0.32508 | 0.10138 | 0.34181 | 0.55188 | 0.40285
2021-10-05 14:15 | 0.29504 | 0.99621 | 0.30831 | 0.29475 | 0.070944 | 0.34158 | 0.5766 | 0.39327
2021-10-05 14:30 | 0.22051 | 0.99621 | 0.28381 | 0.2981 | 0.040506 | 0.3387 | 0.60131 | 0.38369
2021-10-05 14:45 | 0.2736 | 0.85142 | 0.26339 | 0.30671 | 0.029323 | 0.34684 | 0.56149 | 0.37429
2021-10-05 15:00 | 0.33485 | 0.99313 | 0.35323 | 0.48026 | 0.025693 | 0.34881 | 0.49738 | 0.36498
2021-10-05 15:15 | 0.22358 | 0.9957 | 0.38896 | 0.59635 | 0.022064 | 0.26883 | 0.43326 | 0.35567
2021-10-05 15:30 | 0.21847 | 0.98987 | 0.35527 | 0.4279 | 0.018434 | 0.26297 | 0.36914 | 0.34636
2021-10-05 15:45 | 0.22256 | 0.82157 | 1.9091 | 0.57856 | 0.030126 | 0.241 | 0.31898 | 0.3023
2021-10-05 16:00 | 0.22358 | 0.8821 | 1.8887 | 0.53174 | 0.04784 | 0.21732 | 0.27408 | 0.2469
2021-10-05 16:15 | 0.34506 | 0.87515 | 1.7253 | 0.57418 | 0.065553 | 0.21172 | 0.22919 | 0.1915
2021-10-05 16:30 | 0.26135 | 0.90231 | 1.9601 | 0.62712 | 0.083267 | 0.19201 | 0.18429 | 0.13609
2021-10-05 16:45 | 0.21745 | 0.86014 | 1.8376 | 0.98152 | 0.072437 | 0.13547 | 0.14078 | 0.099261
2021-10-05 17:00 | 0.30014 | 0.85883 | 0.94331 | 1.0657 | 0.050371 | 0.1107 | 0.097787 | 0.068684
2021-10-05 17:15 | 0.26645 | 1.181 | 3.0219 | 1.2748 | 0.028306 | 0.06903 | 0.054796 | 0.038107
2021-10-05 17:30 | 0.37569 | 0.86765 | 3.5425 | 0.91545 | 0.00624 | 0.031052 | 0.011804 | 0.007529
2021-10-05 17:45 | 0.293 | 0.89888 | 3.7875 | 0.97175 | 0 | 0.001553 | 0 | 0
2021-10-05 18:00 | 2.6339 | 1.1068 | 4.0019 | 1.9254 | 0 | 0.00101 | 0 | 0
2021-10-05 18:15 | 2.8279 | 1.5238 | 3.91 | 2.1774 | 0 | 0.00025 | 0 | 0
2021-10-05 18:30 | 2.981 | 1.9578 | 3.7365 | 2.3113 | 0 | 3.7e-05 | 0 | 0
2021-10-05 18:45 | 7.0433 | 1.7847 | 4.4099 | 2.9374 | 0 | 0 | 0 | 0
2021-10-05 19:00 | 1.7457 | 1.8097 | 1.2353 | 1.2471 | 0 | 0 | 0 | 0
2021-10-05 19:15 | 3.4813 | 1.5549 | 0.40223 | 0.8752 | 0 | 0 | 0 | 0
2021-10-05 19:30 | 2.8993 | 1.1197 | 0.50228 | 0.89926 | 0 | 0 | 0 | 0
2021-10-05 19:45 | 0.97598 | 1.1462 | 1.1842 | 1.0126 | 0 | 0 | 0 | 0
2021-10-05 20:00 | 2.8687 | 0.92835 | 0.67379 | 0.65702 | 0 | 0 | 0 | 0
2021-10-05 20:15 | 1.6845 | 0.91916 | 0.46144 | 0.71886 | 0 | 0 | 0 | 0
2021-10-05 20:30 | 0.45328 | 0.92078 | 0.47778 | 0.66839 | 0 | 0 | 0 | 0
2021-10-05 20:45 | 0.45328 | 0.90152 | 0.50228 | 0.60918 | 0 | 0 | 0 | 0
2021-10-05 21:00 | 0.49003 | 0.81707 | 0.38794 | 0.51147 | 0 | 0 | 0 | 0
2021-10-05 21:15 | 0.50228 | 0.76949 | 0.31546 | 0.42425 | 0 | 0 | 0 | 0
2021-10-05 21:30 | 0.4737 | 0.75624 | 0.25216 | 0.4174 | 0 | 0 | 0 | 0
2021-10-05 21:45 | 0.53495 | 0.77668 | 0.23685 | 0.36986 | 0 | 0 | 0 | 0
2021-10-05 22:00 | 3.4302 | 1.6763 | 3.1546 | 2.5339 | 0 | 0 | 0 | 0
2021-10-05 22:15 | 3.4302 | 1.7728 | 3.3077 | 2.5579 | 0 | 0 | 0 | 0
2021-10-05 22:30 | 3.3587 | 1.7794 | 3.3383 | 2.5083 | 0 | 0 | 0 | 0
2021-10-05 22:45 | 3.3077 | 1.7794 | 3.3281 | 2.5111 | 0 | 0 | 0 | 0
2021-10-05 23:00 | 3.3179 | 1.7836 | 3.3996 | 2.4672 | 0 | 0 | 0 | 0
2021-10-05 23:15 | 3.3281 | 1.7744 | 3.4608 | 2.5124 | 0 | 0 | 0 | 0
2021-10-05 23:30 | 3.3587 | 1.7744 | 3.4608 | 2.5461 | 0 | 0 | 0 | 0
2021-10-05 23:45 | 3.3485 | 2.0862 | 3.1137 | 2.8906 | 0 | 0 | 0 | 0
2021-10-06 | 3.4098 | 2.2654 | 1.5722 | 2.6922 | 0 | 0 | 0 | 0
2021-10-06 00:15 | 3.4404 | 2.2451 | 0.64112 | 2.5343 | 0 | 0 | 0 | 0
2021-10-06 00:30 | 3.4608 | 2.2793 | 0.73913 | 2.5623 | 0 | 0 | 0 | 0
2021-10-06 00:45 | 3.4608 | 2.1442 | 0.27564 | 2.4943 | 0 | 0 | 0 | 0
2021-10-06 01:00 | 3.4608 | 2.1442 | 0.30218 | 2.4853 | 0 | 0 | 0 | 0
2021-10-06 01:15 | 3.4608 | 2.1826 | 0.38998 | 2.5549 | 0 | 0 | 0 | 0
2021-10-06 01:30 | 3.4608 | 2.1442 | 0.40223 | 2.5048 | 0 | 0 | 0 | 0
2021-10-06 01:45 | 3.4813 | 2.1406 | 0.65746 | 2.5499 | 0 | 0 | 0 | 0
2021-10-06 02:00 | 3.471 | 1.9731 | 0.39611 | 2.5447 | 0 | 0 | 0 | 0
2021-10-06 02:15 | 3.4608 | 2.1678 | 0.27156 | 2.5476 | 0 | 0 | 0 | 0
2021-10-06 02:30 | 3.471 | 2.0165 | 0.26645 | 2.5204 | 0 | 0 | 0 | 0
2021-10-06 02:45 | 3.471 | 2.0165 | 0.34302 | 2.5108 | 0 | 0 | 0 | 0
2021-10-06 03:00 | 3.4608 | 2.0115 | 0.40019 | 2.3002 | 0 | 0 | 0 | 0
2021-10-06 03:15 | 3.471 | 1.9473 | 0.40325 | 2.186 | 0 | 0 | 0 | 0
2021-10-06 03:30 | 2.7564 | 1.6482 | 0.40121 | 2.0195 | 0 | 0 | 0 | 0
2021-10-06 03:45 | 1.4088 | 1.4708 | 0.35527 | 1.7861 | 0 | 0 | 0 | 0
2021-10-06 04:00 | 0.75955 | 1.0948 | 0.28687 | 1.5274 | 0 | 0 | 0 | 0
2021-10-06 04:15 | 0.72279 | 1.1198 | 0.28177 | 1.3466 | 0 | 0 | 0 | 0
2021-10-06 04:30 | 0.30423 | 0.88095 | 0.342 | 1.2442 | 0 | 0 | 0 | 0
2021-10-06 04:45 | 0.29912 | 0.81294 | 0.39611 | 1.2166 | 0 | 0 | 0 | 0
2021-10-06 05:00 | 0.30014 | 0.78713 | 0.27156 | 1.1917 | 0 | 0 | 0 | 0
2021-10-06 05:15 | 0.29912 | 0.79832 | 0.27462 | 1.1777 | 0 | 0 | 0 | 0
2021-10-06 05:30 | 0.30218 | 0.79356 | 0.29096 | 1.1262 | 0 | 0 | 0 | 0
2021-10-06 05:45 | 0.29912 | 0.74176 | 0.39611 | 0.96096 | 0.002324 | 0.014562 | 0.025653 | 0.025787
2021-10-06 06:00 | 0.29606 | 0.57788 | 0.27973 | 0.3369 | 0.005584 | 0.040374 | 0.061218 | 0.06011
2021-10-06 06:15 | 0.29708 | 0.57249 | 0.2685 | 0.26777 | 0.008844 | 0.079611 | 0.096782 | 0.094433
2021-10-06 06:30 | 0.42061 | 0.88347 | 2.8279 | 1.1947 | 0.012104 | 0.13123 | 0.13235 | 0.12876
2021-10-06 06:45 | 0.56354 | 1.0086 | 1.9193 | 1.5156 | 0.029207 | 0.1302 | 0.15952 | 0.16287
2021-10-06 07:00 | 1.7049 | 1.4376 | 1.4599 | 1.6276 | 0.05189 | 0.15306 | 0.18344 | 0.19679
2021-10-06 07:15 | 1.317 | 1.1207 | 0.71054 | 1.2058 | 0.074574 | 0.16898 | 0.20736 | 0.23071
2021-10-06 07:30 | 0.69013 | 1.1194 | 0.5962 | 1.1265 | 0.097257 | 0.19215 | 0.23128 | 0.26463
2021-10-06 07:45 | 0.89022 | 1.0749 | 0.56354 | 1.0445 | 0.10998 | 0.20698 | 0.30568 | 0.29112
2021-10-06 08:00 | 0.74321 | 1.0699 | 0.42061 | 0.99319 | 0.11868 | 0.22947 | 0.39965 | 0.31551
2021-10-06 08:15 | 0.67379 | 1.1016 | 0.46144 | 1.0635 | 0.12738 | 0.23303 | 0.49362 | 0.33991
2021-10-06 08:30 | 0.76771 | 1.0604 | 0.42878 | 0.96168 | 0.13608 | 0.23575 | 0.58759 | 0.36431
2021-10-06 08:45 | 2.5624 | 1.3808 | 0.35731 | 1.5398 | 0.14287 | 0.28708 | 0.60367 | 0.36794
2021-10-06 09:00 | 3.3383 | 1.7095 | 0.3665 | 1.682 | 0.14887 | 0.30523 | 0.58948 | 0.36479
2021-10-06 09:15 | 1.3476 | 1.1498 | 0.3859 | 1.2499 | 0.15488 | 0.32969 | 0.5753 | 0.36164
2021-10-06 09:30 | 0.84122 | 0.99178 | 0.39509 | 1.007 | 0.16089 | 0.34656 | 0.56112 | 0.35849
2021-10-06 09:45 | 0.51453 | 1.1459 | 0.41653 | 0.90729 | 0.18592 | 0.37592 | 0.5761 | 0.3712
2021-10-06 10:00 | 0.54312 | 1.1459 | 0.39202 | 0.88833 | 0.21866 | 0.37697 | 0.60242 | 0.38936
2021-10-06 10:15 | 0.60437 | 1.2486 | 0.33485 | 1.6133 | 0.25139 | 0.37802 | 0.62874 | 0.40753
2021-10-06 10:30 | 0.55945 | 1.1199 | 0.23481 | 1.0437 | 0.28413 | 0.36992 | 0.65506 | 0.42569
2021-10-06 10:45 | 0.49411 | 1.278 | 0.22664 | 0.65162 | 0.27744 | 0.37271 | 0.6508 | 0.42891
2021-10-06 11:00 | 0.48595 | 0.99365 | 0.22562 | 0.37992 | 0.25475 | 0.38419 | 0.63462 | 0.42641
2021-10-06 11:15 | 0.49003 | 0.97555 | 0.22562 | 0.33587 | 0.23206 | 0.38308 | 0.61843 | 0.42391
2021-10-06 11:30 | 0.44103 | 0.9976 | 0.28993 | 0.34287 | 0.20938 | 0.3817 | 0.60225 | 0.42141
2021-10-06 11:45 | 2.8177 | 1.3846 | 0.34098 | 1.0067 | 0.19859 | 0.38222 | 0.50638 | 0.41971
2021-10-06 12:00 | 1.9499 | 1.0728 | 0.22562 | 1.1472 | 0.19264 | 0.37925 | 0.3794 | 0.41731
2021-10-06 12:15 | 0.38488 | 1.1875 | 0.22766 | 0.70092 | 0.18669 | 0.37312 | 0.25243 | 0.4149
2021-10-06 12:30 | 2.4195 | 1.1075 | 0.22868 | 1.0412 | 0.18074 | 0.37018 | 0.12545 | 0.4125
2021-10-06 12:45 | 2.2256 | 1.2429 | 0.27258 | 0.85289 | 0.17427 | 0.37354 | 0.10125 | 0.40436
2021-10-06 13:00 | 0.89431 | 1.248 | 0.34098 | 0.62785 | 0.16758 | 0.38168 | 0.11723 | 0.39615
2021-10-06 13:15 | 0.33281 | 1.3136 | 0.24093 | 0.51584 | 0.16089 | 0.38678 | 0.13321 | 0.38794
2021-10-06 13:30 | 2.7258 | 1.4798 | 0.22766 | 0.7403 | 0.1542 | 0.3885 | 0.14919 | 0.37973
2021-10-06 13:45 | 1.6334 | 1.3695 | 0.22664 | 0.52051 | 0.1452 | 0.38678 | 0.13182 | 0.36618
2021-10-06 14:00 | 0.40325 | 1.3042 | 0.24706 | 0.3226 | 0.13525 | 0.38344 | 0.10138 | 0.34994
2021-10-06 14:15 | 0.40836 | 1.48 | 0.29504 | 0.31108 | 0.12531 | 0.38023 | 0.070944 | 0.3337
2021-10-06 14:30 | 0.40836 | 1.2498 | 0.22051 | 0.30262 | 0.11536 | 0.37569 | 0.040506 | 0.31746
2021-10-06 14:45 | 0.41653 | 0.92944 | 0.2736 | 0.30583 | 0.095015 | 0.37034 | 0.029323 | 0.30918
2021-10-06 15:00 | 0.42061 | 0.95601 | 0.33485 | 0.33267 | 0.070417 | 0.35934 | 0.025693 | 0.30352
2021-10-06 15:15 | 0.51045 | 0.99723 | 0.22358 | 0.3439 | 0.045819 | 0.35358 | 0.022064 | 0.29786
2021-10-06 15:30 | 0.62887 | 1.0352 | 0.21847 | 0.36636 | 0.021222 | 0.34782 | 0.018434 | 0.29221
2021-10-06 15:45 | 0.40427 | 1.1354 | 0.22256 | 0.56776 | 0.052881 | 0.31586 | 0.030126 | 0.25652
2021-10-06 16:00 | 0.32362 | 1.1451 | 0.22358 | 0.52591 | 0.10756 | 0.28528 | 0.04784 | 0.21107
2021-10-06 16:15 | 0.31035 | 1.1287 | 0.34506 | 0.57214 | 0.16223 | 0.25909 | 0.065553 | 0.16563
2021-10-06 16:30 | 0.32669 | 1.1716 | 0.26135 | 0.60262 | 0.21691 | 0.24002 | 0.083267 | 0.12019
2021-10-06 16:45 | 0.42469 | 1.1906 | 0.21745 | 0.97204 | 0.19152 | 0.20535 | 0.072437 | 0.088541
2021-10-06 17:00 | 0.64112 | 0.93004 | 0.30014 | 1.0584 | 0.13333 | 0.14783 | 0.050371 | 0.061344
2021-10-06 17:15 | 0.54312 | 1.1703 | 0.26645 | 1.2741 | 0.075131 | 0.08272 | 0.028306 | 0.034147
2021-10-06 17:30 | 0.39202 | 1.2556 | 0.37569 | 0.93879 | 0.016936 | 0.034415 | 0.00624 | 0.006949
2021-10-06 17:45 | 0.39304 | 1.244 | 0.293 | 0.97321 | 0 | 0.000944 | 0 | 0
2021-10-06 18:00 | 0.89431 | 1.5512 | 2.6339 | 2.2638 | 0 | 0.000607 | 0 | 0
2021-10-06 18:15 | 3.0014 | 1.5902 | 2.8279 | 2.4049 | 0 | 0.000292 | 0 | 0
2021-10-06 18:30 | 1.4497 | 1.5545 | 2.981 | 2.0733 | 0 | 0.00024 | 0 | 0
2021-10-06 18:45 | 1.8887 | 1.4722 | 7.0433 | 3.3169 | 0 | 0 | 0 | 0
2021-10-06 19:00 | 1.4803 | 1.0776 | 1.7457 | 1.1173 | 0 | 0 | 0 | 0
2021-10-06 19:15 | 1.4599 | 1.1429 | 3.4813 | 0.98604 | 0 | 0 | 0 | 0
2021-10-06 19:30 | 0.64112 | 1.0431 | 2.8993 | 1.0247 | 0 | 0 | 0 | 0
2021-10-06 19:45 | 0.63296 | 1.0761 | 0.97598 | 0.977 | 0 | 0 | 0 | 0
2021-10-06 20:00 | 1.5211 | 1.106 | 2.8687 | 1.0021 | 0 | 0 | 0 | 0
2021-10-06 20:15 | 2.2868 | 1.0833 | 1.6845 | 0.89708 | 0 | 0 | 0 | 0
2021-10-06 20:30 | 2.2868 | 1.126 | 0.45328 | 0.66723 | 0 | 0 | 0 | 0
2021-10-06 20:45 | 1.9397 | 1.0494 | 0.45328 | 0.60102 | 0 | 0 | 0 | 0
2021-10-06 21:00 | 0.98006 | 0.73604 | 0.49003 | 0.49747 | 0 | 0 | 0 | 0
2021-10-06 21:15 | 0.56354 | 0.66703 | 0.50228 | 0.41434 | 0 | 0 | 0 | 0
2021-10-06 21:30 | 0.46144 | 0.63793 | 0.4737 | 0.39815 | 0 | 0 | 0 | 0
2021-10-06 21:45 | 0.34915 | 0.66348 | 0.53495 | 0.35819 | 0 | 0 | 0 | 0
2021-10-06 22:00 | 1.0311 | 1.6387 | 3.4302 | 2.5382 | 0 | 0 | 0 | 0
2021-10-06 22:15 | 0.53495 | 1.298 | 3.4302 | 2.5506 | 0 | 0 | 0 | 0
2021-10-06 22:30 | 0.33587 | 1.2128 | 3.3587 | 2.5054 | 0 | 0 | 0 | 0
2021-10-06 22:45 | 0.33894 | 1.2128 | 3.3077 | 2.4936 | 0 | 0 | 0 | 0
2021-10-06 23:00 | 0.33179 | 1.2128 | 3.3179 | 2.4526 | 0 | 0 | 0 | 0
2021-10-06 23:15 | 0.33077 | 1.2128 | 3.3281 | 2.4862 | 0 | 0 | 0 | 0
2021-10-06 23:30 | 0.32567 | 1.2128 | 3.3587 | 2.4965 | 0 | 0 | 0 | 0
2021-10-06 23:45 | 0.32669 | 1.1793 | 3.3485 | 2.8731 | 0 | 0 | 0 | 0
2021-10-07 | 0.32669 | 1.1056 | 3.4098 | 2.6922 | 0 | 0 | 0 | 0
2021-10-07 00:15 | 0.32567 | 1.2132 | 3.4404 | 2.5343 | 0 | 0 | 0 | 0
2021-10-07 00:30 | 0.32158 | 1.0979 | 3.4608 | 2.5623 | 0 | 0 | 0 | 0
2021-10-07 00:45 | 0.31954 | 1.0734 | 3.4608 | 2.4943 | 0 | 0 | 0 | 0
2021-10-07 01:00 | 0.32158 | 0.92684 | 3.4608 | 2.4853 | 0 | 0 | 0 | 0
2021-10-07 01:15 | 0.3226 | 1.0979 | 3.4608 | 2.5549 | 0 | 0 | 0 | 0
2021-10-07 01:30 | 0.3175 | 1.0979 | 3.4608 | 2.5048 | 0 | 0 | 0 | 0
2021-10-07 01:45 | 0.31648 | 1.0979 | 3.4813 | 2.5499 | 0 | 0 | 0 | 0
2021-10-07 02:00 | 0.31648 | 1.0581 | 3.471 | 2.5447 | 0 | 0 | 0 | 0
2021-10-07 02:15 | 0.31852 | 0.94709 | 3.4608 | 2.5476 | 0 | 0 | 0 | 0
2021-10-07 02:30 | 0.3175 | 0.88701 | 3.471 | 2.5204 | 0 | 0 | 0 | 0
2021-10-07 02:45 | 0.31648 | 0.95095 | 3.471 | 2.5108 | 0 | 0 | 0 | 0
2021-10-07 03:00 | 0.31648 | 1.0928 | 3.4608 | 2.3002 | 0 | 0 | 0 | 0
2021-10-07 03:15 | 0.31444 | 1.056 | 3.471 | 2.186 | 0 | 0 | 0 | 0
2021-10-07 03:30 | 0.31852 | 1.0507 | 2.7564 | 2.0195 | 0 | 0 | 0 | 0
2021-10-07 03:45 | 0.31648 | 1.005 | 1.4088 | 1.7861 | 0 | 0 | 0 | 0
2021-10-07 04:00 | 0.31648 | 0.97518 | 0.75955 | 1.5274 | 0 | 0 | 0 | 0
2021-10-07 04:15 | 0.31444 | 1.0592 | 0.72279 | 1.3466 | 0 | 0 | 0 | 0
2021-10-07 04:30 | 0.31239 | 0.99752 | 0.30423 | 1.2442 | 0 | 0 | 0 | 0
2021-10-07 04:45 | 0.31648 | 0.9801 | 0.29912 | 1.2166 | 0 | 0 | 0 | 0
2021-10-07 05:00 | 0.31954 | 0.88612 | 0.30014 | 1.1917 | 0 | 0 | 0 | 0
2021-10-07 05:15 | 0.31137 | 0.90803 | 0.29912 | 1.1777 | 0 | 0 | 0 | 0
2021-10-07 05:30 | 0.31444 | 0.94172 | 0.30218 | 1.1262 | 0 | 0 | 0 | 0
2021-10-07 05:45 | 0.31648 | 0.92594 | 0.29912 | 0.96096 | 0.007549 | 0.017897 | 0.002324 | 0.02349
2021-10-07 06:00 | 0.32056 | 0.55028 | 0.29606 | 0.3369 | 0.018258 | 0.051192 | 0.005584 | 0.054867
2021-10-07 06:15 | 0.31546 | 0.59761 | 0.29708 | 0.26777 | 0.028967 | 0.088411 | 0.008844 | 0.086244
2021-10-07 06:30 | 1.562 | 1.3076 | 0.42061 | 1.1947 | 0.039676 | 0.11791 | 0.012104 | 0.11762
2021-10-07 06:45 | 2.7462 | 1.698 | 0.56354 | 1.5156 | 0.10959 | 0.14815 | 0.029207 | 0.14876
2021-10-07 07:00 | 1.1128 | 1.6036 | 1.7049 | 1.6276 | 0.20433 | 0.17575 | 0.05189 | 0.1799
2021-10-07 07:15 | 0.91881 | 1.286 | 1.317 | 1.2058 | 0.29907 | 0.22077 | 0.074574 | 0.21104
2021-10-07 07:30 | 0.7963 | 1.1982 | 0.69013 | 1.1265 | 0.39381 | 0.26138 | 0.097257 | 0.24218
2021-10-07 07:45 | 0.60845 | 1.1944 | 0.89022 | 1.0445 | 0.3733 | 0.29597 | 0.10998 | 0.26325
2021-10-07 08:00 | 0.66562 | 1.1692 | 0.74321 | 0.99319 | 0.30438 | 0.30537 | 0.11868 | 0.28129
2021-10-07 08:15 | 0.66154 | 1.2936 | 0.67379 | 1.0635 | 0.23546 | 0.31335 | 0.12738 | 0.29934
2021-10-07 08:30 | 0.45736 | 1.1104 | 0.76771 | 0.96168 | 0.16654 | 0.33168 | 0.13608 | 0.31738
2021-10-07 08:45 | 0.51045 | 1.2559 | 2.5624 | 1.5398 | 0.15259 | 0.32086 | 0.14287 | 0.33099
2021-10-07 09:00 | 0.57578 | 1.2374 | 3.3383 | 1.682 | 0.16177 | 0.32306 | 0.14887 | 0.34268
2021-10-07 09:15 | 0.51453 | 1.1959 | 1.3476 | 1.2499 | 0.17096 | 0.33847 | 0.15488 | 0.35437
2021-10-07 09:30 | 0.5717 | 1.1129 | 0.84122 | 1.007 | 0.18014 | 0.34076 | 0.16089 | 0.36607
2021-10-07 09:45 | 0.51862 | 1.0882 | 0.51453 | 0.90729 | 0.17386 | 0.35396 | 0.18592 | 0.38713
2021-10-07 10:00 | 0.51453 | 1.0882 | 0.54312 | 0.88833 | 0.16106 | 0.35642 | 0.21866 | 0.41199
2021-10-07 10:15 | 0.59212 | 1.2291 | 0.60437 | 1.6133 | 0.14826 | 0.35573 | 0.25139 | 0.43685
2021-10-07 10:30 | 0.55537 | 1.0261 | 0.55945 | 1.0437 | 0.13546 | 0.35817 | 0.28413 | 0.46171
2021-10-07 10:45 | 0.42469 | 1.1262 | 0.49411 | 0.65162 | 0.12344 | 0.35756 | 0.27744 | 0.46327
2021-10-07 11:00 | 0.42469 | 0.70918 | 0.48595 | 0.37992 | 0.11176 | 0.35629 | 0.25475 | 0.45601
2021-10-07 11:15 | 0.42878 | 0.71113 | 0.49003 | 0.33587 | 0.10008 | 0.35501 | 0.23206 | 0.44875
2021-10-07 11:30 | 0.23072 | 0.76445 | 0.44103 | 0.34287 | 0.088392 | 0.35374 | 0.20938 | 0.44149
2021-10-07 11:45 | 0.17866 | 1.0402 | 2.8177 | 1.0067 | 0.15521 | 0.35128 | 0.19859 | 0.42426
2021-10-07 12:00 | 0.19091 | 0.95609 | 1.9499 | 1.1472 | 0.25523 | 0.34855 | 0.19264 | 0.40326
2021-10-07 12:15 | 0.29606 | 1.065 | 0.38488 | 0.70092 | 0.35525 | 0.34582 | 0.18669 | 0.38225
2021-10-07 12:30 | 0.28585 | 1.0144 | 2.4195 | 1.0412 | 0.45526 | 0.35036 | 0.18074 | 0.36125
2021-10-07 12:45 | 0.28279 | 1.0277 | 2.2256 | 0.85289 | 0.47441 | 0.33194 | 0.17427 | 0.36156
2021-10-07 13:00 | 0.27156 | 1.0631 | 0.89431 | 0.62785 | 0.45931 | 0.3509 | 0.16758 | 0.36994
2021-10-07 13:15 | 0.18274 | 0.84301 | 0.33281 | 0.51584 | 0.44422 | 0.35547 | 0.16089 | 0.37833
2021-10-07 13:30 | 0.18274 | 1.0277 | 2.7258 | 0.7403 | 0.42912 | 0.36003 | 0.1542 | 0.38672
2021-10-07 13:45 | 0.1807 | 0.81265 | 1.6334 | 0.52051 | 0.35986 | 0.35844 | 0.1452 | 0.37429
2021-10-07 14:00 | 0.17866 | 0.75238 | 0.40325 | 0.3226 | 0.26763 | 0.3388 | 0.13525 | 0.35446
2021-10-07 14:15 | 0.17968 | 0.7116 | 0.40836 | 0.31108 | 0.1754 | 0.3328 | 0.12531 | 0.33464
2021-10-07 14:30 | 0.18376 | 0.7116 | 0.40836 | 0.30262 | 0.083174 | 0.24379 | 0.11536 | 0.31481
2021-10-07 14:45 | 0.25625 | 0.7116 | 0.41653 | 0.30583 | 0.099067 | 0.24029 | 0.095015 | 0.30145
2021-10-07 15:00 | 0.28381 | 0.7851 | 0.42061 | 0.33267 | 0.1609 | 0.23167 | 0.070417 | 0.29009
2021-10-07 15:15 | 0.27973 | 0.76315 | 0.51045 | 0.3439 | 0.22274 | 0.22936 | 0.045819 | 0.27873
2021-10-07 15:30 | 0.25216 | 0.76007 | 0.62887 | 0.36636 | 0.28458 | 0.24799 | 0.021222 | 0.26737
2021-10-07 15:45 | 0.21235 | 0.95044 | 0.40427 | 0.56776 | 0.31039 | 0.23322 | 0.052881 | 0.24021
2021-10-07 16:00 | 0.21235 | 0.82862 | 0.32362 | 0.52591 | 0.32087 | 0.24512 | 0.10756 | 0.20847
2021-10-07 16:15 | 0.20724 | 0.96567 | 0.31035 | 0.57214 | 0.33135 | 0.23354 | 0.16223 | 0.17672
2021-10-07 16:30 | 0.2103 | 0.96567 | 0.32669 | 0.60262 | 0.34183 | 0.21878 | 0.21691 | 0.14497
2021-10-07 16:45 | 0.21235 | 1.0453 | 0.42469 | 0.97204 | 0.2845 | 0.18387 | 0.19152 | 0.112
2021-10-07 17:00 | 0.32771 | 1.1362 | 0.64112 | 1.0584 | 0.19827 | 0.11432 | 0.13333 | 0.077694
2021-10-07 17:15 | 0.30933 | 1.2649 | 0.54312 | 1.2741 | 0.11204 | 0.07122 | 0.075131 | 0.043391
2021-10-07 17:30 | 0.31137 | 1.0361 | 0.39202 | 0.93879 | 0.025804 | 0.031598 | 0.016936 | 0.009087
2021-10-07 17:45 | 0.2297 | 1.0342 | 0.39304 | 0.97321 | 0 | 0.001137 | 0 | 0
2021-10-07 18:00 | 2.6033 | 1.4954 | 0.89431 | 2.2638 | 0 | 0.00074 | 0 | 0
2021-10-07 18:15 | 2.736 | 1.8839 | 3.0014 | 2.4049 | 0 | 0.000432 | 0 | 0
2021-10-07 18:30 | 2.736 | 2.0019 | 1.4497 | 2.0733 | 0 | 0.00024 | 0 | 0
2021-10-07 18:45 | 2.736 | 2.0699 | 1.8887 | 3.3169 | 0 | 0 | 0 | 0
2021-10-07 19:00 | 0.46144 | 1.0576 | 1.4803 | 1.1173 | 0 | 0 | 0 | 0
2021-10-07 19:15 | 0.30933 | 0.92459 | 1.4599 | 0.98604 | 0 | 0 | 0 | 0
2021-10-07 19:30 | 0.31648 | 0.9609 | 0.64112 | 1.0247 | 0 | 0 | 0 | 0
2021-10-07 19:45 | 0.22358 | 0.9609 | 0.63296 | 0.977 | 0 | 0 | 0 | 0
2021-10-07 20:00 | 0.17049 | 0.94209 | 1.5211 | 1.0021 | 0 | 0 | 0 | 0
2021-10-07 20:15 | 0.17253 | 0.82609 | 2.2868 | 0.89708 | 0 | 0 | 0 | 0
2021-10-07 20:30 | 0.17355 | 0.89649 | 2.2868 | 0.66723 | 0 | 0 | 0 | 0
2021-10-07 20:45 | 0.28381 | 0.82698 | 1.9397 | 0.60102 | 0 | 0 | 0 | 0
2021-10-07 21:00 | 0.56354 | 0.63125 | 0.98006 | 0.49747 | 0 | 0 | 0 | 0
2021-10-07 21:15 | 0.33179 | 0.61335 | 0.56354 | 0.41434 | 0 | 0 | 0 | 0
2021-10-07 21:30 | 0.44919 | 0.58336 | 0.46144 | 0.39815 | 0 | 0 | 0 | 0
2021-10-07 21:45 | 0.3369 | 0.59947 | 0.34915 | 0.35819 | 0 | 0 | 0 | 0
2021-10-07 22:00 | 3.2362 | 2.2128 | 1.0311 | 2.5382 | 0 | 0 | 0 | 0
2021-10-07 22:15 | 3.42 | 2.3657 | 0.53495 | 2.5506 | 0 | 0 | 0 | 0
2021-10-07 22:30 | 3.4098 | 2.4651 | 0.33587 | 2.5054 | 0 | 0 | 0 | 0
2021-10-07 22:45 | 3.3179 | 2.361 | 0.33894 | 2.4936 | 0 | 0 | 0 | 0
2021-10-07 23:00 | 3.2873 | 2.3902 | 0.33179 | 2.4526 | 0 | 0 | 0 | 0
2021-10-07 23:15 | 3.2975 | 2.3642 | 0.33077 | 2.4862 | 0 | 0 | 0 | 0
2021-10-07 23:30 | 3.2975 | 2.4329 | 0.32567 | 2.4965 | 0 | 0 | 0 | 0
2021-10-07 23:45 | 3.4098 | 2.4382 | 0.32669 | 2.8731 | 0 | 0 | 0 | 0
2021-10-08 | 3.3996 | 2.1455 | 0.32669 | 2.6922 | 0 | 0 | 0 | 0
2021-10-08 00:15 | 3.3077 | 1.8558 | 0.32567 | 2.5343 | 0 | 0 | 0 | 0
2021-10-08 00:30 | 3.3281 | 2.0465 | 0.32158 | 2.5623 | 0 | 0 | 0 | 0
2021-10-08 00:45 | 3.2975 | 1.8558 | 0.31954 | 2.4943 | 0 | 0 | 0 | 0
2021-10-08 01:00 | 3.3077 | 1.8558 | 0.32158 | 2.4853 | 0 | 0 | 0 | 0
2021-10-08 01:15 | 3.42 | 2.1123 | 0.3226 | 2.5549 | 0 | 0 | 0 | 0
2021-10-08 01:30 | 3.3281 | 2.0465 | 0.3175 | 2.5048 | 0 | 0 | 0 | 0
2021-10-08 01:45 | 3.3077 | 1.8059 | 0.31648 | 2.5499 | 0 | 0 | 0 | 0
2021-10-08 02:00 | 3.3077 | 1.7443 | 0.31648 | 2.5447 | 0 | 0 | 0 | 0
2021-10-08 02:15 | 3.369 | 2.0364 | 0.31852 | 2.5476 | 0 | 0 | 0 | 0
2021-10-08 02:30 | 3.4302 | 2.0364 | 0.3175 | 2.5204 | 0 | 0 | 0 | 0
2021-10-08 02:45 | 3.3894 | 2.0007 | 0.31648 | 2.5108 | 0 | 0 | 0 | 0
2021-10-08 03:00 | 3.3281 | 1.9349 | 0.31648 | 2.3002 | 0 | 0 | 0 | 0
2021-10-08 03:15 | 3.2975 | 1.7054 | 0.31444 | 2.186 | 0 | 0 | 0 | 0
2021-10-08 03:30 | 3.3077 | 1.8022 | 0.31852 | 2.0195 | 0 | 0 | 0 | 0
2021-10-08 03:45 | 3.3587 | 1.9912 | 0.31648 | 1.7861 | 0 | 0 | 0 | 0
2021-10-08 04:00 | 2.2358 | 1.2522 | 0.31648 | 1.5274 | 0 | 0 | 0 | 0
2021-10-08 04:15 | 0.94331 | 1.2894 | 0.31444 | 1.3466 | 0 | 0 | 0 | 0
2021-10-08 04:30 | 0.75546 | 1.0666 | 0.31239 | 1.2442 | 0 | 0 | 0 | 0
2021-10-08 04:45 | 0.38794 | 0.64915 | 0.31648 | 1.2166 | 0 | 0 | 0 | 0
2021-10-08 05:00 | 0.28993 | 0.59515 | 0.31954 | 1.1917 | 0 | 0 | 0 | 0
2021-10-08 05:15 | 0.21235 | 0.60635 | 0.31137 | 1.1777 | 0 | 0 | 0 | 0
2021-10-08 05:30 | 0.21745 | 0.70127 | 0.31444 | 1.1262 | 0 | 0 | 0 | 0
2021-10-08 05:45 | 0.31954 | 0.6307 | 0.31648 | 0.96096 | 0.025182 | 0.020867 | 0.007549 | 0.017056
2021-10-08 06:00 | 0.31546 | 0.50685 | 0.32056 | 0.3369 | 0.061329 | 0.045735 | 0.018258 | 0.04011
2021-10-08 06:15 | 0.20418 | 0.51507 | 0.31546 | 0.26777 | 0.097476 | 0.077586 | 0.028967 | 0.063164
2021-10-08 06:30 | 1.2965 | 0.96529 | 1.562 | 1.1947 | 0.13362 | 0.099885 | 0.039676 | 0.086218
2021-10-08 06:45 | 2.7564 | 1.8288 | 2.7462 | 1.5156 | 0.21684 | 0.14369 | 0.10959 | 0.1173
2021-10-08 07:00 | 1.3884 | 1.4516 | 1.1128 | 1.6276 | 0.32059 | 0.20301 | 0.20433 | 0.15187
2021-10-08 07:15 | 0.64521 | 1.2033 | 0.91881 | 1.2058 | 0.42433 | 0.23906 | 0.29907 | 0.18644
2021-10-08 07:30 | 0.44919 | 1.1299 | 0.7963 | 1.1265 | 0.52808 | 0.28415 | 0.39381 | 0.22101
2021-10-08 07:45 | 0.52678 | 1.1474 | 0.60845 | 1.0445 | 0.57731 | 0.33107 | 0.3733 | 0.23492
2021-10-08 08:00 | 0.54312 | 1.1377 | 0.66562 | 0.99319 | 0.60274 | 0.34368 | 0.30438 | 0.24072
2021-10-08 08:15 | 0.58395 | 1.2736 | 0.66154 | 1.0635 | 0.62816 | 0.35028 | 0.23546 | 0.24652
2021-10-08 08:30 | 0.51045 | 1.1867 | 0.45736 | 0.96168 | 0.65358 | 0.37212 | 0.16654 | 0.25232
2021-10-08 08:45 | 2.3379 | 1.4584 | 0.51045 | 1.5398 | 0.66885 | 0.37837 | 0.15259 | 0.26139
2021-10-08 09:00 | 0.60845 | 1.3863 | 0.57578 | 1.682 | 0.67969 | 0.38293 | 0.16177 | 0.27181
2021-10-08 09:15 | 0.54312 | 1.3362 | 0.51453 | 1.2499 | 0.69052 | 0.40042 | 0.17096 | 0.28223
2021-10-08 09:30 | 0.53087 | 1.2235 | 0.5717 | 1.007 | 0.70135 | 0.38534 | 0.18014 | 0.29265
2021-10-08 09:45 | 0.44103 | 1.1926 | 0.51862 | 0.90729 | 0.70695 | 0.38813 | 0.17386 | 0.31204
2021-10-08 10:00 | 0.42469 | 1.1926 | 0.51453 | 0.88833 | 0.71026 | 0.39051 | 0.16106 | 0.33486
2021-10-08 10:15 | 0.58804 | 1.4303 | 0.59212 | 1.6133 | 0.71357 | 0.39289 | 0.14826 | 0.35768
2021-10-08 10:30 | 0.33894 | 1.1838 | 0.55537 | 1.0437 | 0.71688 | 0.39527 | 0.13546 | 0.3805
2021-10-08 10:45 | 0.34098 | 1.0781 | 0.42469 | 0.65162 | 0.71556 | 0.39234 | 0.12344 | 0.38314
2021-10-08 11:00 | 0.38386 | 1.3381 | 0.42469 | 0.37992 | 0.7122 | 0.38351 | 0.11176 | 0.37794
2021-10-08 11:15 | 0.34608 | 1.0489 | 0.42878 | 0.33587 | 0.70884 | 0.38302 | 0.10008 | 0.37275
2021-10-08 11:30 | 0.44511 | 1.0903 | 0.23072 | 0.34287 | 0.70549 | 0.38252 | 0.088392 | 0.36755
2021-10-08 11:45 | 0.40836 | 1.1436 | 0.17866 | 1.0067 | 0.58214 | 0.3887 | 0.15521 | 0.36191
2021-10-08 12:00 | 0.32465 | 1.1423 | 0.19091 | 1.1472 | 0.40604 | 0.38619 | 0.25523 | 0.3567
2021-10-08 12:15 | 0.26543 | 1.0883 | 0.29606 | 0.70092 | 0.22994 | 0.38368 | 0.35525 | 0.3515
2021-10-08 12:30 | 1.1128 | 1.1713 | 0.28585 | 1.0412 | 0.053841 | 0.39385 | 0.45526 | 0.34629
2021-10-08 12:45 | 0.3369 | 1.0546 | 0.28279 | 0.85289 | 0.047811 | 0.39608 | 0.47441 | 0.34576
2021-10-08 13:00 | 0.36752 | 1.0546 | 0.27156 | 0.62785 | 0.11668 | 0.39944 | 0.45931 | 0.34682
2021-10-08 13:15 | 0.30218 | 1.0711 | 0.18274 | 0.51584 | 0.18554 | 0.4028 | 0.44422 | 0.34788
2021-10-08 13:30 | 0.3226 | 1.0883 | 0.18274 | 0.7403 | 0.25441 | 0.39622 | 0.42912 | 0.34895
2021-10-08 13:45 | 0.31444 | 1.1039 | 0.1807 | 0.52051 | 0.26353 | 0.40387 | 0.35986 | 0.32571
2021-10-08 14:00 | 0.27768 | 1.3332 | 0.17866 | 0.3226 | 0.24629 | 0.3936 | 0.26763 | 0.29313
2021-10-08 14:15 | 0.35119 | 1.1451 | 0.17968 | 0.31108 | 0.22904 | 0.38144 | 0.1754 | 0.26055
2021-10-08 14:30 | 0.49411 | 1.1342 | 0.18376 | 0.30262 | 0.2118 | 0.35671 | 0.083174 | 0.22797
2021-10-08 14:45 | 0.39611 | 1.1192 | 0.25625 | 0.30583 | 0.20992 | 0.33015 | 0.099067 | 0.21888
2021-10-08 15:00 | 0.36752 | 1.0406 | 0.28381 | 0.33267 | 0.21481 | 0.33876 | 0.1609 | 0.21887
2021-10-08 15:15 | 0.32465 | 1.0352 | 0.27973 | 0.3439 | 0.21971 | 0.2627 | 0.22274 | 0.21886
2021-10-08 15:30 | 0.45736 | 1.0484 | 0.25216 | 0.36636 | 0.22461 | 0.24106 | 0.28458 | 0.21885
2021-10-08 15:45 | 0.56354 | 1.1375 | 0.21235 | 0.56776 | 0.23213 | 0.256 | 0.31039 | 0.20348
2021-10-08 16:00 | 0.34608 | 1.1521 | 0.21235 | 0.52591 | 0.24081 | 0.30269 | 0.32087 | 0.18311
2021-10-08 16:15 | 0.8453 | 0.96938 | 0.20724 | 0.57214 | 0.24949 | 0.29049 | 0.33135 | 0.16273
2021-10-08 16:30 | 0.90247 | 0.97606 | 0.2103 | 0.60262 | 0.25817 | 0.26721 | 0.34183 | 0.14236
2021-10-08 16:45 | 0.82897 | 1.0706 | 0.21235 | 0.97204 | 0.21566 | 0.20362 | 0.2845 | 0.11288
2021-10-08 17:00 | 1.0719 | 1.1508 | 0.32771 | 1.0584 | 0.15046 | 0.14628 | 0.19827 | 0.078527
2021-10-08 17:15 | 1.1128 | 1.2664 | 0.30933 | 1.2741 | 0.085252 | 0.084328 | 0.11204 | 0.044168
2021-10-08 17:30 | 1.3476 | 1.0551 | 0.31137 | 0.93879 | 0.020047 | 0.024277 | 0.025804 | 0.009809
2021-10-08 17:45 | 1.1842 | 1.1311 | 0.2297 | 0.97321 | 0 | 0.000861 | 0 | 0
2021-10-08 18:00 | 0.79222 | 1.4664 | 2.6033 | 2.2638 | 0 | 0.000571 | 0 | 0
2021-10-08 18:15 | 0.53087 | 1.49 | 2.736 | 2.4049 | 0 | 0.000224 | 0 | 0
2021-10-08 18:30 | 0.53495 | 1.4383 | 2.736 | 2.0733 | 0 | 0.000129 | 0 | 0
2021-10-08 18:45 | 3.8488 | 2.6332 | 2.736 | 3.3169 | 0 | 0 | 0 | 0
2021-10-08 19:00 | 1.7151 | 1.18 | 0.46144 | 1.1173 | 0 | 0 | 0 | 0
2021-10-08 19:15 | 0.32465 | 0.78837 | 0.30933 | 0.98604 | 0 | 0 | 0 | 0
2021-10-08 19:30 | 0.4737 | 0.98164 | 0.31648 | 1.0247 | 0 | 0 | 0 | 0
2021-10-08 19:45 | 0.5962 | 1.0076 | 0.22358 | 0.977 | 0 | 0 | 0 | 0
2021-10-08 20:00 | 0.62479 | 1.0002 | 0.17049 | 1.0021 | 0 | 0 | 0 | 0
2021-10-08 20:15 | 0.51862 | 0.87627 | 0.17253 | 0.89708 | 0 | 0 | 0 | 0
2021-10-08 20:30 | 0.52678 | 0.88184 | 0.17355 | 0.66723 | 0 | 0 | 0 | 0
2021-10-08 20:45 | 0.53087 | 0.85287 | 0.28381 | 0.60102 | 0 | 0 | 0 | 0
2021-10-08 21:00 | 0.52678 | 0.62921 | 0.56354 | 0.49747 | 0 | 0 | 0 | 0
2021-10-08 21:15 | 0.45328 | 0.5645 | 0.33179 | 0.41434 | 0 | 0 | 0 | 0
2021-10-08 21:30 | 0.41244 | 0.52606 | 0.44919 | 0.39815 | 0 | 0 | 0 | 0
2021-10-08 21:45 | 0.41244 | 0.53163 | 0.3369 | 0.35819 | 0 | 0 | 0 | 0
2021-10-08 22:00 | 3.3894 | 2.279 | 3.2362 | 2.5382 | 0 | 0 | 0 | 0
2021-10-08 22:15 | 3.471 | 2.3561 | 3.42 | 2.5506 | 0 | 0 | 0 | 0
2021-10-08 22:30 | 3.3485 | 2.4553 | 3.4098 | 2.5054 | 0 | 0 | 0 | 0
2021-10-08 22:45 | 3.3077 | 1.9746 | 3.3179 | 2.4936 | 0 | 0 | 0 | 0
2021-10-08 23:00 | 3.3485 | 2.4787 | 3.2873 | 2.4526 | 0 | 0 | 0 | 0
2021-10-08 23:15 | 3.4915 | 2.4323 | 3.2975 | 2.4862 | 0 | 0 | 0 | 0
2021-10-08 23:30 | 3.3996 | 2.4583 | 3.2975 | 2.4965 | 0 | 0 | 0 | 0
2021-10-08 23:45 | 3.369 | 2.3304 | 3.4098 | 2.8731 | 0 | 0 | 0 | 0
2021-10-09 | 3.4506 | 1.7831 | 3.3996 | 2.6922 | 0 | 0 | 0 | 0
2021-10-09 00:15 | 3.3996 | 1.7228 | 3.3077 | 2.5343 | 0 | 0 | 0 | 0
2021-10-09 00:30 | 3.4098 | 1.6739 | 3.3281 | 2.5623 | 0 | 0 | 0 | 0
2021-10-09 00:45 | 3.4506 | 1.5924 | 3.2975 | 2.4943 | 0 | 0 | 0 | 0
2021-10-09 01:00 | 3.3587 | 1.5924 | 3.3077 | 2.4853 | 0 | 0 | 0 | 0
2021-10-09 01:15 | 3.471 | 1.6057 | 3.42 | 2.5549 | 0 | 0 | 0 | 0
2021-10-09 01:30 | 3.369 | 1.5924 | 3.3281 | 2.5048 | 0 | 0 | 0 | 0
2021-10-09 01:45 | 3.4302 | 1.6284 | 3.3077 | 2.5499 | 0 | 0 | 0 | 0
2021-10-09 02:00 | 3.4915 | 1.4813 | 3.3077 | 2.5447 | 0 | 0 | 0 | 0
2021-10-09 02:15 | 3.369 | 1.6217 | 3.369 | 2.5476 | 0 | 0 | 0 | 0
2021-10-09 02:30 | 3.4302 | 1.4813 | 3.4302 | 2.5204 | 0 | 0 | 0 | 0
2021-10-09 02:45 | 3.2669 | 1.3296 | 3.3894 | 2.5108 | 0 | 0 | 0 | 0
2021-10-09 03:00 | 1.6539 | 1.1044 | 3.3281 | 2.3002 | 0 | 0 | 0 | 0
2021-10-09 03:15 | 0.95556 | 1.035 | 3.2975 | 2.186 | 0 | 0 | 0 | 0
2021-10-09 03:30 | 0.62479 | 1.0935 | 3.3077 | 2.0195 | 0 | 0 | 0 | 0
2021-10-09 03:45 | 0.3665 | 0.94505 | 3.3587 | 1.7861 | 0 | 0 | 0 | 0
2021-10-09 04:00 | 0.25318 | 0.98522 | 2.2358 | 1.5274 | 0 | 0 | 0 | 0
2021-10-09 04:15 | 0.36446 | 0.95382 | 0.94331 | 1.3466 | 0 | 0 | 0 | 0
2021-10-09 04:30 | 0.25727 | 0.95717 | 0.75546 | 1.2442 | 0 | 0 | 0 | 0
2021-10-09 04:45 | 0.30729 | 0.91338 | 0.38794 | 1.2166 | 0 | 0 | 0 | 0
2021-10-09 05:00 | 0.40223 | 0.84312 | 0.28993 | 1.1917 | 0 | 0 | 0 | 0
2021-10-09 05:15 | 0.27564 | 0.91369 | 0.21235 | 1.1777 | 0 | 0 | 0 | 0
2021-10-09 05:30 | 0.26543 | 0.91369 | 0.21745 | 1.1262 | 0 | 0 | 0 | 0
2021-10-09 05:45 | 0.36242 | 0.95178 | 0.31954 | 0.96096 | 0.023463 | 0.022029 | 0.025182 | 0.014664
2021-10-09 06:00 | 0.26237 | 0.57863 | 0.31546 | 0.3369 | 0.057545 | 0.058126 | 0.061329 | 0.03494
2021-10-09 06:15 | 0.27666 | 0.60335 | 0.20418 | 0.26777 | 0.091627 | 0.11059 | 0.097476 | 0.055216
2021-10-09 06:30 | 1.5518 | 1.1331 | 1.2965 | 1.1947 | 0.12571 | 0.14744 | 0.13362 | 0.075492
2021-10-09 06:45 | 2.1643 | 1.3798 | 2.7564 | 1.5156 | 0.20803 | 0.18688 | 0.21684 | 0.11077
2021-10-09 07:00 | 1.1434 | 1.4504 | 1.3884 | 1.6276 | 0.31222 | 0.21695 | 0.32059 | 0.15254
2021-10-09 07:15 | 0.64929 | 1.132 | 0.64521 | 1.2058 | 0.4164 | 0.25128 | 0.42433 | 0.19431
2021-10-09 07:30 | 0.75955 | 1.1439 | 0.44919 | 1.1265 | 0.52059 | 0.29896 | 0.52808 | 0.23608
2021-10-09 07:45 | 0.64112 | 1.2587 | 0.52678 | 1.0445 | 0.57398 | 0.31515 | 0.57731 | 0.24949
2021-10-09 08:00 | 0.64521 | 1.1388 | 0.54312 | 0.99319 | 0.60432 | 0.33147 | 0.60274 | 0.25143
2021-10-09 08:15 | 0.51862 | 1.4022 | 0.58395 | 1.0635 | 0.63466 | 0.34886 | 0.62816 | 0.25337
2021-10-09 08:30 | 0.46961 | 1.2989 | 0.51045 | 0.96168 | 0.665 | 0.38022 | 0.65358 | 0.25531
2021-10-09 08:45 | 0.48595 | 1.3848 | 2.3379 | 1.5398 | 0.67955 | 0.37985 | 0.66885 | 0.26481
2021-10-09 09:00 | 0.49411 | 1.3887 | 0.60845 | 1.682 | 0.68692 | 0.40943 | 0.67969 | 0.27689
2021-10-09 09:15 | 0.5472 | 1.3699 | 0.54312 | 1.2499 | 0.69429 | 0.41583 | 0.69052 | 0.28897
2021-10-09 09:30 | 0.63296 | 1.2466 | 0.53087 | 1.007 | 0.70166 | 0.41801 | 0.70135 | 0.30106
2021-10-09 09:45 | 0.5717 | 1.2273 | 0.44103 | 0.90729 | 0.70817 | 0.42573 | 0.70695 | 0.3196
2021-10-09 10:00 | 0.55128 | 1.2273 | 0.42469 | 0.88833 | 0.71429 | 0.42772 | 0.71026 | 0.34068
2021-10-09 10:15 | 3.1035 | 1.4488 | 0.58804 | 1.6133 | 0.72041 | 0.43685 | 0.71357 | 0.36174
2021-10-09 10:30 | 0.57987 | 1.2909 | 0.33894 | 1.0437 | 0.72652 | 0.44169 | 0.71688 | 0.38282
2021-10-09 10:45 | 0.55945 | 1.2885 | 0.34098 | 0.65162 | 0.72632 | 0.42229 | 0.71556 | 0.38488
2021-10-09 11:00 | 0.44919 | 1.3347 | 0.38386 | 0.37992 | 0.72323 | 0.4203 | 0.7122 | 0.37942
2021-10-09 11:15 | 0.44511 | 1.3647 | 0.34608 | 0.33587 | 0.72015 | 0.40775 | 0.70884 | 0.37397
2021-10-09 11:30 | 0.43694 | 1.4486 | 0.44511 | 0.34287 | 0.71706 | 0.40665 | 0.70549 | 0.36852
2021-10-09 11:45 | 2.6543 | 1.4025 | 0.40836 | 1.0067 | 0.71646 | 0.41746 | 0.58214 | 0.34545
2021-10-09 12:00 | 1.7049 | 1.1058 | 0.32465 | 1.1472 | 0.717 | 0.40508 | 0.40604 | 0.31527
2021-10-09 12:15 | 0.37365 | 1.3092 | 0.26543 | 0.70092 | 0.71753 | 0.41474 | 0.22994 | 0.2851
2021-10-09 12:30 | 1.0924 | 1.1245 | 1.1128 | 1.0412 | 0.71807 | 0.39158 | 0.053841 | 0.25492
2021-10-09 12:45 | 0.67379 | 1.1314 | 0.3369 | 0.85289 | 0.71728 | 0.37405 | 0.047811 | 0.25796
2021-10-09 13:00 | 0.42878 | 1.2825 | 0.36752 | 0.62785 | 0.71588 | 0.35495 | 0.11668 | 0.2747
2021-10-09 13:15 | 0.4737 | 1.0115 | 0.30218 | 0.51584 | 0.71447 | 0.38569 | 0.18554 | 0.29144
2021-10-09 13:30 | 0.47778 | 1.1572 | 0.3226 | 0.7403 | 0.71307 | 0.40691 | 0.25441 | 0.30818
2021-10-09 13:45 | 0.47778 | 1.0248 | 0.31444 | 0.52051 | 0.70762 | 0.40735 | 0.26353 | 0.2912
2021-10-09 14:00 | 0.46961 | 0.9712 | 0.27768 | 0.3226 | 0.70031 | 0.42272 | 0.24629 | 0.26083
2021-10-09 14:15 | 0.45736 | 1.2869 | 0.35119 | 0.31108 | 0.693 | 0.42092 | 0.22904 | 0.23046
2021-10-09 14:30 | 0.35119 | 1.1791 | 0.49411 | 0.30262 | 0.68569 | 0.40525 | 0.2118 | 0.20009
2021-10-09 14:45 | 0.35119 | 1.3654 | 0.39611 | 0.30583 | 0.66932 | 0.40117 | 0.20992 | 0.19484
2021-10-09 15:00 | 0.3859 | 1.2566 | 0.36752 | 0.33267 | 0.64878 | 0.40686 | 0.21481 | 0.19945
2021-10-09 15:15 | 0.46144 | 1.0798 | 0.32465 | 0.3439 | 0.62825 | 0.39601 | 0.21971 | 0.20406
2021-10-09 15:30 | 0.35629 | 1.1342 | 0.45736 | 0.36636 | 0.60772 | 0.37877 | 0.22461 | 0.20867
2021-10-09 15:45 | 0.38692 | 1.2367 | 0.56354 | 0.56776 | 0.55058 | 0.3368 | 0.23213 | 0.20128
2021-10-09 16:00 | 0.50636 | 1.2483 | 0.34608 | 0.52591 | 0.47662 | 0.29557 | 0.24081 | 0.19004
2021-10-09 16:15 | 0.39407 | 1.2661 | 0.8453 | 0.57214 | 0.40266 | 0.24472 | 0.24949 | 0.17881
2021-10-09 16:30 | 0.37569 | 1.2661 | 0.90247 | 0.60262 | 0.32869 | 0.2286 | 0.25817 | 0.16757
2021-10-09 16:45 | 0.42469 | 1.1736 | 0.82897 | 0.97204 | 0.25311 | 0.17524 | 0.21566 | 0.13581
2021-10-09 17:00 | 0.61254 | 1.2904 | 1.0719 | 1.0584 | 0.17677 | 0.12536 | 0.15046 | 0.094562
2021-10-09 17:15 | 0.40836 | 1.2644 | 1.1128 | 1.2741 | 0.10043 | 0.06549 | 0.085252 | 0.053314
2021-10-09 17:30 | 0.27156 | 1.0989 | 1.3476 | 0.93879 | 0.024097 | 0.01392 | 0.020047 | 0.012067
2021-10-09 17:45 | 0.38998 | 1.1212 | 1.1842 | 0.97321 | 0 | 0 | 0 | 0
2021-10-09 18:00 | 2.6135 | 1.5539 | 0.79222 | 2.2638 | 0 | 0 | 0 | 0
2021-10-09 18:15 | 2.7666 | 1.5381 | 0.53087 | 2.4049 | 0 | 0 | 0 | 0
2021-10-09 18:30 | 2.7768 | 1.5527 | 0.53495 | 2.0733 | 0 | 0 | 0 | 0
2021-10-09 18:45 | 2.9708 | 1.8726 | 3.8488 | 3.3169 | 0 | 0 | 0 | 0
2021-10-09 19:00 | 0.78813 | 1.1915 | 1.7151 | 1.1173 | 0 | 0 | 0 | 0
2021-10-09 19:15 | 0.55537 | 1.0588 | 0.32465 | 0.98604 | 0 | 0 | 0 | 0
2021-10-09 19:30 | 0.62479 | 1.1011 | 0.4737 | 1.0247 | 0 | 0 | 0 | 0
2021-10-09 19:45 | 0.65337 | 1.0594 | 0.5962 | 0.977 | 0 | 0 | 0 | 0
2021-10-09 20:00 | 0.8208 | 1.1036 | 0.62479 | 1.0021 | 0 | 0 | 0 | 0
2021-10-09 20:15 | 0.92289 | 0.96845 | 0.51862 | 0.89708 | 0 | 0 | 0 | 0
2021-10-09 20:30 | 0.57578 | 0.93378 | 0.52678 | 0.66723 | 0 | 0 | 0 | 0
2021-10-09 20:45 | 0.32158 | 0.92591 | 0.53087 | 0.60102 | 0 | 0 | 0 | 0
2021-10-09 21:00 | 0.34404 | 0.68265 | 0.52678 | 0.49747 | 0 | 0 | 0 | 0
2021-10-09 21:15 | 0.42878 | 0.61893 | 0.45328 | 0.41434 | 0 | 0 | 0 | 0
2021-10-09 21:30 | 0.46553 | 0.59733 | 0.41244 | 0.39815 | 0 | 0 | 0 | 0
2021-10-09 21:45 | 0.46144 | 0.56186 | 0.41244 | 0.35819 | 0 | 0 | 0 | 0
2021-10-09 22:00 | 3.3485 | 1.6836 | 3.3894 | 2.5382 | 0 | 0 | 0 | 0
2021-10-09 22:15 | 3.5119 | 1.8027 | 3.471 | 2.5506 | 0 | 0 | 0 | 0
2021-10-09 22:30 | 3.471 | 1.9275 | 3.3485 | 2.5054 | 0 | 0 | 0 | 0
2021-10-09 22:45 | 3.5731 | 1.8891 | 3.3077 | 2.4936 | 0 | 0 | 0 | 0
2021-10-09 23:00 | 3.3077 | 1.7808 | 3.3485 | 2.4526 | 0 | 0 | 0 | 0
2021-10-09 23:15 | 3.3179 | 1.8999 | 3.4915 | 2.4862 | 0 | 0 | 0 | 0
2021-10-09 23:30 | 3.3894 | 2.0452 | 3.3996 | 2.4965 | 0 | 0 | 0 | 0
2021-10-09 23:45 | 3.3077 | 1.8147 | 3.369 | 2.8731 | 0 | 0 | 0 | 0
2021-10-10 | 3.3485 | 2.3216 | 3.4506 | 2.6922 | 0 | 0 | 0 | 0
2021-10-10 00:15 | 5.5058 | 2.0385 | 3.3996 | 2.5343 | 0 | 0 | 0 | 0
2021-10-10 00:30 | 5.5211 | 1.9547 | 3.4098 | 2.5623 | 0 | 0 | 0 | 0
2021-10-10 00:45 | 5.5364 | 2.3377 | 3.4506 | 2.4943 | 0 | 0 | 0 | 0
2021-10-10 01:00 | 5.5518 | 1.9567 | 3.3587 | 2.4853 | 0 | 0 | 0 | 0
2021-10-10 01:15 | 5.5671 | 2.3361 | 3.471 | 2.5549 | 0 | 0 | 0 | 0
2021-10-10 01:30 | 5.5824 | 1.9567 | 3.369 | 2.5048 | 0 | 0 | 0 | 0
2021-10-10 01:45 | 5.5977 | 2.2163 | 3.4302 | 2.5499 | 0 | 0 | 0 | 0
2021-10-10 02:00 | 5.613 | 2.2895 | 3.4915 | 2.5447 | 0 | 0 | 0 | 0
2021-10-10 02:15 | 5.6284 | 2.4022 | 3.369 | 2.5476 | 0 | 0 | 0 | 0
2021-10-10 02:30 | 5.6437 | 2.2879 | 3.4302 | 2.5204 | 0 | 0 | 0 | 0
2021-10-10 02:45 | 5.659 | 2.2879 | 3.2669 | 2.5108 | 0 | 0 | 0 | 0
2021-10-10 03:00 | 5.6743 | 2.1985 | 1.6539 | 2.3002 | 0 | 0 | 0 | 0
2021-10-10 03:15 | 5.6896 | 2.1617 | 0.95556 | 2.186 | 0 | 0 | 0 | 0
2021-10-10 03:30 | 5.705 | 2.2491 | 0.62479 | 2.0195 | 0 | 0 | 0 | 0
2021-10-10 03:45 | 5.7203 | 1.9895 | 0.3665 | 1.7861 | 0 | 0 | 0 | 0
2021-10-10 04:00 | 5.7356 | 2.3064 | 0.25318 | 1.5274 | 0 | 0 | 0 | 0
2021-10-10 04:15 | 5.7509 | 2.2556 | 0.36446 | 1.3466 | 0 | 0 | 0 | 0
2021-10-10 04:30 | 5.7662 | 2.2275 | 0.25727 | 1.2442 | 0 | 0 | 0 | 0
2021-10-10 04:45 | 5.7815 | 2.0713 | 0.30729 | 1.2166 | 0 | 0 | 0 | 0
2021-10-10 05:00 | 5.7969 | 1.9022 | 0.40223 | 1.1917 | 0 | 0 | 0 | 0
2021-10-10 05:15 | 5.8122 | 1.9022 | 0.27564 | 1.1777 | 0 | 0 | 0 | 0
2021-10-10 05:30 | 5.8275 | 1.5432 | 0.26543 | 1.1262 | 0 | 0 | 0 | 0
2021-10-10 05:45 | 5.8428 | 1.0976 | 0.36242 | 0.96096 | 0.021627 | 0.025029 | 0.023463 | 0.012358
2021-10-10 06:00 | 5.8581 | 0.5525 | 0.26237 | 0.3369 | 0.053422 | 0.057354 | 0.057545 | 0.029919
2021-10-10 06:15 | 5.8735 | 0.5712 | 0.27666 | 0.26777 | 0.085217 | 0.10082 | 0.091627 | 0.04748
2021-10-10 06:30 | 5.8888 | 0.94897 | 1.5518 | 1.1947 | 0.11701 | 0.14444 | 0.12571 | 0.065041
2021-10-10 06:45 | 5.9041 | 1.2398 | 2.1643 | 1.5156 | 0.1907 | 0.18865 | 0.20803 | 0.10562
2021-10-10 07:00 | 5.9194 | 1.5877 | 1.1434 | 1.6276 | 0.28412 | 0.23021 | 0.31222 | 0.15622
2021-10-10 07:15 | 5.9347 | 1.1478 | 0.64929 | 1.2058 | 0.37754 | 0.26668 | 0.4164 | 0.20681
2021-10-10 07:30 | 5.95 | 1.2338 | 0.75955 | 1.1265 | 0.47095 | 0.3139 | 0.52059 | 0.2574
2021-10-10 07:45 | 5.9653 | 1.1996 | 0.64112 | 1.0445 | 0.52719 | 0.33435 | 0.57398 | 0.28296
2021-10-10 08:00 | 5.9807 | 1.1385 | 0.64521 | 0.99319 | 0.56589 | 0.35244 | 0.60432 | 0.29736
2021-10-10 08:15 | 5.996 | 1.2483 | 0.51862 | 1.0635 | 0.60459 | 0.36075 | 0.63466 | 0.31177
2021-10-10 08:30 | 6.0113 | 1.1772 | 0.46961 | 0.96168 | 0.64329 | 0.36455 | 0.665 | 0.32617
2021-10-10 08:45 | 6.0266 | 1.6672 | 0.48595 | 1.5398 | 0.66141 | 0.37943 | 0.67955 | 0.33624
2021-10-10 09:00 | 6.0419 | 1.9877 | 0.49411 | 1.682 | 0.66979 | 0.39414 | 0.68692 | 0.34457
2021-10-10 09:15 | 6.0573 | 1.5135 | 0.5472 | 1.2499 | 0.67818 | 0.42096 | 0.69429 | 0.35291
2021-10-10 09:30 | 6.0726 | 1.2749 | 0.63296 | 1.007 | 0.68657 | 0.43508 | 0.70166 | 0.36124
2021-10-10 09:45 | 6.0879 | 1.2255 | 0.5717 | 0.90729 | 0.6932 | 0.43912 | 0.70817 | 0.37845
2021-10-10 10:00 | 6.1032 | 1.2255 | 0.55128 | 0.88833 | 0.69902 | 0.44291 | 0.71429 | 0.399
2021-10-10 10:15 | 6.1185 | 1.5085 | 3.1035 | 1.6133 | 0.70483 | 0.4467 | 0.72041 | 0.41955
2021-10-10 10:30 | 6.1338 | 1.258 | 0.57987 | 1.0437 | 0.71064 | 0.45754 | 0.72652 | 0.4401
2021-10-10 10:45 | 6.1492 | 1.341 | 0.55945 | 0.65162 | 0.71057 | 0.45741 | 0.72632 | 0.43458
2021-10-10 11:00 | 6.1645 | 1.3473 | 0.44919 | 0.37992 | 0.70772 | 0.45846 | 0.72323 | 0.41902
2021-10-10 11:15 | 6.1798 | 1.0399 | 0.44511 | 0.33587 | 0.70487 | 0.4565 | 0.72015 | 0.40346
2021-10-10 11:30 | 6.1951 | 1.073 | 0.43694 | 0.34287 | 0.70202 | 0.45455 | 0.71706 | 0.38789
2021-10-10 11:45 | 6.2104 | 1.2447 | 2.6543 | 1.0067 | 0.70317 | 0.45127 | 0.71646 | 0.36257
2021-10-10 12:00 | 6.2257 | 1.0842 | 1.7049 | 1.1472 | 0.70623 | 0.45161 | 0.717 | 0.33288
2021-10-10 12:15 | 6.2411 | 1.1249 | 0.37365 | 0.70092 | 0.70928 | 0.45195 | 0.71753 | 0.30319
2021-10-10 12:30 | 6.2564 | 1.307 | 1.0924 | 1.0412 | 0.71234 | 0.4107 | 0.71807 | 0.2735
2021-10-10 12:45 | 6.2717 | 1.1718 | 0.67379 | 0.85289 | 0.7176 | 0.40222 | 0.71728 | 0.27621
2021-10-10 13:00 | 6.287 | 1.232 | 0.42878 | 0.62785 | 0.72391 | 0.43992 | 0.71588 | 0.29232
2021-10-10 13:15 | 6.3024 | 0.95113 | 0.4737 | 0.51584 | 0.73023 | 0.43906 | 0.71447 | 0.30842
2021-10-10 13:30 | 6.3177 | 1.233 | 0.47778 | 0.7403 | 0.73654 | 0.4382 | 0.71307 | 0.32452
2021-10-10 13:45 | 6.333 | 1.0705 | 0.47778 | 0.52051 | 0.702 | 0.41181 | 0.70762 | 0.31578
2021-10-10 14:00 | 6.3483 | 1.0015 | 0.46961 | 0.3226 | 0.648 | 0.40756 | 0.70031 | 0.29665
2021-10-10 14:15 | 6.3636 | 0.99915 | 0.45736 | 0.31108 | 0.59401 | 0.40391 | 0.693 | 0.27752
2021-10-10 14:30 | 6.3789 | 1.0177 | 0.35119 | 0.30262 | 0.54001 | 0.41174 | 0.68569 | 0.25839
2021-10-10 14:45 | 6.3942 | 1.088 | 0.35119 | 0.30583 | 0.52101 | 0.3957 | 0.66932 | 0.24625
2021-10-10 15:00 | 6.4096 | 1.042 | 0.3859 | 0.33267 | 0.51868 | 0.4132 | 0.64878 | 0.23754
2021-10-10 15:15 | 6.4249 | 1.0667 | 0.46144 | 0.3439 | 0.51636 | 0.39534 | 0.62825 | 0.22883
2021-10-10 15:30 | 6.4402 | 0.99644 | 0.35629 | 0.36636 | 0.51403 | 0.38451 | 0.60772 | 0.22013
2021-10-10 15:45 | 6.4555 | 1.0147 | 0.38692 | 0.56776 | 0.47709 | 0.33619 | 0.55058 | 0.21501
2021-10-10 16:00 | 6.4708 | 1.0235 | 0.50636 | 0.52591 | 0.42361 | 0.27553 | 0.47662 | 0.21086
2021-10-10 16:15 | 6.4862 | 1.0239 | 0.39407 | 0.57214 | 0.37014 | 0.23557 | 0.40266 | 0.20671
2021-10-10 16:30 | 6.5015 | 1.0239 | 0.37569 | 0.60262 | 0.31666 | 0.20275 | 0.32869 | 0.20256
2021-10-10 16:45 | 5.5021 | 1.3188 | 0.42469 | 0.97204 | 0.24874 | 0.16588 | 0.25311 | 0.16593
2021-10-10 17:00 | 4.464 | 1.4247 | 0.61254 | 1.0584 | 0.17391 | 0.1151 | 0.17677 | 0.11563
2021-10-10 17:15 | 4.2999 | 1.5007 | 0.40836 | 1.2741 | 0.099072 | 0.062105 | 0.10043 | 0.06533
2021-10-10 17:30 | 4.3052 | 1.0506 | 0.27156 | 0.93879 | 0.024238 | 0.01324 | 0.024097 | 0.015031
2021-10-10 17:45 | 4.4023 | 1.1687 | 0.38998 | 0.97321 | 0 | 0 | 0 | 0
2021-10-10 18:00 | 4.0325 | 1.8352 | 2.6135 | 2.2638 | 0 | 0 | 0 | 0
2021-10-10 18:15 | 3.8284 | 1.9051 | 2.7666 | 2.4049 | 0 | 0 | 0 | 0
2021-10-10 18:30 | 3.8284 | 1.2567 | 2.7768 | 2.0733 | 0 | 0 | 0 | 0
2021-10-10 18:45 | 4.8426 | 1.5726 | 2.9708 | 3.3169 | 0 | 0 | 0 | 0
2021-10-10 19:00 | 1.4905 | 0.98634 | 0.78813 | 1.1173 | 0 | 0 | 0 | 0
2021-10-10 19:15 | 1.2659 | 0.92441 | 0.55537 | 0.98604 | 0 | 0 | 0 | 0
2021-10-10 19:30 | 0.91064 | 1.1951 | 0.62479 | 1.0247 | 0 | 0 | 0 | 0
2021-10-10 19:45 | 1.4088 | 1.2345 | 0.65337 | 0.977 | 0 | 0 | 0 | 0
2021-10-10 20:00 | 1.6232 | 0.90923 | 0.8208 | 1.0021 | 0 | 0 | 0 | 0
2021-10-10 20:15 | 0.70646 | 0.79926 | 0.92289 | 0.89708 | 0 | 0 | 0 | 0
2021-10-10 20:30 | 0.65746 | 0.82474 | 0.57578 | 0.66723 | 0 | 0 | 0 | 0
2021-10-10 20:45 | 0.66971 | 0.82467 | 0.32158 | 0.60102 | 0 | 0 | 0 | 0
2021-10-10 21:00 | 0.62887 | 0.7418 | 0.34404 | 0.49747 | 0 | 0 | 0 | 0
2021-10-10 21:15 | 0.61662 | 0.60087 | 0.42878 | 0.41434 | 0 | 0 | 0 | 0
2021-10-10 21:30 | 0.61662 | 0.58699 | 0.46553 | 0.39815 | 0 | 0 | 0 | 0
2021-10-10 21:45 | 0.60029 | 0.63717 | 0.46144 | 0.35819 | 0 | 0 | 0 | 0
2021-10-10 22:00 | 3.4608 | 1.1466 | 3.3485 | 2.5382 | 0 | 0 | 0 | 0
2021-10-10 22:15 | 3.665 | 1.0002 | 3.5119 | 2.5506 | 0 | 0 | 0 | 0
2021-10-10 22:30 | 3.6956 | 0.98942 | 3.471 | 2.5054 | 0 | 0 | 0 | 0
2021-10-10 22:45 | 3.6548 | 0.98942 | 3.5731 | 2.4936 | 0 | 0 | 0 | 0
2021-10-10 23:00 | 3.6548 | 1.0896 | 3.3077 | 2.4526 | 0 | 0 | 0 | 0
2021-10-10 23:15 | 3.6854 | 1.0394 | 3.3179 | 2.4862 | 0 | 0 | 0 | 0
2021-10-10 23:30 | 3.5731 | 0.98942 | 3.3894 | 2.4965 | 0 | 0 | 0 | 0
2021-10-10 23:45 | 3.5323 | 1.8665 | 3.3077 | 2.8731 | 0 | 0 | 0 | 0
2021-10-11 | 3.5425 | 1.691 | 3.3485 | 2.6922 | 0 | 0 | 0 | 0
2021-10-11 00:15 | 3.42 | 1.472 | 5.5058 | 2.8439 | 0 | 0 | 0 | 0
2021-10-11 00:30 | 3.42 | 1.6678 | 5.5211 | 2.8814 | 0 | 0 | 0 | 0
2021-10-11 00:45 | 3.4506 | 1.3533 | 5.5364 | 2.804 | 0 | 0 | 0 | 0
2021-10-11 01:00 | 3.42 | 1.5476 | 5.5518 | 2.8059 | 0 | 0 | 0 | 0
2021-10-11 01:15 | 3.471 | 1.6678 | 5.5671 | 2.866 | 0 | 0 | 0 | 0
2021-10-11 01:30 | 3.5629 | 1.6678 | 5.5824 | 2.8298 | 0 | 0 | 0 | 0
2021-10-11 01:45 | 3.4915 | 1.2226 | 5.5977 | 2.8698 | 0 | 0 | 0 | 0
2021-10-11 02:00 | 3.3894 | 1.2068 | 5.613 | 2.8419 | 0 | 0 | 0 | 0
2021-10-11 02:15 | 3.4302 | 1.5213 | 5.6284 | 2.8295 | 0 | 0 | 0 | 0
2021-10-11 02:30 | 3.4098 | 1.4231 | 5.6437 | 2.8454 | 0 | 0 | 0 | 0
2021-10-11 02:45 | 3.4915 | 1.3848 | 5.659 | 2.8307 | 0 | 0 | 0 | 0
2021-10-11 03:00 | 3.5221 | 1.1567 | 5.6743 | 2.6208 | 0 | 0 | 0 | 0
2021-10-11 03:15 | 3.42 | 1.1182 | 5.6896 | 2.5088 | 0 | 0 | 0 | 0
2021-10-11 03:30 | 3.4098 | 1.1046 | 5.705 | 2.3532 | 0 | 0 | 0 | 0
2021-10-11 03:45 | 3.4098 | 0.94403 | 5.7203 | 2.1279 | 0 | 0 | 0 | 0
2021-10-11 04:00 | 3.42 | 0.89985 | 5.7356 | 1.8567 | 0 | 0 | 0 | 0
2021-10-11 04:15 | 3.4915 | 1.0337 | 5.7509 | 1.6898 | 0 | 0 | 0 | 0
2021-10-11 04:30 | 3.5629 | 0.7831 | 5.7662 | 1.5852 | 0 | 0 | 0 | 0
2021-10-11 04:45 | 3.4302 | 0.95011 | 5.7815 | 1.5481 | 0 | 0 | 0 | 0
2021-10-11 05:00 | 3.4506 | 0.98503 | 5.7969 | 1.5414 | 0 | 0 | 0 | 0
2021-10-11 05:15 | 3.42 | 0.95011 | 5.8122 | 1.515 | 0 | 0 | 0 | 0
2021-10-11 05:30 | 3.4506 | 0.95011 | 5.8275 | 1.508 | 0 | 0 | 0 | 0
2021-10-11 05:45 | 3.5119 | 0.98503 | 5.8428 | 1.5535 | 0.002708 | 0.019147 | 0.021627 | 0.015114
2021-10-11 06:00 | 0.4982 | 1.14 | 5.8581 | 1.121 | 0.006738 | 0.049992 | 0.053422 | 0.036765
2021-10-11 06:15 | 0.25318 | 0.99427 | 5.8735 | 1.0768 | 0.010767 | 0.088877 | 0.085217 | 0.058416
2021-10-11 06:30 | 0.2981 | 0.7487 | 5.8888 | 1.9899 | 0.014797 | 0.12592 | 0.11701 | 0.080067
2021-10-11 06:45 | 0.27156 | 0.72652 | 5.9041 | 2.3189 | 0.054579 | 0.1739 | 0.1907 | 0.13125
2021-10-11 07:00 | 3.3077 | 0.72303 | 5.9194 | 2.2705 | 0.11184 | 0.22673 | 0.28412 | 0.19545
2021-10-11 07:15 | 3.42 | 0.77154 | 5.9347 | 1.9481 | 0.1691 | 0.28167 | 0.37754 | 0.25966
2021-10-11 07:30 | 3.4302 | 0.77077 | 5.95 | 1.8073 | 0.22636 | 0.32379 | 0.47095 | 0.32386
2021-10-11 07:45 | 3.42 | 0.6506 | 5.9653 | 1.7876 | 0.25715 | 0.34488 | 0.52719 | 0.35648
2021-10-11 08:00 | 5.3278 | 0.81362 | 5.9807 | 1.7624 | 0.27498 | 0.36347 | 0.56589 | 0.37499
2021-10-11 08:15 | 5.7634 | 0.87046 | 5.996 | 1.8366 | 0.29281 | 0.38825 | 0.60459 | 0.39351
2021-10-11 08:30 | 5.4309 | 0.92267 | 6.0113 | 1.7353 | 0.31064 | 0.43477 | 0.64329 | 0.41203
2021-10-11 08:45 | 5.3638 | 0.85934 | 6.0266 | 2.2619 | 0.35666 | 0.44393 | 0.66141 | 0.42117
2021-10-11 09:00 | 6.7209 | 0.85934 | 6.0419 | 2.1499 | 0.4165 | 0.4586 | 0.66979 | 0.42643
2021-10-11 09:15 | 5.5561 | 0.85934 | 6.0573 | 1.8731 | 0.47633 | 0.46352 | 0.67818 | 0.43169
2021-10-11 09:30 | 4.2225 | 0.89204 | 6.0726 | 1.804 | 0.53617 | 0.48452 | 0.68657 | 0.43695
2021-10-11 09:45 | 4.517 | 0.92267 | 6.0879 | 1.7392 | 0.5213 | 0.48901 | 0.6932 | 0.45318
2021-10-11 10:00 | 6.2203 | 0.92267 | 6.1032 | 1.7216 | 0.46973 | 0.49324 | 0.69902 | 0.47347
2021-10-11 10:15 | 0.42469 | 1.0286 | 6.1185 | 2.4424 | 0.41817 | 0.51862 | 0.70483 | 0.49376
2021-10-11 10:30 | 0.32873 | 0.95584 | 6.1338 | 1.8831 | 0.3666 | 0.5217 | 0.71064 | 0.51405
2021-10-11 10:45 | 0.30321 | 1.0779 | 6.1492 | 1.477 | 0.29102 | 0.52155 | 0.71057 | 0.51144
2021-10-11 11:00 | 0.30014 | 1.1033 | 6.1645 | 1.197 | 0.20363 | 0.51615 | 0.70772 | 0.49982
2021-10-11 11:15 | 0.32158 | 1.1033 | 6.1798 | 1.1919 | 0.11624 | 0.51843 | 0.70487 | 0.48821
2021-10-11 11:30 | 0.33383 | 1.1017 | 6.1951 | 1.2019 | 0.028845 | 0.48887 | 0.70202 | 0.47659
2021-10-11 11:45 | 0.42061 | 0.81401 | 6.2104 | 1.868 | 0.038692 | 0.49473 | 0.70317 | 0.45289
2021-10-11 12:00 | 0.8208 | 0.9891 | 6.2257 | 1.8587 | 0.096447 | 0.48085 | 0.70623 | 0.42406
2021-10-11 12:15 | 5.2799 | 0.97231 | 6.2411 | 1.3431 | 0.1542 | 0.46329 | 0.70928 | 0.39522
2021-10-11 12:30 | 3.5323 | 0.84216 | 6.2564 | 1.6695 | 0.21196 | 0.47232 | 0.71234 | 0.36639
2021-10-11 12:45 | 3.5425 | 0.80984 | 6.2717 | 1.4747 | 0.2359 | 0.44664 | 0.7176 | 0.36957
2021-10-11 13:00 | 3.5425 | 0.99169 | 6.287 | 1.2679 | 0.24316 | 0.47115 | 0.72391 | 0.38604
2021-10-11 13:15 | 3.614 | 0.92729 | 6.3024 | 1.2738 | 0.25042 | 0.46516 | 0.73023 | 0.40251
2021-10-11 13:30 | 3.5425 | 0.99726 | 6.3177 | 1.5763 | 0.25768 | 0.45663 | 0.73654 | 0.41897
2021-10-11 13:45 | 3.6548 | 0.91801 | 6.333 | 1.3806 | 0.24069 | 0.44305 | 0.702 | 0.40531
2021-10-11 14:00 | 3.6956 | 1.1553 | 6.3483 | 1.1951 | 0.21172 | 0.41554 | 0.648 | 0.37868
2021-10-11 14:15 | 3.6344 | 1.0812 | 6.3636 | 1.1948 | 0.18274 | 0.40541 | 0.59401 | 0.35204
2021-10-11 14:30 | 3.614 | 1.065 | 6.3789 | 1.1887 | 0.15377 | 0.40368 | 0.54001 | 0.32541
2021-10-11 14:45 | 3.6752 | 1.065 | 6.3942 | 1.193 | 0.14666 | 0.38988 | 0.52101 | 0.31216
2021-10-11 15:00 | 3.5936 | 1.1178 | 6.4096 | 1.2222 | 0.15038 | 0.38209 | 0.51868 | 0.30524
2021-10-11 15:15 | 6.9887 | 1.1002 | 6.4249 | 1.2305 | 0.15409 | 0.37189 | 0.51636 | 0.29831
2021-10-11 15:30 | 4.1238 | 1.0498 | 6.4402 | 1.2441 | 0.15781 | 0.3617 | 0.51403 | 0.29139
2021-10-11 15:45 | 2.0316 | 1.0381 | 6.4555 | 1.4506 | 0.14236 | 0.32124 | 0.47709 | 0.28174
2021-10-11 16:00 | 0.36446 | 1.0414 | 6.4708 | 1.4245 | 0.11741 | 0.27913 | 0.42361 | 0.2702
2021-10-11 16:15 | 0.31852 | 1.0324 | 6.4862 | 1.4734 | 0.092465 | 0.23867 | 0.37014 | 0.25866
2021-10-11 16:30 | 0.33792 | 1.1732 | 6.5015 | 1.5054 | 0.067517 | 0.20264 | 0.31666 | 0.24712
2021-10-11 16:45 | 3.4404 | 1.048 | 5.5021 | 1.3497 | 0.049344 | 0.15361 | 0.24874 | 0.20096
2021-10-11 17:00 | 5.1437 | 1.1879 | 4.464 | 1.1944 | 0.034536 | 0.10417 | 0.17391 | 0.14013
2021-10-11 17:15 | 5.3422 | 0.95171 | 4.2999 | 1.4231 | 0.019727 | 0.053677 | 0.099072 | 0.079289
2021-10-11 17:30 | 4.4745 | 1.2403 | 4.3052 | 1.5066 | 0.004918 | 0.012049 | 0.024238 | 0.018452
2021-10-11 17:45 | 5.6146 | 1.127 | 4.4023 | 1.5257 | 0 | 0 | 0 | 0
2021-10-11 18:00 | 4.2141 | 1.5231 | 4.0325 | 2.5102 | 0 | 0 | 0 | 0
2021-10-11 18:15 | 5.0986 | 1.5909 | 3.8284 | 2.8002 | 0 | 0 | 0 | 0
2021-10-11 18:30 | 4.6579 | 1.4811 | 3.8284 | 2.5776 | 0 | 0 | 0 | 0
2021-10-11 18:45 | 4.7918 | 1.3976 | 4.8426 | 3.9629 | 0 | 0 | 0 | 0
2021-10-11 19:00 | 1.6947 | 1.4298 | 1.4905 | 1.2738 | 0 | 0 | 0 | 0
2021-10-11 19:15 | 1.4599 | 0.80568 | 1.2659 | 1.1141 | 0 | 0 | 0 | 0
2021-10-11 19:30 | 1.5926 | 0.88509 | 0.91064 | 0.90976 | 0 | 0 | 0 | 0
2021-10-11 19:45 | 2.3379 | 1.1522 | 1.4088 | 0.81074 | 0 | 0 | 0 | 0
2021-10-11 20:00 | 0.69013 | 1.1576 | 1.6232 | 1.1861 | 0 | 0 | 0 | 0
2021-10-11 20:15 | 0.54312 | 0.85154 | 0.70646 | 0.96475 | 0 | 0 | 0 | 0
2021-10-11 20:30 | 0.55537 | 0.83017 | 0.65746 | 0.73592 | 0 | 0 | 0 | 0
2021-10-11 20:45 | 0.55537 | 0.82045 | 0.66971 | 0.6716 | 0 | 0 | 0 | 0
2021-10-11 21:00 | 0.47778 | 0.72004 | 0.62887 | 0.56018 | 0 | 0 | 0 | 0
2021-10-11 21:15 | 0.49003 | 0.74524 | 0.61662 | 0.45882 | 0 | 0 | 0 | 0
2021-10-11 21:30 | 0.40632 | 0.74524 | 0.61662 | 0.4473 | 0 | 0 | 0 | 0
2021-10-11 21:45 | 0.36038 | 0.74524 | 0.60029 | 0.41886 | 0 | 0 | 0 | 0
2021-10-11 22:00 | 3.3077 | 1.3152 | 3.4608 | 3.0073 | 0 | 0 | 0 | 0
2021-10-11 22:15 | 2.7156 | 1.331 | 3.665 | 3.0487 | 0 | 0 | 0 | 0
2021-10-11 22:30 | 1.1638 | 1.8885 | 3.6956 | 2.994 | 0 | 0 | 0 | 0
2021-10-11 22:45 | 0.89839 | 1.8885 | 3.6548 | 2.9755 | 0 | 0 | 0 | 0
2021-10-11 23:00 | 0.68604 | 1.7347 | 3.6548 | 2.9497 | 0 | 0 | 0 | 0
2021-10-11 23:15 | 0.29198 | 1.7347 | 3.6854 | 2.9874 | 0 | 0 | 0 | 0
2021-10-11 23:30 | 0.24399 | 1.8003 | 3.5731 | 2.9721 | 0 | 0 | 0 | 0
2021-10-11 23:45 | 0.24502 | 1.7059 | 3.5323 | 2.9154 | 0 | 0 | 0 | 0
2021-10-12 | 0.35017 | 1.3054 | 3.5425 | 2.7214 | 0 | 0 | 0 | 0
2021-10-12 00:15 | 0.36344 | 1.0529 | 3.42 | 2.8629 | 0 | 0 | 0 | 0
2021-10-12 00:30 | 0.3226 | 1.1231 | 3.42 | 2.8858 | 0 | 0 | 0 | 0
2021-10-12 00:45 | 0.24297 | 0.84131 | 3.4506 | 2.8273 | 0 | 0 | 0 | 0
2021-10-12 01:00 | 0.24502 | 0.86506 | 3.42 | 2.8176 | 0 | 0 | 0 | 0
2021-10-12 01:15 | 0.25931 | 0.84131 | 3.471 | 2.8718 | 0 | 0 | 0 | 0
2021-10-12 01:30 | 0.30831 | 0.86575 | 3.5629 | 2.8604 | 0 | 0 | 0 | 0
2021-10-12 01:45 | 0.37569 | 1.0993 | 3.4915 | 2.8975 | 0 | 0 | 0 | 0
2021-10-12 02:00 | 0.30729 | 0.8866 | 3.3894 | 2.855 | 0 | 0 | 0 | 0
2021-10-12 02:15 | 0.30014 | 0.86216 | 3.4302 | 2.8353 | 0 | 0 | 0 | 0
2021-10-12 02:30 | 0.24502 | 0.76396 | 3.4098 | 2.8527 | 0 | 0 | 0 | 0
2021-10-12 02:45 | 0.24604 | 0.68422 | 3.4915 | 2.8482 | 0 | 0 | 0 | 0
2021-10-12 03:00 | 0.26441 | 0.70866 | 3.5221 | 2.6223 | 0 | 0 | 0 | 0
2021-10-12 03:15 | 0.32056 | 0.7324 | 3.42 | 2.5073 | 0 | 0 | 0 | 0
2021-10-12 03:30 | 0.37161 | 0.82178 | 3.4098 | 2.3605 | 0 | 0 | 0 | 0
2021-10-12 03:45 | 0.28993 | 0.79734 | 3.4098 | 2.1337 | 0 | 0 | 0 | 0
2021-10-12 04:00 | 0.28177 | 0.79734 | 3.42 | 1.8582 | 0 | 0 | 0 | 0
2021-10-12 04:15 | 0.29198 | 0.82672 | 3.4915 | 1.6956 | 0 | 0 | 0 | 0
2021-10-12 04:30 | 0.24604 | 0.82595 | 3.5629 | 1.6144 | 0 | 0 | 0 | 0
2021-10-12 04:45 | 0.25931 | 0.89572 | 3.4302 | 1.5598 | 0 | 0 | 0 | 0
2021-10-12 05:00 | 0.3665 | 0.84753 | 3.4506 | 1.5473 | 0 | 0 | 0 | 0
2021-10-12 05:15 | 0.35425 | 0.88313 | 3.42 | 1.515 | 0 | 0 | 0 | 0
2021-10-12 05:30 | 0.25829 | 0.85939 | 3.4506 | 1.5241 | 0 | 0 | 0 | 0
2021-10-12 05:45 | 0.23991 | 0.86772 | 3.5119 | 1.5783 | 0.002874 | 0.016251 | 0.002708 | 0.015501
2021-10-12 06:00 | 0.28585 | 1.066 | 0.4982 | 1.1186 | 0.007204 | 0.039175 | 0.006738 | 0.037728
2021-10-12 06:15 | 0.27768 | 0.98512 | 0.25318 | 1.0698 | 0.011533 | 0.071496 | 0.010767 | 0.059954
2021-10-12 06:30 | 2.7258 | 0.78484 | 0.2981 | 1.9779 | 0.015863 | 0.10369 | 0.014797 | 0.082181
2021-10-12 06:45 | 0.63704 | 0.99276 | 0.27156 | 2.3322 | 0.021241 | 0.129 | 0.054579 | 0.13835
2021-10-12 07:00 | 1.0311 | 1.1815 | 3.3077 | 2.2909 | 0.02715 | 0.16306 | 0.11184 | 0.20977
2021-10-12 07:15 | 0.49411 | 0.99398 | 3.42 | 1.9422 | 0.03306 | 0.19479 | 0.1691 | 0.28119
2021-10-12 07:30 | 0.80447 | 0.89216 | 3.4302 | 1.8102 | 0.038969 | 0.24227 | 0.22636 | 0.35262
2021-10-12 07:45 | 0.51045 | 0.89216 | 3.42 | 1.8022 | 0.064741 | 0.25805 | 0.25715 | 0.38923
2021-10-12 08:00 | 0.37671 | 0.72995 | 5.3278 | 2.0466 | 0.10061 | 0.25436 | 0.27498 | 0.41009
2021-10-12 08:15 | 0.4982 | 0.70837 | 5.7634 | 2.0941 | 0.13647 | 0.28375 | 0.29281 | 0.43095
2021-10-12 08:30 | 0.50228 | 0.72995 | 5.4309 | 2.0109 | 0.17233 | 0.30603 | 0.31064 | 0.45182
2021-10-12 08:45 | 0.54312 | 0.67822 | 5.3638 | 2.5206 | 0.20615 | 0.31272 | 0.35666 | 0.46651
2021-10-12 09:00 | 0.42061 | 0.6747 | 6.7209 | 2.5923 | 0.23891 | 0.31612 | 0.4165 | 0.479
2021-10-12 09:15 | 0.42469 | 0.71671 | 5.5561 | 2.136 | 0.27168 | 0.31951 | 0.47633 | 0.4915
2021-10-12 09:30 | 0.53087 | 0.73171 | 4.2225 | 1.8953 | 0.30445 | 0.3229 | 0.53617 | 0.50399
2021-10-12 09:45 | 0.46553 | 0.67943 | 4.517 | 1.8668 | 0.32822 | 0.3259 | 0.5213 | 0.50936
2021-10-12 10:00 | 0.2787 | 0.64787 | 6.2203 | 2.107 | 0.34741 | 0.32871 | 0.46973 | 0.51078
2021-10-12 10:15 | 0.39202 | 0.62608 | 0.42469 | 1.6809 | 0.3666 | 0.33153 | 0.41817 | 0.51219
2021-10-12 10:30 | 0.36854 | 0.86916 | 0.32873 | 1.2473 | 0.38579 | 0.33434 | 0.3666 | 0.51361
2021-10-12 10:45 | 0.2736 | 0.9298 | 0.30321 | 1.214 | 0.32735 | 0.33425 | 0.29102 | 0.49931
2021-10-12 11:00 | 0.2491 | 0.9298 | 0.30014 | 1.2048 | 0.22929 | 0.33283 | 0.20363 | 0.47827
2021-10-12 11:15 | 0.26952 | 0.9298 | 0.32158 | 1.2053 | 0.13123 | 0.33127 | 0.11624 | 0.45724
2021-10-12 11:30 | 0.36038 | 0.96572 | 0.33383 | 1.1961 | 0.033171 | 0.34624 | 0.028845 | 0.4362
2021-10-12 11:45 | 0.33281 | 0.70661 | 0.42061 | 1.8616 | 0.021258 | 0.32843 | 0.038692 | 0.41438
2021-10-12 12:00 | 0.25522 | 0.84106 | 0.8208 | 1.6346 | 0.053382 | 0.32982 | 0.096447 | 0.39328
2021-10-12 12:15 | 0.31137 | 0.60942 | 5.2799 | 1.8669 | 0.085507 | 0.33655 | 0.1542 | 0.37219
2021-10-12 12:30 | 0.44919 | 0.58861 | 3.5323 | 2.1326 | 0.11763 | 0.34163 | 0.21196 | 0.35109
2021-10-12 12:45 | 0.34098 | 0.61019 | 3.5425 | 1.9437 | 0.1112 | 0.36587 | 0.2359 | 0.35264
2021-10-12 13:00 | 0.34302 | 0.67352 | 3.5425 | 1.7332 | 0.085015 | 0.33507 | 0.24316 | 0.36339
2021-10-12 13:15 | 0.42469 | 0.78627 | 3.614 | 1.6355 | 0.058834 | 0.34124 | 0.25042 | 0.37414
2021-10-12 13:30 | 0.2787 | 0.70596 | 3.5425 | 1.971 | 0.032654 | 0.33115 | 0.25768 | 0.38489
2021-10-12 13:45 | 0.31137 | 0.75046 | 3.6548 | 1.8315 | 0.024626 | 0.3319 | 0.24069 | 0.36439
2021-10-12 14:00 | 0.37671 | 0.81379 | 3.6956 | 1.66 | 0.025906 | 0.32536 | 0.21172 | 0.33008
2021-10-12 14:15 | 0.25931 | 0.81379 | 3.6344 | 1.6699 | 0.027186 | 0.32244 | 0.18274 | 0.29578
2021-10-12 14:30 | 0.26543 | 0.81379 | 3.614 | 1.6644 | 0.028466 | 0.3079 | 0.15377 | 0.26148
2021-10-12 14:45 | 0.26543 | 0.70027 | 3.6752 | 1.6804 | 0.042663 | 0.30163 | 0.14666 | 0.2529
2021-10-12 15:00 | 0.33383 | 0.7278 | 3.5936 | 1.6851 | 0.063493 | 0.29379 | 0.15038 | 0.25567
2021-10-12 15:15 | 0.2787 | 0.66799 | 6.9887 | 2.1733 | 0.084324 | 0.28595 | 0.15409 | 0.25843
2021-10-12 15:30 | 0.30933 | 0.67652 | 4.1238 | 1.7825 | 0.10515 | 0.27812 | 0.15781 | 0.2612
2021-10-12 15:45 | 0.28585 | 0.80356 | 2.0316 | 1.4681 | 0.10927 | 0.24541 | 0.14236 | 0.25651
2021-10-12 16:00 | 0.38284 | 0.97675 | 0.36446 | 1.2068 | 0.10479 | 0.222 | 0.11741 | 0.24782
2021-10-12 16:15 | 0.2685 | 0.90492 | 0.31852 | 1.2724 | 0.10031 | 0.19178 | 0.092465 | 0.23913
2021-10-12 16:30 | 0.26339 | 0.73662 | 0.33792 | 1.2737 | 0.095833 | 0.16018 | 0.067517 | 0.23044
2021-10-12 16:45 | 1.1434 | 0.77761 | 3.4404 | 1.5787 | 0.07875 | 0.11689 | 0.049344 | 0.1879
2021-10-12 17:00 | 1.2965 | 0.70291 | 5.1437 | 1.7944 | 0.055175 | 0.080341 | 0.034536 | 0.13109
2021-10-12 17:15 | 0.37977 | 0.88957 | 5.3422 | 1.7546 | 0.031599 | 0.043747 | 0.019727 | 0.07428
2021-10-12 17:30 | 0.35731 | 0.93753 | 4.4745 | 1.6397 | 0.008024 | 0.010012 | 0.004918 | 0.017469
2021-10-12 17:45 | 0.25522 | 0.82624 | 5.6146 | 1.7867 | 0 | 0 | 0 | 0
2021-10-12 18:00 | 0.35527 | 1.5463 | 4.2141 | 2.5405 | 0 | 0 | 0 | 0
2021-10-12 18:15 | 2.5829 | 1.4615 | 5.0986 | 2.97 | 0 | 0 | 0 | 0
2021-10-12 18:30 | 3.369 | 1.5111 | 4.6579 | 2.7092 | 0 | 0 | 0 | 0
2021-10-12 18:45 | 3.3485 | 1.6102 | 4.7918 | 4.0174 | 0 | 0 | 0 | 0
2021-10-12 19:00 | 2.052 | 1.4371 | 1.6947 | 1.3394 | 0 | 0 | 0 | 0
2021-10-12 19:15 | 1.4088 | 1.239 | 1.4599 | 1.2652 | 0 | 0 | 0 | 0
2021-10-12 19:30 | 1.2863 | 1.2538 | 1.5926 | 1.0655 | 0 | 0 | 0 | 0
2021-10-12 19:45 | 0.66562 | 1.1229 | 2.3379 | 0.97554 | 0 | 0 | 0 | 0
2021-10-12 20:00 | 0.68196 | 1.2324 | 0.69013 | 1.1885 | 0 | 0 | 0 | 0
2021-10-12 20:15 | 0.92697 | 1.1282 | 0.54312 | 0.97641 | 0 | 0 | 0 | 0
2021-10-12 20:30 | 0.62887 | 0.91025 | 0.55537 | 0.747 | 0 | 0 | 0 | 0
2021-10-12 20:45 | 0.53495 | 0.81485 | 0.55537 | 0.67919 | 0 | 0 | 0 | 0
2021-10-12 21:00 | 0.48595 | 0.825 | 0.47778 | 0.57301 | 0 | 0 | 0 | 0
2021-10-12 21:15 | 0.5227 | 0.74399 | 0.49003 | 0.48376 | 0 | 0 | 0 | 0
2021-10-12 21:30 | 0.51453 | 0.73074 | 0.40632 | 0.46932 | 0 | 0 | 0 | 0
2021-10-12 21:45 | 0.4737 | 0.74571 | 0.36038 | 0.43651 | 0 | 0 | 0 | 0
2021-10-12 22:00 | 3.4404 | 1.5633 | 3.3077 | 3.0291 | 0 | 0 | 0 | 0
2021-10-12 22:15 | 3.8284 | 1.689 | 2.7156 | 2.9641 | 0 | 0 | 0 | 0
2021-10-12 22:30 | 3.471 | 1.9476 | 1.1638 | 2.6834 | 0 | 0 | 0 | 0
2021-10-12 22:45 | 3.4404 | 1.5818 | 0.89839 | 2.6284 | 0 | 0 | 0 | 0
2021-10-12 23:00 | 3.3996 | 1.6598 | 0.68604 | 2.562 | 0 | 0 | 0 | 0
2021-10-12 23:15 | 3.4608 | 1.5693 | 0.29198 | 2.5347 | 0 | 0 | 0 | 0
2021-10-12 23:30 | 3.5629 | 1.6895 | 0.24399 | 2.5126 | 0 | 0 | 0 | 0
2021-10-12 23:45 | 3.5731 | 1.5332 | 0.24502 | 2.5056 | 0 | 0 | 0 | 0
2021-10-13 | 3.6344 | 2.2909 | 0.35017 | 2.5468 | 0 | 0 | 0 | 0
2021-10-13 00:15 | 3.5629 | 2.5194 | 0.36344 | 2.8232 | 0 | 0 | 0 | 0
2021-10-13 00:30 | 3.4813 | 2.5194 | 0.3226 | 2.8263 | 0 | 0 | 0 | 0
2021-10-13 00:45 | 3.3894 | 2.5194 | 0.24297 | 2.8226 | 0 | 0 | 0 | 0
2021-10-13 01:00 | 3.4302 | 2.5194 | 0.24502 | 2.8094 | 0 | 0 | 0 | 0
2021-10-13 01:15 | 3.42 | 2.5194 | 0.25931 | 2.8531 | 0 | 0 | 0 | 0
2021-10-13 01:30 | 3.5017 | 2.5194 | 0.30831 | 2.847 | 0 | 0 | 0 | 0
2021-10-13 01:45 | 3.4915 | 2.3828 | 0.37569 | 2.8572 | 0 | 0 | 0 | 0
2021-10-13 02:00 | 1.8478 | 2.3212 | 0.30729 | 2.8423 | 0 | 0 | 0 | 0
2021-10-13 02:15 | 0.91472 | 2.3212 | 0.30014 | 2.8394 | 0 | 0 | 0 | 0
2021-10-13 02:30 | 0.35221 | 2.3212 | 0.24502 | 2.8496 | 0 | 0 | 0 | 0
2021-10-13 02:45 | 0.43286 | 2.3212 | 0.24604 | 2.8343 | 0 | 0 | 0 | 0
2021-10-13 03:00 | 0.42878 | 2.1851 | 0.26441 | 2.6029 | 0 | 0 | 0 | 0
2021-10-13 03:15 | 0.31546 | 2.197 | 0.32056 | 2.4955 | 0 | 0 | 0 | 0
2021-10-13 03:30 | 0.2981 | 1.9552 | 0.37161 | 2.3563 | 0 | 0 | 0 | 0
2021-10-13 03:45 | 0.30218 | 1.7594 | 0.28993 | 2.1244 | 0 | 0 | 0 | 0
2021-10-13 04:00 | 0.45328 | 1.6828 | 0.28177 | 1.8575 | 0 | 0 | 0 | 0
2021-10-13 04:15 | 0.43694 | 1.531 | 0.29198 | 1.697 | 0 | 0 | 0 | 0
2021-10-13 04:30 | 0.35935 | 1.1511 | 0.24604 | 1.6006 | 0 | 0 | 0 | 0
2021-10-13 04:45 | 0.30218 | 1.1578 | 0.25931 | 1.5403 | 0 | 0 | 0 | 0
2021-10-13 05:00 | 0.30014 | 1.2039 | 0.3665 | 1.5608 | 0 | 0 | 0 | 0
2021-10-13 05:15 | 0.31341 | 1.169 | 0.35425 | 1.5264 | 0 | 0 | 0 | 0
2021-10-13 05:30 | 0.33383 | 1.169 | 0.25829 | 1.5194 | 0 | 0 | 0 | 0
2021-10-13 05:45 | 0.42061 | 1.2151 | 0.23991 | 1.556 | 0.006575 | 0.018818 | 0.002874 | 0.012247
2021-10-13 06:00 | 0.39815 | 1.0016 | 0.28585 | 1.1195 | 0.016604 | 0.042672 | 0.007204 | 0.030011
2021-10-13 06:15 | 0.30218 | 1.0003 | 0.27768 | 1.0711 | 0.026633 | 0.070487 | 0.011533 | 0.047776
2021-10-13 06:30 | 2.2153 | 1.127 | 2.7258 | 1.9634 | 0.036662 | 0.098306 | 0.015863 | 0.06554
2021-10-13 06:45 | 2.491 | 1.2499 | 0.63704 | 2.149 | 0.092341 | 0.13256 | 0.021241 | 0.1186
2021-10-13 07:00 | 1.1536 | 1.4892 | 1.0311 | 2.2297 | 0.17204 | 0.1831 | 0.02715 | 0.18745
2021-10-13 07:15 | 1.123 | 1.5947 | 0.49411 | 1.9113 | 0.25174 | 0.22063 | 0.03306 | 0.25629
2021-10-13 07:30 | 0.51862 | 1.4379 | 0.80447 | 1.84 | 0.33144 | 0.26022 | 0.038969 | 0.32514
2021-10-13 07:45 | 0.53087 | 1.5854 | 0.51045 | 1.7946 | 0.38132 | 0.27733 | 0.064741 | 0.35481
2021-10-13 08:00 | 2.103 | 1.6664 | 0.37671 | 2.0403 | 0.41549 | 0.29604 | 0.10061 | 0.36737
2021-10-13 08:15 | 0.61662 | 1.7076 | 0.4982 | 2.0994 | 0.44965 | 0.31755 | 0.13647 | 0.37993
2021-10-13 08:30 | 0.4737 | 1.7282 | 0.50228 | 2.0214 | 0.48382 | 0.34563 | 0.17233 | 0.3925
2021-10-13 08:45 | 0.53087 | 1.8309 | 0.54312 | 2.5472 | 0.52006 | 0.35319 | 0.20615 | 0.40973
2021-10-13 09:00 | 0.54312 | 1.8816 | 0.42061 | 2.6 | 0.55739 | 0.35702 | 0.23891 | 0.42892
2021-10-13 09:15 | 0.53495 | 1.823 | 0.42469 | 2.1415 | 0.59472 | 0.36085 | 0.27168 | 0.44812
2021-10-13 09:30 | 0.51453 | 1.6096 | 0.53087 | 1.9147 | 0.63205 | 0.36469 | 0.30445 | 0.46732
2021-10-13 09:45 | 0.44511 | 1.7541 | 0.46553 | 1.8738 | 0.61394 | 0.36807 | 0.32822 | 0.47395
2021-10-13 10:00 | 0.46553 | 1.8788 | 0.2787 | 2.0908 | 0.56653 | 0.37125 | 0.34741 | 0.47435
2021-10-13 10:15 | 0.4737 | 1.2718 | 0.39202 | 1.689 | 0.51912 | 0.37443 | 0.3666 | 0.47475
2021-10-13 10:30 | 0.45328 | 1.3262 | 0.36854 | 1.2664 | 0.4717 | 0.37761 | 0.38579 | 0.47515
2021-10-13 10:45 | 0.48595 | 1.2161 | 0.2736 | 1.2207 | 0.45176 | 0.3775 | 0.32735 | 0.4531
2021-10-13 11:00 | 0.61254 | 1.2305 | 0.2491 | 1.2082 | 0.44635 | 0.3759 | 0.22929 | 0.42037
2021-10-13 11:15 | 0.62887 | 1.3383 | 0.26952 | 1.2116 | 0.44094 | 0.37429 | 0.13123 | 0.38764
2021-10-13 11:30 | 0.52678 | 1.3229 | 0.36038 | 1.2062 | 0.43553 | 0.31229 | 0.033171 | 0.35491
2021-10-13 11:45 | 0.62479 | 1.45 | 0.33281 | 1.8604 | 0.39446 | 0.32941 | 0.021258 | 0.34508
2021-10-13 12:00 | 2.542 | 1.3327 | 0.25522 | 1.6389 | 0.33447 | 0.38252 | 0.053382 | 0.34671
2021-10-13 12:15 | 1.3578 | 1.5373 | 0.31137 | 1.8789 | 0.27448 | 0.3728 | 0.085507 | 0.34834
2021-10-13 12:30 | 0.81672 | 1.3836 | 0.44919 | 2.1641 | 0.2145 | 0.38009 | 0.11763 | 0.34998
2021-10-13 12:45 | 1.1434 | 1.5678 | 0.34098 | 1.9535 | 0.21224 | 0.37984 | 0.1112 | 0.35407
2021-10-13 13:00 | 0.90656 | 1.6331 | 0.34302 | 1.7335 | 0.24064 | 0.37311 | 0.085015 | 0.35879
2021-10-13 13:15 | 0.51862 | 1.5397 | 0.42469 | 1.6618 | 0.26905 | 0.37521 | 0.058834 | 0.36351
2021-10-13 13:30 | 1.7355 | 1.6949 | 0.2787 | 1.9783 | 0.29745 | 0.35657 | 0.032654 | 0.36824
2021-10-13 13:45 | 2.6033 | 1.8051 | 0.31137 | 1.8436 | 0.30447 | 0.36024 | 0.024626 | 0.34907
2021-10-13 14:00 | 0.46553 | 1.6564 | 0.37671 | 1.6786 | 0.30013 | 0.35942 | 0.025906 | 0.3193
2021-10-13 14:15 | 0.40836 | 1.6564 | 0.25931 | 1.6648 | 0.29579 | 0.3562 | 0.027186 | 0.28953
2021-10-13 14:30 | 0.36344 | 1.6035 | 0.26543 | 1.6708 | 0.29144 | 0.35468 | 0.028466 | 0.25976
2021-10-13 14:45 | 0.34608 | 1.5302 | 0.26543 | 1.6793 | 0.3252 | 0.34746 | 0.042663 | 0.25481
2021-10-13 15:00 | 0.51045 | 1.5232 | 0.33383 | 1.685 | 0.37925 | 0.33861 | 0.063493 | 0.26107
2021-10-13 15:15 | 0.42061 | 1.8247 | 0.2787 | 2.1812 | 0.4333 | 0.3306 | 0.084324 | 0.26733
2021-10-13 15:30 | 0.39815 | 1.7422 | 0.30933 | 1.7954 | 0.48735 | 0.30401 | 0.10515 | 0.27359
2021-10-13 15:45 | 0.38794 | 1.4447 | 0.28585 | 1.4771 | 0.46019 | 0.28385 | 0.10927 | 0.26782
2021-10-13 16:00 | 0.49003 | 1.2073 | 0.38284 | 1.2295 | 0.38971 | 0.24635 | 0.10479 | 0.25595
2021-10-13 16:15 | 0.50228 | 1.2211 | 0.2685 | 1.2614 | 0.31922 | 0.20365 | 0.10031 | 0.24409
2021-10-13 16:30 | 0.43694 | 1.2992 | 0.26339 | 1.274 | 0.24874 | 0.16565 | 0.095833 | 0.23223
2021-10-13 16:45 | 0.45736 | 1.4409 | 1.1434 | 1.711 | 0.18767 | 0.11053 | 0.07875 | 0.1888
2021-10-13 17:00 | 0.53087 | 1.5563 | 1.2965 | 1.9368 | 0.13162 | 0.070665 | 0.055175 | 0.13178
2021-10-13 17:15 | 0.58804 | 1.4369 | 0.37977 | 1.7708 | 0.07558 | 0.044239 | 0.031599 | 0.07475
2021-10-13 17:30 | 0.51045 | 1.3307 | 0.35731 | 1.6371 | 0.019535 | 0.011185 | 0.008024 | 0.017723
2021-10-13 17:45 | 0.46961 | 1.4948 | 0.25522 | 1.7813 | 0 | 0 | 0 | 0
2021-10-13 18:00 | 0.46144 | 1.4695 | 0.35527 | 2.215 | 0 | 0 | 0 | 0
2021-10-13 18:15 | 0.55945 | 1.5976 | 2.5829 | 2.935 | 0 | 0 | 0 | 0
2021-10-13 18:30 | 2.491 | 1.5113 | 3.369 | 2.7647 | 0 | 0 | 0 | 0
2021-10-13 18:45 | 3.6854 | 1.6382 | 3.3485 | 3.4896 | 0 | 0 | 0 | 0
2021-10-13 19:00 | 1.4088 | 1.2236 | 2.052 | 1.3832 | 0 | 0 | 0 | 0
2021-10-13 19:15 | 1.1638 | 1.1379 | 1.4088 | 0.96912 | 0 | 0 | 0 | 0
2021-10-13 19:30 | 1.1944 | 1.014 | 1.2863 | 0.83509 | 0 | 0 | 0 | 0
2021-10-13 19:45 | 0.69013 | 1.0815 | 0.66562 | 0.9312 | 0 | 0 | 0 | 0
2021-10-13 20:00 | 0.70646 | 1.0588 | 0.68196 | 0.87608 | 0 | 0 | 0 | 0
2021-10-13 20:15 | 0.70238 | 0.97264 | 0.92697 | 0.8682 | 0 | 0 | 0 | 0
2021-10-13 20:30 | 1.2761 | 0.97264 | 0.62887 | 0.77209 | 0 | 0 | 0 | 0
2021-10-13 20:45 | 1.0719 | 1.0078 | 0.53495 | 0.69085 | 0 | 0 | 0 | 0
2021-10-13 21:00 | 1.0924 | 0.91849 | 0.48595 | 0.57243 | 0 | 0 | 0 | 0
2021-10-13 21:15 | 0.56354 | 0.63207 | 0.5227 | 0.48668 | 0 | 0 | 0 | 0
2021-10-13 21:30 | 0.58804 | 0.6241 | 0.51453 | 0.47515 | 0 | 0 | 0 | 0
2021-10-13 21:45 | 0.39713 | 0.64021 | 0.4737 | 0.42775 | 0 | 0 | 0 | 0
2021-10-13 22:00 | 3.1852 | 1.4944 | 3.4404 | 3.0306 | 0 | 0 | 0 | 0
2021-10-13 22:15 | 3.369 | 1.2505 | 3.8284 | 3.021 | 0 | 0 | 0 | 0
2021-10-13 22:30 | 3.3996 | 1.1246 | 3.471 | 2.6994 | 0 | 0 | 0 | 0
2021-10-13 22:45 | 3.3996 | 1.1246 | 3.4404 | 2.6473 | 0 | 0 | 0 | 0
2021-10-13 23:00 | 3.5017 | 1.1476 | 3.3996 | 2.5737 | 0 | 0 | 0 | 0
2021-10-13 23:15 | 3.5119 | 1.1265 | 3.4608 | 2.5537 | 0 | 0 | 0 | 0
2021-10-13 23:30 | 3.3485 | 1.1265 | 3.5629 | 2.5417 | 0 | 0 | 0 | 0
2021-10-13 23:45 | 3.3485 | 1.0883 | 3.5731 | 2.5377 | 0 | 0 | 0 | 0
2021-10-14 | 3.4404 | 1.1839 | 3.6344 | 2.5789 | 0 | 0 | 0 | 0
2021-10-14 00:15 | 3.4302 | 1.2369 | 3.5629 | 2.8407 | 0 | 0 | 0 | 0
2021-10-14 00:30 | 3.5629 | 1.2193 | 3.4813 | 2.8292 | 0 | 0 | 0 | 0
2021-10-14 00:45 | 3.4404 | 1.2301 | 3.3894 | 2.8124 | 0 | 0 | 0 | 0
2021-10-14 01:00 | 3.3996 | 1.2301 | 3.4302 | 2.805 | 0 | 0 | 0 | 0
2021-10-14 01:15 | 3.369 | 1.2301 | 3.42 | 2.8473 | 0 | 0 | 0 | 0
2021-10-14 01:30 | 3.4098 | 1.2301 | 3.5017 | 2.8528 | 0 | 0 | 0 | 0
2021-10-14 01:45 | 3.5119 | 1.2369 | 3.4915 | 2.8587 | 0 | 0 | 0 | 0
2021-10-14 02:00 | 3.4915 | 1.3948 | 1.8478 | 2.6105 | 0 | 0 | 0 | 0
2021-10-14 02:15 | 3.4506 | 1.2677 | 0.91472 | 2.4757 | 0 | 0 | 0 | 0
2021-10-14 02:30 | 2.9198 | 1.1986 | 0.35221 | 2.4041 | 0 | 0 | 0 | 0
2021-10-14 02:45 | 1.4497 | 1.1986 | 0.43286 | 2.4003 | 0 | 0 | 0 | 0
2021-10-14 03:00 | 0.68196 | 1.1965 | 0.42878 | 2.1697 | 0 | 0 | 0 | 0
2021-10-14 03:15 | 0.82897 | 1.2171 | 0.31546 | 2.0447 | 0 | 0 | 0 | 0
2021-10-14 03:30 | 0.27564 | 1.2239 | 0.2981 | 2.0051 | 0 | 0 | 0 | 0
2021-10-14 03:45 | 0.26748 | 1.2191 | 0.30218 | 1.9663 | 0 | 0 | 0 | 0
2021-10-14 04:00 | 0.30218 | 1.2191 | 0.45328 | 1.8137 | 0 | 0 | 0 | 0
2021-10-14 04:15 | 0.40019 | 1.2972 | 0.43694 | 1.6562 | 0 | 0 | 0 | 0
2021-10-14 04:30 | 0.29198 | 1.2972 | 0.35935 | 1.6085 | 0 | 0 | 0 | 0
2021-10-14 04:45 | 0.30218 | 1.229 | 0.30218 | 1.5407 | 0 | 0 | 0 | 0
2021-10-14 05:00 | 0.3175 | 1.1853 | 0.30014 | 1.5608 | 0 | 0 | 0 | 0
2021-10-14 05:15 | 0.31648 | 1.3446 | 0.31341 | 1.5285 | 0 | 0 | 0 | 0
2021-10-14 05:30 | 0.38692 | 1.2688 | 0.33383 | 1.5239 | 0 | 0 | 0 | 0
2021-10-14 05:45 | 0.26441 | 1.2403 | 0.42061 | 1.5734 | 0 | 0.016786 | 0.006575 | 0.012854
2021-10-14 06:00 | 0.28279 | 1.1686 | 0.39815 | 1.1341 | 0 | 0.04076 | 0.016604 | 0.031586
2021-10-14 06:15 | 0.31954 | 1.2159 | 0.30218 | 1.0718 | 0 | 0.064321 | 0.026633 | 0.050317
2021-10-14 06:30 | 2.2766 | 1.7928 | 2.2153 | 2.2198 | 0 | 0.088239 | 0.036662 | 0.069049
2021-10-14 06:45 | 1.5824 | 1.8392 | 2.491 | 2.4244 | 0.051826 | 0.1138 | 0.092341 | 0.12762
2021-10-14 07:00 | 0.80447 | 1.6565 | 1.1536 | 2.1509 | 0.13193 | 0.13861 | 0.17204 | 0.20461
2021-10-14 07:15 | 0.39202 | 1.5973 | 1.123 | 1.8836 | 0.21203 | 0.18014 | 0.25174 | 0.2816
2021-10-14 07:30 | 0.44511 | 1.5711 | 0.51862 | 1.8155 | 0.29213 | 0.20855 | 0.33144 | 0.3586
2021-10-14 07:45 | 0.5717 | 1.3309 | 0.53087 | 1.7433 | 0.31975 | 0.24705 | 0.38132 | 0.39357
2021-10-14 08:00 | 0.58804 | 1.5635 | 2.103 | 2.2346 | 0.31867 | 0.2791 | 0.41549 | 0.40977
2021-10-14 08:15 | 0.75546 | 1.5744 | 0.61662 | 2.0912 | 0.3176 | 0.31344 | 0.44965 | 0.42597
2021-10-14 08:30 | 0.49411 | 1.3511 | 0.4737 | 1.9794 | 0.31653 | 0.33381 | 0.48382 | 0.44217
2021-10-14 08:45 | 0.61254 | 1.5538 | 0.53087 | 2.2569 | 0.32116 | 0.34112 | 0.52006 | 0.46361
2021-10-14 09:00 | 0.44103 | 1.5576 | 0.54312 | 2.2007 | 0.3289 | 0.34482 | 0.55739 | 0.48728
2021-10-14 09:15 | 0.39611 | 1.5761 | 0.53495 | 2.0254 | 0.33665 | 0.34852 | 0.59472 | 0.51095
2021-10-14 09:30 | 0.39917 | 1.5761 | 0.51453 | 1.868 | 0.3444 | 0.36167 | 0.63205 | 0.53463
2021-10-14 09:45 | 0.52678 | 1.5761 | 0.44511 | 1.8638 | 0.39148 | 0.35549 | 0.61394 | 0.53509
2021-10-14 10:00 | 0.55537 | 1.5079 | 0.46553 | 2.0797 | 0.46011 | 0.35856 | 0.56653 | 0.52404
2021-10-14 10:15 | 0.46961 | 1.4205 | 0.4737 | 1.6704 | 0.52874 | 0.36163 | 0.51912 | 0.51299
2021-10-14 10:30 | 0.53087 | 1.3152 | 0.45328 | 1.2512 | 0.59738 | 0.3647 | 0.4717 | 0.50194
2021-10-14 10:45 | 0.4982 | 1.1032 | 0.48595 | 1.2196 | 0.62662 | 0.36137 | 0.45176 | 0.478
2021-10-14 11:00 | 0.42469 | 1.0394 | 0.61254 | 1.2263 | 0.63425 | 0.35983 | 0.44635 | 0.44774
2021-10-14 11:15 | 0.44103 | 1.1018 | 0.62887 | 1.2314 | 0.64187 | 0.36826 | 0.44094 | 0.41748
2021-10-14 11:30 | 0.44919 | 1.1413 | 0.52678 | 1.2184 | 0.6495 | 0.26768 | 0.43553 | 0.38721
2021-10-14 11:45 | 0.3614 | 1.2937 | 0.62479 | 1.5471 | 0.65351 | 0.23822 | 0.39446 | 0.37306
2021-10-14 12:00 | 0.23685 | 1.1601 | 2.542 | 1.7235 | 0.65555 | 0.31204 | 0.33447 | 0.36697
2021-10-14 12:15 | 0.2246 | 1.0545 | 1.3578 | 2.0179 | 0.65758 | 0.34213 | 0.27448 | 0.36089
2021-10-14 12:30 | 0.25318 | 1.2566 | 0.81672 | 1.9351 | 0.65962 | 0.34391 | 0.2145 | 0.3548
2021-10-14 12:45 | 0.24195 | 1.2421 | 1.1434 | 1.7989 | 0.65784 | 0.34369 | 0.21224 | 0.35949
2021-10-14 13:00 | 0.28279 | 1.1604 | 0.90656 | 1.7353 | 0.65396 | 0.30616 | 0.24064 | 0.36923
2021-10-14 13:15 | 0.34506 | 1.1749 | 0.51862 | 1.6883 | 0.65009 | 0.29167 | 0.26905 | 0.37897
2021-10-14 13:30 | 0.31137 | 1.1429 | 1.7355 | 1.8368 | 0.64621 | 0.21818 | 0.29745 | 0.3887
2021-10-14 13:45 | 0.23889 | 1.1429 | 2.6033 | 1.9822 | 0.63976 | 0.2514 | 0.30447 | 0.37183
2021-10-14 14:00 | 0.23276 | 1.1749 | 0.46553 | 1.6874 | 0.63188 | 0.26824 | 0.30013 | 0.34286
2021-10-14 14:15 | 0.23378 | 1.0592 | 0.40836 | 1.6648 | 0.62401 | 0.26583 | 0.29579 | 0.31388
2021-10-14 14:30 | 0.25114 | 1.0592 | 0.36344 | 1.6644 | 0.61614 | 0.26954 | 0.29144 | 0.28491
2021-10-14 14:45 | 0.35731 | 1.0592 | 0.34608 | 1.6692 | 0.60076 | 0.28693 | 0.3252 | 0.28769
2021-10-14 15:00 | 0.29708 | 1.1769 | 0.51045 | 1.6978 | 0.58124 | 0.30022 | 0.37925 | 0.30519
2021-10-14 15:15 | 0.22256 | 1.1666 | 0.42061 | 2.1684 | 0.56171 | 0.30422 | 0.4333 | 0.32268
2021-10-14 15:30 | 0.22153 | 1.1065 | 0.39815 | 1.7625 | 0.54219 | 0.30749 | 0.48735 | 0.34018
2021-10-14 15:45 | 0.21439 | 1.2274 | 0.38794 | 1.4748 | 0.47661 | 0.28263 | 0.46019 | 0.326
2021-10-14 16:00 | 0.2981 | 1.107 | 0.49003 | 1.2533 | 0.38557 | 0.23273 | 0.38971 | 0.29626
2021-10-14 16:15 | 0.35323 | 1.2366 | 0.50228 | 1.2889 | 0.29452 | 0.19584 | 0.31922 | 0.26652
2021-10-14 16:30 | 0.2491 | 1.2366 | 0.43694 | 1.2897 | 0.20347 | 0.15299 | 0.24874 | 0.23678
2021-10-14 16:45 | 0.21541 | 1.1311 | 0.45736 | 1.7156 | 0.14351 | 0.10945 | 0.18767 | 0.18825
2021-10-14 17:00 | 0.25931 | 1.2271 | 0.53087 | 1.921 | 0.10075 | 0.065526 | 0.13162 | 0.13153
2021-10-14 17:15 | 0.22664 | 1.1337 | 0.58804 | 1.7772 | 0.058004 | 0.041436 | 0.07558 | 0.074814
2021-10-14 17:30 | 0.35323 | 1.135 | 0.51045 | 1.654 | 0.015253 | 0.009993 | 0.019535 | 0.018095
2021-10-14 17:45 | 0.31546 | 1.2106 | 0.46961 | 1.7922 | 0 | 0 | 0 | 0
2021-10-14 18:00 | 0.24093 | 1.4358 | 0.46144 | 2.1532 | 0 | 0 | 0 | 0
2021-10-14 18:15 | 0.26135 | 1.6571 | 0.55945 | 2.5861 | 0 | 0 | 0 | 0
2021-10-14 18:30 | 0.23685 | 1.7149 | 2.491 | 2.9134 | 0 | 0 | 0 | 0
2021-10-14 18:45 | 0.2981 | 1.9297 | 3.6854 | 3.7463 | 0 | 0 | 0 | 0
2021-10-14 19:00 | 0.35323 | 1.1572 | 1.4088 | 1.373 | 0 | 0 | 0 | 0
2021-10-14 19:15 | 0.25318 | 0.95825 | 1.1638 | 0.92683 | 0 | 0 | 0 | 0
2021-10-14 19:30 | 0.49411 | 0.95825 | 1.1944 | 0.91414 | 0 | 0 | 0 | 0
2021-10-14 19:45 | 1.0821 | 0.95118 | 0.69013 | 0.93937 | 0 | 0 | 0 | 0
2021-10-14 20:00 | 0.24399 | 0.93944 | 0.70646 | 0.75969 | 0 | 0 | 0 | 0
2021-10-14 20:15 | 0.35017 | 0.83267 | 0.70238 | 0.64185 | 0 | 0 | 0 | 0
2021-10-14 20:30 | 0.3175 | 0.84135 | 1.2761 | 0.6277 | 0 | 0 | 0 | 0
2021-10-14 20:45 | 0.2491 | 0.84063 | 1.0719 | 0.56689 | 0 | 0 | 0 | 0
2021-10-14 21:00 | 0.25012 | 0.81686 | 1.0924 | 0.58847 | 0 | 0 | 0 | 0
2021-10-14 21:15 | 0.33179 | 0.627 | 0.56354 | 0.48668 | 0 | 0 | 0 | 0
2021-10-14 21:30 | 0.4053 | 0.61089 | 0.58804 | 0.49324 | 0 | 0 | 0 | 0
2021-10-14 21:45 | 0.38488 | 0.627 | 0.39713 | 0.43461 | 0 | 0 | 0 | 0
2021-10-14 22:00 | 3.2362 | 2.1184 | 3.1852 | 3.3383 | 0 | 0 | 0 | 0
2021-10-14 22:15 | 3.3587 | 2.4948 | 3.369 | 3.4258 | 0 | 0 | 0 | 0
2021-10-14 22:30 | 3.3996 | 2.7243 | 3.3996 | 3.1371 | 0 | 0 | 0 | 0
2021-10-14 22:45 | 3.5119 | 2.5462 | 3.3996 | 3.0846 | 0 | 0 | 0 | 0
2021-10-14 23:00 | 3.4506 | 2.3664 | 3.5017 | 3.0265 | 0 | 0 | 0 | 0
2021-10-14 23:15 | 3.3894 | 2.3664 | 3.5119 | 3.0081 | 0 | 0 | 0 | 0
2021-10-14 23:30 | 3.3485 | 2.3664 | 3.3485 | 2.9736 | 0 | 0 | 0 | 0
2021-10-14 23:45 | 3.4404 | 2.671 | 3.3485 | 2.9693 | 0 | 0 | 0 | 0
2021-10-15 | 3.5221 | 2.5478 | 3.4404 | 3.0237 | 0 | 0 | 0 | 0
2021-10-15 00:15 | 3.3894 | 2.2997 | 3.4302 | 3.2842 | 0 | 0 | 0 | 0
2021-10-15 00:30 | 3.3894 | 2.5155 | 3.5629 | 3.2923 | 0 | 0 | 0 | 0
2021-10-15 00:45 | 3.4098 | 2.2997 | 3.4404 | 3.2583 | 0 | 0 | 0 | 0
2021-10-15 01:00 | 3.4813 | 2.2997 | 3.3996 | 3.2447 | 0 | 0 | 0 | 0
2021-10-15 01:15 | 3.3792 | 2.6169 | 3.369 | 3.2825 | 0 | 0 | 0 | 0
2021-10-15 01:30 | 3.4098 | 2.5155 | 3.4098 | 3.2946 | 0 | 0 | 0 | 0
2021-10-15 01:45 | 3.3894 | 2.2692 | 3.5119 | 3.3152 | 0 | 0 | 0 | 0
2021-10-15 02:00 | 3.4302 | 2.1677 | 3.4915 | 3.064 | 0 | 0 | 0 | 0
2021-10-15 02:15 | 3.4915 | 2.3885 | 3.4506 | 2.9231 | 0 | 0 | 0 | 0
2021-10-15 02:30 | 3.3894 | 2.3507 | 2.9198 | 2.7758 | 0 | 0 | 0 | 0
2021-10-15 02:45 | 3.3894 | 2.2425 | 1.4497 | 2.5622 | 0 | 0 | 0 | 0
2021-10-15 03:00 | 3.3894 | 2.1056 | 0.68196 | 2.2219 | 0 | 0 | 0 | 0
2021-10-15 03:15 | 3.5017 | 1.643 | 0.82897 | 2.1182 | 0 | 0 | 0 | 0
2021-10-15 03:30 | 3.471 | 1.6349 | 0.27564 | 1.9989 | 0 | 0 | 0 | 0
2021-10-15 03:45 | 3.3894 | 2.1766 | 0.26748 | 1.9593 | 0 | 0 | 0 | 0
2021-10-15 04:00 | 3.4302 | 1.4597 | 0.30218 | 1.8117 | 0 | 0 | 0 | 0
2021-10-15 04:15 | 3.471 | 1.5909 | 0.40019 | 1.6685 | 0 | 0 | 0 | 0
2021-10-15 04:30 | 3.5017 | 1.3139 | 0.29198 | 1.6056 | 0 | 0 | 0 | 0
2021-10-15 04:45 | 3.3894 | 1.2339 | 0.30218 | 1.5387 | 0 | 0 | 0 | 0
2021-10-15 05:00 | 3.3894 | 1.234 | 0.3175 | 1.5605 | 0 | 0 | 0 | 0
2021-10-15 05:15 | 3.3077 | 1.245 | 0.31648 | 1.5292 | 0 | 0 | 0 | 0
2021-10-15 05:30 | 2.0418 | 1.2583 | 0.38692 | 1.5343 | 0 | 0 | 0 | 0
2021-10-15 05:45 | 1.2863 | 1.2854 | 0.26441 | 1.5659 | 0 | 0.014007 | 0 | 0.011776
2021-10-15 06:00 | 0.29198 | 1.1263 | 0.28279 | 1.1287 | 0 | 0.033018 | 0 | 0.028977
2021-10-15 06:15 | 0.26135 | 1.0554 | 0.31954 | 1.0724 | 0 | 0.049627 | 0 | 0.046179
2021-10-15 06:30 | 0.3369 | 1.6466 | 2.2766 | 2.3218 | 0 | 0.071765 | 0 | 0.063381
2021-10-15 06:45 | 0.92289 | 2.0382 | 1.5824 | 2.2581 | 0.063474 | 0.14894 | 0.051826 | 0.11936
2021-10-15 07:00 | 1.6743 | 1.588 | 0.80447 | 2.1069 | 0.16284 | 0.23576 | 0.13193 | 0.19427
2021-10-15 07:15 | 1.2455 | 1.5335 | 0.39202 | 1.8083 | 0.26221 | 0.2895 | 0.21203 | 0.26917
2021-10-15 07:30 | 0.72688 | 1.376 | 0.44511 | 1.7653 | 0.36158 | 0.35834 | 0.29213 | 0.34408
2021-10-15 07:45 | 0.53495 | 1.3917 | 0.5717 | 1.738 | 0.40964 | 0.39175 | 0.31975 | 0.38592
2021-10-15 08:00 | 0.71054 | 1.6455 | 0.58804 | 2.2235 | 0.42863 | 0.41655 | 0.31867 | 0.41181
2021-10-15 08:15 | 0.61254 | 1.6455 | 0.75546 | 2.1046 | 0.44762 | 0.44575 | 0.3176 | 0.43771
2021-10-15 08:30 | 0.52678 | 1.666 | 0.49411 | 1.9846 | 0.46662 | 0.47245 | 0.31653 | 0.4636
2021-10-15 08:45 | 0.39917 | 1.7224 | 0.61254 | 2.2715 | 0.44886 | 0.48279 | 0.32116 | 0.48769
2021-10-15 09:00 | 0.52678 | 1.676 | 0.44103 | 2.1815 | 0.41026 | 0.48503 | 0.3289 | 0.51116
2021-10-15 09:15 | 0.56354 | 1.6966 | 0.39611 | 2.0085 | 0.37166 | 0.49024 | 0.33665 | 0.53463
2021-10-15 09:30 | 0.62887 | 1.6966 | 0.39917 | 1.8434 | 0.33305 | 0.49544 | 0.3444 | 0.55809
2021-10-15 09:45 | 0.64521 | 1.7119 | 0.52678 | 1.865 | 0.35304 | 0.50004 | 0.39148 | 0.56618
2021-10-15 10:00 | 0.60029 | 1.7119 | 0.55537 | 2.0856 | 0.4063 | 0.50436 | 0.46011 | 0.56676
2021-10-15 10:15 | 0.44103 | 1.8193 | 0.46961 | 1.6529 | 0.45956 | 0.50868 | 0.52874 | 0.56735
2021-10-15 10:30 | 0.38488 | 1.3566 | 0.53087 | 1.2477 | 0.51283 | 0.513 | 0.59738 | 0.56793
2021-10-15 10:45 | 2.4501 | 1.2746 | 0.4982 | 1.2301 | 0.52774 | 0.51285 | 0.62662 | 0.54989
2021-10-15 11:00 | 0.81672 | 1.2468 | 0.42469 | 1.2263 | 0.52083 | 0.51555 | 0.63425 | 0.52238
2021-10-15 11:15 | 0.45736 | 1.3091 | 0.44103 | 1.2331 | 0.51392 | 0.52582 | 0.64187 | 0.49488
2021-10-15 11:30 | 0.5227 | 1.3664 | 0.44919 | 1.2496 | 0.50701 | 0.53018 | 0.6495 | 0.46737
2021-10-15 11:45 | 0.44103 | 1.6708 | 0.3614 | 1.5732 | 0.51944 | 0.52974 | 0.65351 | 0.44424
2021-10-15 12:00 | 0.36752 | 1.3423 | 0.23685 | 1.73 | 0.54289 | 0.52352 | 0.65555 | 0.42416
2021-10-15 12:15 | 2.1541 | 1.4507 | 0.2246 | 2.0077 | 0.56633 | 0.52431 | 0.65758 | 0.40408
2021-10-15 12:30 | 3.2975 | 1.7283 | 0.25318 | 1.9304 | 0.58978 | 0.50649 | 0.65962 | 0.38399
2021-10-15 12:45 | 0.21541 | 1.5432 | 0.24195 | 1.793 | 0.57362 | 0.50616 | 0.65784 | 0.3857
2021-10-15 13:00 | 0.2981 | 1.5141 | 0.28279 | 1.7369 | 0.53486 | 0.51061 | 0.65396 | 0.39704
2021-10-15 13:15 | 0.33587 | 1.5141 | 0.34506 | 1.7115 | 0.4961 | 0.53359 | 0.65009 | 0.40838
2021-10-15 13:30 | 0.33894 | 1.5432 | 0.31137 | 1.8552 | 0.45734 | 0.53963 | 0.64621 | 0.41972
2021-10-15 13:45 | 0.30218 | 1.5432 | 0.23889 | 1.9905 | 0.43729 | 0.51707 | 0.63976 | 0.41181
2021-10-15 14:00 | 0.342 | 1.4216 | 0.23276 | 1.6952 | 0.42794 | 0.51173 | 0.63188 | 0.39489
2021-10-15 14:15 | 0.3471 | 1.5141 | 0.23378 | 1.6726 | 0.41858 | 0.50331 | 0.62401 | 0.37797
2021-10-15 14:30 | 0.33792 | 1.6242 | 0.25114 | 1.674 | 0.40922 | 0.498 | 0.61614 | 0.36105
2021-10-15 14:45 | 0.46553 | 1.5563 | 0.35731 | 1.6837 | 0.40905 | 0.48611 | 0.60076 | 0.35936
2021-10-15 15:00 | 0.37977 | 1.4498 | 0.29708 | 1.6997 | 0.41415 | 0.4712 | 0.58124 | 0.36523
2021-10-15 15:15 | 0.40427 | 1.3656 | 0.22256 | 2.1602 | 0.41925 | 0.45628 | 0.56171 | 0.37111
2021-10-15 15:30 | 0.53903 | 1.4955 | 0.22153 | 1.7581 | 0.42434 | 0.44137 | 0.54219 | 0.37698
2021-10-15 15:45 | 1.123 | 1.4478 | 0.21439 | 1.4751 | 0.38637 | 0.38691 | 0.47661 | 0.34975
2021-10-15 16:00 | 0.87389 | 1.3955 | 0.2981 | 1.2655 | 0.32371 | 0.3289 | 0.38557 | 0.3055
2021-10-15 16:15 | 0.85347 | 1.4804 | 0.35323 | 1.3097 | 0.26105 | 0.27354 | 0.29452 | 0.26126
2021-10-15 16:30 | 1.6334 | 1.4936 | 0.2491 | 1.2953 | 0.1984 | 0.25233 | 0.20347 | 0.21701
2021-10-15 16:45 | 1.3272 | 1.4257 | 0.21541 | 1.7161 | 0.14767 | 0.20626 | 0.14351 | 0.16811
2021-10-15 17:00 | 1.2761 | 1.5769 | 0.25931 | 1.9113 | 0.10379 | 0.13904 | 0.10075 | 0.1176
2021-10-15 17:15 | 0.63704 | 1.4366 | 0.22664 | 1.7654 | 0.059901 | 0.061605 | 0.058004 | 0.067095
2021-10-15 17:30 | 0.55128 | 1.4119 | 0.35323 | 1.66 | 0.016017 | 0.013756 | 0.015253 | 0.016587
2021-10-15 17:45 | 1.8172 | 1.6997 | 0.31546 | 1.8045 | 0 | 0 | 0 | 0
2021-10-15 18:00 | 1.2659 | 1.5192 | 0.24093 | 1.8157 | 0 | 0 | 0 | 0
2021-10-15 18:15 | 0.91064 | 1.3124 | 0.26135 | 2.2326 | 0 | 0 | 0 | 0
2021-10-15 18:30 | 0.46144 | 1.3947 | 0.23685 | 2.5564 | 0 | 0 | 0 | 0
2021-10-15 18:45 | 0.41653 | 2.4095 | 0.2981 | 3.398 | 0 | 0 | 0 | 0
2021-10-15 19:00 | 1.9397 | 1.3578 | 0.35323 | 1.3575 | 0 | 0 | 0 | 0
2021-10-15 19:15 | 1.5926 | 0.95118 | 0.25318 | 0.91881 | 0 | 0 | 0 | 0
2021-10-15 19:30 | 0.4982 | 1.0218 | 0.49411 | 0.93952 | 0 | 0 | 0 | 0
2021-10-15 19:45 | 0.57987 | 1.1323 | 1.0821 | 1.062 | 0 | 0 | 0 | 0
2021-10-15 20:00 | 0.62887 | 0.97285 | 0.24399 | 0.77019 | 0 | 0 | 0 | 0
2021-10-15 20:15 | 0.66562 | 0.8544 | 0.35017 | 0.66723 | 0 | 0 | 0 | 0
2021-10-15 20:30 | 0.66154 | 0.8544 | 0.3175 | 0.64827 | 0 | 0 | 0 | 0
2021-10-15 20:45 | 0.5227 | 0.78008 | 0.2491 | 0.56193 | 0 | 0 | 0 | 0
2021-10-15 21:00 | 0.50228 | 0.69497 | 0.25012 | 0.5437 | 0 | 0 | 0 | 0
2021-10-15 21:15 | 0.41244 | 0.69253 | 0.33179 | 0.48668 | 0 | 0 | 0 | 0
2021-10-15 21:30 | 0.35527 | 0.70864 | 0.4053 | 0.48697 | 0 | 0 | 0 | 0
2021-10-15 21:45 | 0.33077 | 0.70864 | 0.38488 | 0.44146 | 0 | 0 | 0 | 0
2021-10-15 22:00 | 0.31035 | 2.5089 | 3.2362 | 3.3383 | 0 | 0 | 0 | 0
2021-10-15 22:15 | 0.39202 | 2.4156 | 3.3587 | 3.4171 | 0 | 0 | 0 | 0
2021-10-15 22:30 | 0.37773 | 2.446 | 3.3996 | 3.1356 | 0 | 0 | 0 | 0
2021-10-15 22:45 | 0.25114 | 2.2051 | 3.5119 | 3.1123 | 0 | 0 | 0 | 0
2021-10-15 23:00 | 0.27666 | 2.5128 | 3.4506 | 3.0499 | 0 | 0 | 0 | 0
2021-10-15 23:15 | 0.2297 | 2.5803 | 3.3894 | 3.0213 | 0 | 0 | 0 | 0
2021-10-15 23:30 | 0.31546 | 2.6083 | 3.3485 | 2.9809 | 0 | 0 | 0 | 0
2021-10-15 23:45 | 0.37263 | 2.6083 | 3.4404 | 2.9737 | 0 | 0 | 0 | 0
2021-10-16 | 0.28687 | 1.9483 | 3.5221 | 3.0412 | 0 | 0 | 0 | 0
2021-10-16 00:15 | 0.24297 | 2.0961 | 3.3894 | 3.2959 | 0 | 0 | 0 | 0
2021-10-16 00:30 | 0.2246 | 2.0961 | 3.3894 | 3.301 | 0 | 0 | 0 | 0
2021-10-16 00:45 | 0.35731 | 2.0588 | 3.4098 | 3.2743 | 0 | 0 | 0 | 0
2021-10-16 01:00 | 0.33996 | 2.0588 | 3.4813 | 3.2695 | 0 | 0 | 0 | 0
2021-10-16 01:15 | 0.23174 | 2.0588 | 3.3792 | 3.2767 | 0 | 0 | 0 | 0
2021-10-16 01:30 | 0.24706 | 2.0682 | 3.4098 | 3.3063 | 0 | 0 | 0 | 0
2021-10-16 01:45 | 0.31852 | 2.0656 | 3.3894 | 3.3268 | 0 | 0 | 0 | 0
2021-10-16 02:00 | 0.34302 | 2.0393 | 3.4302 | 3.0815 | 0 | 0 | 0 | 0
2021-10-16 02:15 | 0.25522 | 1.9493 | 3.4915 | 2.9406 | 0 | 0 | 0 | 0
2021-10-16 02:30 | 0.26543 | 1.9015 | 3.3894 | 2.77 | 0 | 0 | 0 | 0
2021-10-16 02:45 | 0.32056 | 1.6673 | 3.3894 | 2.5622 | 0 | 0 | 0 | 0
2021-10-16 03:00 | 0.30831 | 1.3419 | 3.3894 | 2.2307 | 0 | 0 | 0 | 0
2021-10-16 03:15 | 0.22153 | 1.3419 | 3.5017 | 2.1474 | 0 | 0 | 0 | 0
2021-10-16 03:30 | 0.24808 | 1.2038 | 3.471 | 2.0223 | 0 | 0 | 0 | 0
2021-10-16 03:45 | 0.37977 | 1.0195 | 3.3894 | 1.9636 | 0 | 0 | 0 | 0
2021-10-16 04:00 | 0.35527 | 1.0195 | 3.4302 | 1.9823 | 0 | 0 | 0 | 0
2021-10-16 04:15 | 0.2491 | 1.1245 | 3.471 | 2.0296 | 0 | 0 | 0 | 0
2021-10-16 04:30 | 0.23174 | 1.0785 | 3.5017 | 1.9979 | 0 | 0 | 0 | 0
2021-10-16 04:45 | 0.34506 | 1.0785 | 3.3894 | 1.9674 | 0 | 0 | 0 | 0
2021-10-16 05:00 | 0.24297 | 1.2702 | 3.3894 | 2.0033 | 0 | 0 | 0 | 0
2021-10-16 05:15 | 0.2246 | 1.2353 | 3.3077 | 1.9714 | 0 | 0 | 0 | 0
2021-10-16 05:30 | 0.33383 | 1.3669 | 2.0418 | 1.7949 | 0 | 0 | 0 | 0
2021-10-16 05:45 | 0.34915 | 1.2949 | 1.2863 | 1.7041 | 0 | 0.004305 | 0 | 0.008178
2021-10-16 06:00 | 0.28993 | 1.068 | 0.29198 | 1.1254 | 0 | 0.003063 | 0 | 0.020216
2021-10-16 06:15 | 0.25829 | 1.0641 | 0.26135 | 1.0806 | 0 | 0.005731 | 0 | 0.032254
2021-10-16 06:30 | 0.4053 | 1.6062 | 0.3369 | 2.1848 | 0 | 0.02844 | 0 | 0.044292
2021-10-16 06:45 | 0.51045 | 1.6853 | 0.92289 | 1.9962 | 0.009141 | 0.10426 | 0.063474 | 0.097456
2021-10-16 07:00 | 0.65337 | 1.6797 | 1.6743 | 2.1477 | 0.023637 | 0.18421 | 0.16284 | 0.17173
2021-10-16 07:15 | 0.3614 | 1.5622 | 1.2455 | 1.8941 | 0.038133 | 0.24142 | 0.26221 | 0.24601
2021-10-16 07:30 | 0.45736 | 1.6523 | 0.72688 | 1.805 | 0.052629 | 0.2985 | 0.36158 | 0.32029
2021-10-16 07:45 | 0.46961 | 1.6752 | 0.53495 | 1.7392 | 0.061153 | 0.32909 | 0.40964 | 0.36197
2021-10-16 08:00 | 0.52678 | 1.3934 | 0.71054 | 2.2474 | 0.066173 | 0.35289 | 0.42863 | 0.38694
2021-10-16 08:15 | 0.45736 | 1.6647 | 0.61254 | 2.1087 | 0.071193 | 0.37889 | 0.44762 | 0.41192
2021-10-16 08:30 | 0.36548 | 1.6853 | 0.52678 | 1.987 | 0.076212 | 0.40571 | 0.46662 | 0.43689
2021-10-16 08:45 | 0.37977 | 1.6552 | 0.39917 | 1.9946 | 0.077818 | 0.41459 | 0.44886 | 0.45626
2021-10-16 09:00 | 0.37569 | 1.6017 | 0.52678 | 2.1698 | 0.077418 | 0.41909 | 0.41026 | 0.47267
2021-10-16 09:15 | 0.38692 | 1.6888 | 0.56354 | 2.0114 | 0.077018 | 0.42359 | 0.37166 | 0.48907
2021-10-16 09:30 | 0.50228 | 1.5959 | 0.62887 | 1.8574 | 0.076618 | 0.42809 | 0.33305 | 0.50548
2021-10-16 09:45 | 0.42878 | 1.6888 | 0.64521 | 1.8942 | 0.081861 | 0.43206 | 0.35304 | 0.51562
2021-10-16 10:00 | 0.24195 | 1.5095 | 0.60029 | 2.1107 | 0.090426 | 0.43579 | 0.4063 | 0.52334
2021-10-16 10:15 | 0.21745 | 1.7106 | 0.44103 | 1.6319 | 0.09899 | 0.43952 | 0.45956 | 0.53106
2021-10-16 10:30 | 0.21949 | 1.3689 | 0.38488 | 1.2543 | 0.10755 | 0.44325 | 0.51283 | 0.53878
2021-10-16 10:45 | 0.28381 | 1.4433 | 2.4501 | 1.5314 | 0.10457 | 0.44313 | 0.52774 | 0.52305
2021-10-16 11:00 | 1.9907 | 1.4518 | 0.81672 | 1.2881 | 0.094778 | 0.44124 | 0.52083 | 0.49504
2021-10-16 11:15 | 1.1434 | 1.3775 | 0.45736 | 1.249 | 0.084986 | 0.43936 | 0.51392 | 0.46703
2021-10-16 11:30 | 0.31239 | 1.3775 | 0.5227 | 1.2607 | 0.075194 | 0.45503 | 0.50701 | 0.43902
2021-10-16 11:45 | 0.29912 | 1.797 | 0.44103 | 1.5779 | 0.066071 | 0.45465 | 0.51944 | 0.43528
2021-10-16 12:00 | 0.3175 | 1.2767 | 0.36752 | 1.7362 | 0.057341 | 0.44987 | 0.54289 | 0.44371
2021-10-16 12:15 | 0.37058 | 1.3358 | 2.1541 | 2.2775 | 0.048612 | 0.43777 | 0.56633 | 0.45213
2021-10-16 12:30 | 1.5007 | 1.2916 | 3.2975 | 2.2425 | 0.039883 | 0.44122 | 0.58978 | 0.46056
2021-10-16 12:45 | 2.3072 | 1.1931 | 0.21541 | 1.7757 | 0.09427 | 0.44093 | 0.57362 | 0.46081
2021-10-16 13:00 | 0.20622 | 1.4591 | 0.2981 | 1.727 | 0.18596 | 0.44166 | 0.53486 | 0.45678
2021-10-16 13:15 | 0.22358 | 1.5352 | 0.33587 | 1.7163 | 0.27766 | 0.44201 | 0.4961 | 0.45274
2021-10-16 13:30 | 0.35935 | 1.4304 | 0.33894 | 1.8575 | 0.36935 | 0.43635 | 0.45734 | 0.44871
2021-10-16 13:45 | 0.24297 | 1.4797 | 0.30218 | 1.9888 | 0.4264 | 0.45173 | 0.43729 | 0.43664
2021-10-16 14:00 | 0.21439 | 1.4536 | 0.342 | 1.7044 | 0.46292 | 0.44355 | 0.42794 | 0.42084
2021-10-16 14:15 | 0.22153 | 1.3954 | 0.3471 | 1.672 | 0.49945 | 0.43892 | 0.41858 | 0.40504
2021-10-16 14:30 | 0.31444 | 1.3758 | 0.33792 | 1.6517 | 0.53598 | 0.43429 | 0.40922 | 0.38925
2021-10-16 14:45 | 0.31341 | 1.5066 | 0.46553 | 1.6936 | 0.54207 | 0.42392 | 0.40905 | 0.38781
2021-10-16 15:00 | 0.20928 | 1.3793 | 0.37977 | 1.7014 | 0.53012 | 0.41091 | 0.41415 | 0.39371
2021-10-16 15:15 | 0.22562 | 1.3179 | 0.40427 | 2.1716 | 0.51816 | 0.38014 | 0.41925 | 0.39961
2021-10-16 15:30 | 0.22868 | 1.392 | 0.53903 | 1.7698 | 0.5062 | 0.36772 | 0.42434 | 0.40551
2021-10-16 15:45 | 0.31852 | 1.4016 | 1.123 | 1.555 | 0.45208 | 0.31513 | 0.38637 | 0.37178
2021-10-16 16:00 | 0.2736 | 1.4279 | 0.87389 | 1.3409 | 0.37292 | 0.2655 | 0.32371 | 0.31735
2021-10-16 16:15 | 0.31444 | 1.5708 | 0.85347 | 1.3109 | 0.29376 | 0.21669 | 0.26105 | 0.26291
2021-10-16 16:30 | 0.45736 | 1.4242 | 1.6334 | 1.3997 | 0.2146 | 0.19377 | 0.1984 | 0.20847
2021-10-16 16:45 | 0.53903 | 1.3925 | 1.3272 | 1.7872 | 0.15607 | 0.15914 | 0.14767 | 0.1584
2021-10-16 17:00 | 0.60845 | 1.4735 | 1.2761 | 1.9404 | 0.1098 | 0.10573 | 0.10379 | 0.11094
2021-10-16 17:15 | 0.50636 | 1.2101 | 0.63704 | 1.6974 | 0.063533 | 0.052057 | 0.059901 | 0.063474
2021-10-16 17:30 | 0.49003 | 1.1973 | 0.55128 | 1.5462 | 0.017267 | 0.010908 | 0.016017 | 0.016012
2021-10-16 17:45 | 0.50636 | 1.2497 | 1.8172 | 1.8949 | 0 | 0 | 0 | 0
2021-10-16 18:00 | 0.60437 | 1.6187 | 1.2659 | 1.8834 | 0 | 0 | 0 | 0
2021-10-16 18:15 | 0.53495 | 1.5575 | 0.91064 | 2.2868 | 0 | 0 | 0 | 0
2021-10-16 18:30 | 1.5926 | 1.5226 | 0.46144 | 2.5459 | 0 | 0 | 0 | 0
2021-10-16 18:45 | 0.58395 | 1.5474 | 0.41653 | 2.9077 | 0 | 0 | 0 | 0
2021-10-16 19:00 | 0.65746 | 1.3521 | 1.9397 | 1.3896 | 0 | 0 | 0 | 0
2021-10-16 19:15 | 0.73096 | 1.1589 | 1.5926 | 1.0999 | 0 | 0 | 0 | 0
2021-10-16 19:30 | 0.72688 | 1.0665 | 0.4982 | 0.94302 | 0 | 0 | 0 | 0
2021-10-16 19:45 | 0.73096 | 1.2377 | 0.57987 | 1.0597 | 0 | 0 | 0 | 0
2021-10-16 20:00 | 0.61662 | 1.0307 | 0.62887 | 0.77078 | 0 | 0 | 0 | 0
2021-10-16 20:15 | 0.53903 | 1.004 | 0.66562 | 0.68823 | 0 | 0 | 0 | 0
2021-10-16 20:30 | 0.50636 | 0.87793 | 0.66154 | 0.66752 | 0 | 0 | 0 | 0
2021-10-16 20:45 | 0.56354 | 0.79608 | 0.5227 | 0.56076 | 0 | 0 | 0 | 0
2021-10-16 21:00 | 0.56762 | 0.70737 | 0.50228 | 0.5402 | 0 | 0 | 0 | 0
2021-10-16 21:15 | 0.51862 | 0.61893 | 0.41244 | 0.48084 | 0 | 0 | 0 | 0
2021-10-16 21:30 | 0.70646 | 0.61926 | 0.35527 | 0.4788 | 0 | 0 | 0 | 0
2021-10-16 21:45 | 0.50228 | 0.61089 | 0.33077 | 0.4298 | 0 | 0 | 0 | 0
2021-10-16 22:00 | 0.56354 | 1.7726 | 0.31035 | 2.8985 | 0 | 0 | 0 | 0
2021-10-16 22:15 | 0.56354 | 2.2741 | 0.39202 | 2.9772 | 0 | 0 | 0 | 0
2021-10-16 22:30 | 0.55945 | 2.1685 | 0.37773 | 2.7112 | 0 | 0 | 0 | 0
2021-10-16 22:45 | 0.6207 | 2.2426 | 0.25114 | 2.6756 | 0 | 0 | 0 | 0
2021-10-16 23:00 | 0.42061 | 2.1115 | 0.27666 | 2.611 | 0 | 0 | 0 | 0
2021-10-16 23:15 | 0.31648 | 2.1178 | 0.2297 | 2.5553 | 0 | 0 | 0 | 0
2021-10-16 23:30 | 0.30627 | 1.9845 | 0.31546 | 2.5403 | 0 | 0 | 0 | 0
2021-10-16 23:45 | 0.27462 | 1.7979 | 0.37263 | 2.5457 | 0 | 0 | 0 | 0
2021-10-17 | 0.31239 | 2.0734 | 0.28687 | 2.5893 | 0 | 0 | 0 | 0
2021-10-17 00:15 | 0.30218 | 2.3196 | 0.24297 | 2.845 | 0 | 0 | 0 | 0
2021-10-17 00:30 | 0.41653 | 2.3196 | 0.2246 | 2.846 | 0 | 0 | 0 | 0
2021-10-17 00:45 | 0.38386 | 2.3196 | 0.35731 | 2.8324 | 0 | 0 | 0 | 0
2021-10-17 01:00 | 0.27462 | 2.3196 | 0.33996 | 2.8383 | 0 | 0 | 0 | 0
2021-10-17 01:15 | 0.2787 | 2.3196 | 0.23174 | 2.8139 | 0 | 0 | 0 | 0
2021-10-17 01:30 | 0.28891 | 2.3196 | 0.24706 | 2.8603 | 0 | 0 | 0 | 0
2021-10-17 01:45 | 0.27564 | 2.4852 | 0.31852 | 2.8823 | 0 | 0 | 0 | 0
2021-10-17 02:00 | 0.42061 | 2.3966 | 0.34302 | 2.6317 | 0 | 0 | 0 | 0
2021-10-17 02:15 | 0.42061 | 2.0696 | 0.25522 | 2.4958 | 0 | 0 | 0 | 0
2021-10-17 02:30 | 0.25727 | 1.8631 | 0.26543 | 2.3179 | 0 | 0 | 0 | 0
2021-10-17 02:45 | 0.29402 | 1.7616 | 0.32056 | 2.1413 | 0 | 0 | 0 | 0
2021-10-17 03:00 | 0.27666 | 1.6209 | 0.30831 | 2.0385 | 0 | 0 | 0 | 0
2021-10-17 03:15 | 0.31852 | 1.7813 | 0.22153 | 2.0425 | 0 | 0 | 0 | 0
2021-10-17 03:30 | 0.42061 | 1.3646 | 0.24808 | 1.9685 | 0 | 0 | 0 | 0
2021-10-17 03:45 | 0.40223 | 1.5169 | 0.37977 | 1.9655 | 0 | 0 | 0 | 0
2021-10-17 04:00 | 0.27564 | 1.3156 | 0.35527 | 1.9969 | 0 | 0 | 0 | 0
2021-10-17 04:15 | 0.28993 | 1.3786 | 0.2491 | 2.0131 | 0 | 0 | 0 | 0
2021-10-17 04:30 | 0.27768 | 1.4649 | 0.23174 | 1.9943 | 0 | 0 | 0 | 0
2021-10-17 04:45 | 0.3614 | 1.2455 | 0.34506 | 1.9728 | 0 | 0 | 0 | 0
2021-10-17 05:00 | 0.41653 | 1.3232 | 0.24297 | 1.9806 | 0 | 0 | 0 | 0
2021-10-17 05:15 | 0.32873 | 1.3942 | 0.2246 | 1.9641 | 0 | 0 | 0 | 0
2021-10-17 05:30 | 0.28993 | 1.3883 | 0.33383 | 1.8047 | 0 | 0 | 0 | 0
2021-10-17 05:45 | 0.28993 | 1.4101 | 0.34915 | 1.7022 | 0 | 0.004366 | 0 | 0.004826
2021-10-17 06:00 | 0.30218 | 1.169 | 0.28993 | 1.1293 | 0 | 0.010762 | 0 | 0.011995
2021-10-17 06:15 | 0.36854 | 1.238 | 0.25829 | 1.078 | 0 | 0.015767 | 0 | 0.019164
2021-10-17 06:30 | 0.43286 | 1.4931 | 0.4053 | 2.021 | 0 | 0.033666 | 0 | 0.026333
2021-10-17 06:45 | 0.32975 | 1.3913 | 0.51045 | 1.7599 | 0.011433 | 0.099314 | 0.009141 | 0.069043
2021-10-17 07:00 | 0.28789 | 1.5531 | 0.65337 | 2.0777 | 0.029804 | 0.15654 | 0.023637 | 0.13051
2021-10-17 07:15 | 0.29402 | 1.4967 | 0.3614 | 1.853 | 0.048175 | 0.2284 | 0.038133 | 0.19197
2021-10-17 07:30 | 1.3067 | 1.5275 | 0.45736 | 1.7618 | 0.066546 | 0.29309 | 0.052629 | 0.25344
2021-10-17 07:45 | 1.8274 | 1.5063 | 0.46961 | 1.7147 | 0.073408 | 0.32041 | 0.061153 | 0.28871
2021-10-17 08:00 | 1.4701 | 1.6013 | 0.52678 | 2.2305 | 0.073275 | 0.34702 | 0.066173 | 0.31006
2021-10-17 08:15 | 0.89022 | 1.5989 | 0.45736 | 2.0999 | 0.073143 | 0.36379 | 0.071193 | 0.33142
2021-10-17 08:30 | 0.93106 | 1.7071 | 0.36548 | 1.9721 | 0.07301 | 0.38656 | 0.076212 | 0.35278
2021-10-17 08:45 | 0.72279 | 1.6859 | 0.37977 | 1.9794 | 0.07034 | 0.39502 | 0.077818 | 0.3703
2021-10-17 09:00 | 0.71463 | 1.648 | 0.37569 | 2.1529 | 0.066125 | 0.39646 | 0.077418 | 0.3856
2021-10-17 09:15 | 0.7473 | 1.6859 | 0.38692 | 1.9885 | 0.061911 | 0.40071 | 0.077018 | 0.40089
2021-10-17 09:30 | 0.88205 | 1.7735 | 0.50228 | 1.8387 | 0.057696 | 0.40497 | 0.076618 | 0.41619
2021-10-17 09:45 | 0.66562 | 1.7735 | 0.42878 | 1.8738 | 0.063237 | 0.40873 | 0.081861 | 0.42615
2021-10-17 10:00 | 0.63296 | 1.8135 | 0.24195 | 2.0665 | 0.074723 | 0.41226 | 0.090426 | 0.43422
2021-10-17 10:15 | 0.55945 | 1.5969 | 0.21745 | 1.2196 | 0.08621 | 0.41579 | 0.09899 | 0.44229
2021-10-17 10:30 | 0.46553 | 1.5969 | 0.21949 | 1.2028 | 0.097696 | 0.41932 | 0.10755 | 0.45036
2021-10-17 10:45 | 0.41244 | 1.6636 | 0.28381 | 1.492 | 0.11576 | 0.42221 | 0.10457 | 0.43423
2021-10-17 11:00 | 0.46144 | 1.3564 | 1.9907 | 1.5083 | 0.13785 | 0.42041 | 0.094778 | 0.40526
2021-10-17 11:15 | 0.32567 | 1.3462 | 1.1434 | 1.3488 | 0.15993 | 0.41862 | 0.084986 | 0.37629
2021-10-17 11:30 | 2.2256 | 1.3483 | 0.31239 | 1.2429 | 0.18201 | 0.39554 | 0.075194 | 0.34732
2021-10-17 11:45 | 5.6821 | 1.2863 | 0.29912 | 1.2415 | 0.23678 | 0.42337 | 0.066071 | 0.34237
2021-10-17 12:00 | 3.5425 | 1.3303 | 0.3175 | 1.538 | 0.31153 | 0.43555 | 0.057341 | 0.34947
2021-10-17 12:15 | 3.8079 | 1.6668 | 0.37058 | 2.2771 | 0.38628 | 0.44531 | 0.048612 | 0.35657
2021-10-17 12:30 | 4.3293 | 1.6257 | 1.5007 | 2.3009 | 0.46103 | 0.44564 | 0.039883 | 0.36367
2021-10-17 12:45 | 3.4506 | 1.7077 | 2.3072 | 2.009 | 0.49632 | 0.41714 | 0.09427 | 0.37181
2021-10-17 13:00 | 3.4915 | 1.6341 | 0.20622 | 1.6952 | 0.50746 | 0.42923 | 0.18596 | 0.38107
2021-10-17 13:15 | 3.6446 | 1.5559 | 0.22358 | 1.6806 | 0.5186 | 0.43297 | 0.27766 | 0.39034
2021-10-17 13:30 | 5.3873 | 1.6148 | 0.35935 | 1.8406 | 0.52974 | 0.42724 | 0.36935 | 0.3996
2021-10-17 13:45 | 3.7365 | 1.6611 | 0.24297 | 1.9552 | 0.46856 | 0.41957 | 0.4264 | 0.39646
2021-10-17 14:00 | 3.6038 | 1.6749 | 0.21439 | 1.6679 | 0.36304 | 0.41171 | 0.46292 | 0.38693
2021-10-17 14:15 | 1.9601 | 1.6749 | 0.22153 | 1.6383 | 0.25753 | 0.40742 | 0.49945 | 0.37739
2021-10-17 14:30 | 2.1949 | 1.6749 | 0.31444 | 1.6465 | 0.15201 | 0.40312 | 0.53598 | 0.36786
2021-10-17 14:45 | 2.0826 | 1.6235 | 0.31341 | 1.6882 | 0.1537 | 0.39349 | 0.54207 | 0.36963
2021-10-17 15:00 | 2.1439 | 1.6887 | 0.20928 | 1.6762 | 0.22121 | 0.38142 | 0.53012 | 0.37676
2021-10-17 15:15 | 4.7794 | 1.7496 | 0.22562 | 2.1379 | 0.28872 | 0.36935 | 0.51816 | 0.38388
2021-10-17 15:30 | 2.0826 | 1.7552 | 0.22868 | 1.7515 | 0.35624 | 0.35728 | 0.5062 | 0.39101
2021-10-17 15:45 | 1.858 | 1.7723 | 0.31852 | 1.5453 | 0.32335 | 0.2961 | 0.45208 | 0.35771
2021-10-17 16:00 | 0.70238 | 1.8375 | 0.2736 | 1.3077 | 0.22874 | 0.2546 | 0.37292 | 0.30253
2021-10-17 16:15 | 0.391 | 1.8375 | 0.31444 | 1.2995 | 0.13412 | 0.20206 | 0.29376 | 0.24735
2021-10-17 16:30 | 0.3175 | 1.8375 | 0.45736 | 1.4114 | 0.039507 | 0.17936 | 0.2146 | 0.19218
2021-10-17 16:45 | 2.93 | 1.705 | 0.53903 | 1.8036 | 0.002916 | 0.14312 | 0.15607 | 0.14453
2021-10-17 17:00 | 1.9703 | 1.705 | 0.60845 | 1.9399 | 0.002054 | 0.094572 | 0.1098 | 0.10137
2021-10-17 17:15 | 0.48595 | 1.3988 | 0.50636 | 1.7114 | 0.001191 | 0.053747 | 0.063533 | 0.058202
2021-10-17 17:30 | 0.55537 | 1.601 | 0.49003 | 1.5774 | 0.000329 | 0.012018 | 0.017267 | 0.015036
2021-10-17 17:45 | 0.66971 | 1.6188 | 0.50636 | 1.9115 | 0 | 0 | 0 | 0
2021-10-17 18:00 | 0.80855 | 1.611 | 0.60437 | 1.5964 | 0 | 0 | 0 | 0
2021-10-17 18:15 | 0.8698 | 1.5464 | 0.53495 | 1.968 | 0 | 0 | 0 | 0
2021-10-17 18:30 | 0.7718 | 1.4399 | 1.5926 | 2.3767 | 0 | 0 | 0 | 0
2021-10-17 18:45 | 0.73504 | 1.4696 | 0.58395 | 2.5667 | 0 | 0 | 0 | 0
2021-10-17 19:00 | 0.75955 | 1.1348 | 0.65746 | 1.3709 | 0 | 0 | 0 | 0
2021-10-17 19:15 | 2.0622 | 1.1194 | 0.73096 | 1.125 | 0 | 0 | 0 | 0
2021-10-17 19:30 | 1.7457 | 1.2071 | 0.72688 | 0.9576 | 0 | 0 | 0 | 0
2021-10-17 19:45 | 1.6334 | 1.1574 | 0.73096 | 1.0708 | 0 | 0 | 0 | 0
2021-10-17 20:00 | 0.71871 | 1.0729 | 0.61662 | 0.74161 | 0 | 0 | 0 | 0
2021-10-17 20:15 | 0.51045 | 1.0082 | 0.53903 | 0.63339 | 0 | 0 | 0 | 0
2021-10-17 20:30 | 0.72279 | 1.0325 | 0.50636 | 0.6576 | 0 | 0 | 0 | 0
2021-10-17 20:45 | 1.1128 | 0.97585 | 0.56354 | 0.59533 | 0 | 0 | 0 | 0
2021-10-17 21:00 | 1.4701 | 0.75747 | 0.56762 | 0.57214 | 0 | 0 | 0 | 0
2021-10-17 21:15 | 0.54312 | 0.57878 | 0.51862 | 0.49368 | 0 | 0 | 0 | 0
2021-10-17 21:30 | 0.342 | 0.59789 | 0.70646 | 0.51322 | 0 | 0 | 0 | 0
2021-10-17 21:45 | 0.49003 | 0.56553 | 0.50228 | 0.43563 | 0 | 0 | 0 | 0
2021-10-17 22:00 | 3.4404 | 1.8728 | 0.56354 | 2.5006 | 0 | 0 | 0 | 0
2021-10-17 22:15 | 3.6548 | 1.9976 | 0.56354 | 2.556 | 0 | 0 | 0 | 0
2021-10-17 22:30 | 3.5323 | 1.8303 | 0.55945 | 2.2953 | 0 | 0 | 0 | 0
2021-10-17 22:45 | 3.4915 | 1.8238 | 0.6207 | 2.2538 | 0 | 0 | 0 | 0
2021-10-17 23:00 | 3.5731 | 1.9505 | 0.42061 | 2.1986 | 0 | 0 | 0 | 0
2021-10-17 23:15 | 3.5936 | 1.675 | 0.31648 | 2.1265 | 0 | 0 | 0 | 0
2021-10-17 23:30 | 3.5119 | 1.7725 | 0.30627 | 2.0998 | 0 | 0 | 0 | 0
2021-10-17 23:45 | 3.5119 | 1.8245 | 0.27462 | 2.1124 | 0 | 0 | 0 | 0
2021-10-18 | 3.4506 | 2.0952 | 0.31239 | 2.1555 | 0 | 0 | 0 | 0
2021-10-18 00:15 | 3.3894 | 2.0355 | 0.30218 | 2.1016 | 0 | 0 | 0 | 0
2021-10-18 00:30 | 3.3383 | 1.9312 | 0.41653 | 2.1168 | 0 | 0 | 0 | 0
2021-10-18 00:45 | 3.3792 | 1.9788 | 0.38386 | 2.0963 | 0 | 0 | 0 | 0
2021-10-18 01:00 | 3.3894 | 2.0797 | 0.27462 | 2.0844 | 0 | 0 | 0 | 0
2021-10-18 01:15 | 3.3077 | 1.7336 | 0.2787 | 2.0584 | 0 | 0 | 0 | 0
2021-10-18 01:30 | 3.3383 | 2.0355 | 0.28891 | 2.1041 | 0 | 0 | 0 | 0
2021-10-18 01:45 | 3.5119 | 2.1483 | 0.27564 | 2.122 | 0 | 0 | 0 | 0
2021-10-18 02:00 | 3.42 | 2.0628 | 0.42061 | 1.89 | 0 | 0 | 0 | 0
2021-10-18 02:15 | 3.369 | 1.9009 | 0.42061 | 1.7519 | 0 | 0 | 0 | 0
2021-10-18 02:30 | 3.175 | 1.9733 | 0.25727 | 1.5484 | 0 | 0 | 0 | 0
2021-10-18 02:45 | 1.7764 | 1.9333 | 0.29402 | 1.3749 | 0 | 0 | 0 | 0
2021-10-18 03:00 | 1.2047 | 1.8762 | 0.27666 | 1.2674 | 0 | 0 | 0 | 0
2021-10-18 03:15 | 0.86164 | 1.9197 | 0.31852 | 1.2752 | 0 | 0 | 0 | 0
2021-10-18 03:30 | 0.51862 | 1.7984 | 0.42061 | 1.2136 | 0 | 0 | 0 | 0
2021-10-18 03:45 | 0.22664 | 1.8582 | 0.40223 | 1.2058 | 0 | 0 | 0 | 0
2021-10-18 04:00 | 0.26543 | 1.8812 | 0.27564 | 1.2169 | 0 | 0 | 0 | 0
2021-10-18 04:15 | 0.29912 | 1.8133 | 0.28993 | 1.233 | 0 | 0 | 0 | 0
2021-10-18 04:30 | 0.21847 | 1.8359 | 0.27768 | 1.2102 | 0 | 0 | 0 | 0
2021-10-18 04:45 | 0.23378 | 1.9027 | 0.3614 | 1.1985 | 0 | 0 | 0 | 0
2021-10-18 05:00 | 0.31444 | 1.7512 | 0.41653 | 1.2119 | 0 | 0 | 0 | 0
2021-10-18 05:15 | 0.24502 | 1.8055 | 0.32873 | 1.1807 | 0 | 0 | 0 | 0
2021-10-18 05:30 | 0.21949 | 1.7967 | 0.28993 | 1.0136 | 0 | 0 | 0 | 0
2021-10-18 05:45 | 0.24706 | 1.756 | 0.28993 | 0.90889 | 0 | 0.001372 | 0 | 0.001737
2021-10-18 06:00 | 0.31954 | 0.66523 | 0.30218 | 0.33558 | 0 | 0.004511 | 0 | 0.004364
2021-10-18 06:15 | 0.28993 | 0.73914 | 0.36854 | 0.29154 | 0 | 0.005478 | 0 | 0.00699
2021-10-18 06:30 | 0.26748 | 1.4206 | 0.43286 | 1.2416 | 0 | 0.009447 | 0 | 0.009617
2021-10-18 06:45 | 0.27973 | 1.2069 | 0.32975 | 0.96358 | 0.053954 | 0.0687 | 0.011433 | 0.043433
2021-10-18 07:00 | 0.84938 | 1.884 | 0.28789 | 1.2732 | 0.14181 | 0.10117 | 0.029804 | 0.094178
2021-10-18 07:15 | 0.44511 | 1.6391 | 0.29402 | 1.0471 | 0.22967 | 0.14193 | 0.048175 | 0.14492
2021-10-18 07:30 | 0.23174 | 1.5892 | 1.3067 | 1.0985 | 0.31753 | 0.1809 | 0.066546 | 0.19567
2021-10-18 07:45 | 0.30627 | 1.5751 | 1.8274 | 1.1236 | 0.36357 | 0.20455 | 0.073408 | 0.22388
2021-10-18 08:00 | 0.40019 | 1.8137 | 1.4701 | 1.5861 | 0.38331 | 0.2133 | 0.073275 | 0.23969
2021-10-18 08:15 | 1.7151 | 1.7928 | 0.89022 | 1.3705 | 0.40305 | 0.24291 | 0.073143 | 0.2555
2021-10-18 08:30 | 0.55537 | 1.9429 | 0.93106 | 1.2463 | 0.42279 | 0.26482 | 0.07301 | 0.27131
2021-10-18 08:45 | 0.63704 | 1.8788 | 0.72279 | 1.2217 | 0.44869 | 0.26852 | 0.07034 | 0.28586
2021-10-18 09:00 | 0.87389 | 1.7742 | 0.71463 | 1.3918 | 0.47847 | 0.27548 | 0.066125 | 0.29936
2021-10-18 09:15 | 0.82897 | 1.8817 | 0.7473 | 1.2299 | 0.50825 | 0.27843 | 0.061911 | 0.31285
2021-10-18 09:30 | 0.76363 | 1.6851 | 0.88205 | 1.0972 | 0.53804 | 0.29596 | 0.057696 | 0.32635
2021-10-18 09:45 | 1.858 | 1.6711 | 0.66562 | 1.0991 | 0.56145 | 0.29871 | 0.063237 | 0.33615
2021-10-18 10:00 | 1.8989 | 1.9004 | 0.63296 | 1.285 | 0.58083 | 0.29074 | 0.074723 | 0.34503
2021-10-18 10:15 | 1.8376 | 1.491 | 0.55945 | 0.42542 | 0.60022 | 0.30137 | 0.08621 | 0.35391
2021-10-18 10:30 | 1.8376 | 1.5018 | 0.46553 | 0.39304 | 0.61961 | 0.30776 | 0.097696 | 0.36279
2021-10-18 10:45 | 0.40019 | 1.8343 | 0.41244 | 0.67248 | 0.60599 | 0.30102 | 0.11576 | 0.34926
2021-10-18 11:00 | 0.25012 | 1.9173 | 0.46144 | 0.69363 | 0.57152 | 0.29268 | 0.13785 | 0.32385
2021-10-18 11:15 | 0.18785 | 1.6329 | 0.32567 | 0.51249 | 0.53704 | 0.282 | 0.15993 | 0.29845
2021-10-18 11:30 | 0.17457 | 1.8108 | 2.2256 | 0.67583 | 0.50256 | 0.26712 | 0.18201 | 0.27304
2021-10-18 11:45 | 0.18172 | 1.8352 | 5.6821 | 1.166 | 0.51355 | 0.26367 | 0.23678 | 0.27574
2021-10-18 12:00 | 1.0046 | 1.199 | 3.5425 | 1.1546 | 0.55332 | 0.26387 | 0.31153 | 0.29309
2021-10-18 12:15 | 2.7768 | 1.8942 | 3.8079 | 1.9295 | 0.59309 | 0.23434 | 0.38628 | 0.31043
2021-10-18 12:30 | 0.57578 | 2.0372 | 4.3293 | 2.0256 | 0.63286 | 0.23337 | 0.46103 | 0.32777
2021-10-18 12:45 | 2.8279 | 1.8489 | 3.4506 | 1.606 | 0.64576 | 0.28884 | 0.49632 | 0.3402
2021-10-18 13:00 | 3.471 | 2.0025 | 3.4915 | 1.2958 | 0.64162 | 0.3132 | 0.50746 | 0.35015
2021-10-18 13:15 | 3.5221 | 1.9955 | 3.6446 | 1.3009 | 0.63748 | 0.31593 | 0.5186 | 0.36011
2021-10-18 13:30 | 3.2669 | 1.8249 | 5.3873 | 1.7077 | 0.63335 | 0.30563 | 0.52974 | 0.37006
2021-10-18 13:45 | 1.5824 | 2.0252 | 3.7365 | 1.5843 | 0.61518 | 0.30615 | 0.46856 | 0.36311
2021-10-18 14:00 | 0.64521 | 1.9579 | 3.6038 | 1.2758 | 0.58811 | 0.30299 | 0.36304 | 0.34622
2021-10-18 14:15 | 1.6641 | 1.839 | 1.9601 | 1.0092 | 0.56104 | 0.29983 | 0.25753 | 0.32933
2021-10-18 14:30 | 1.9805 | 1.7674 | 2.1949 | 1.0488 | 0.53397 | 0.28912 | 0.15201 | 0.31243
2021-10-18 14:45 | 0.35731 | 1.7785 | 2.0826 | 1.0722 | 0.48834 | 0.28221 | 0.1537 | 0.31716
2021-10-18 15:00 | 0.39202 | 1.846 | 2.1439 | 1.0668 | 0.43091 | 0.27356 | 0.22121 | 0.33426
2021-10-18 15:15 | 0.37977 | 2.1201 | 4.7794 | 1.9028 | 0.37348 | 0.2649 | 0.28872 | 0.35137
2021-10-18 15:30 | 0.31239 | 1.8769 | 2.0826 | 1.129 | 0.31605 | 0.26438 | 0.35624 | 0.36847
2021-10-18 15:45 | 0.31852 | 1.1019 | 1.858 | 0.88847 | 0.26419 | 0.23375 | 0.32335 | 0.33575
2021-10-18 16:00 | 0.27666 | 1.3833 | 0.70238 | 0.48361 | 0.21588 | 0.19744 | 0.22874 | 0.27469
2021-10-18 16:15 | 0.40019 | 1.2218 | 0.391 | 0.42878 | 0.16758 | 0.16225 | 0.13412 | 0.21364
2021-10-18 16:30 | 0.36854 | 1.2497 | 0.3175 | 0.52795 | 0.11927 | 0.13519 | 0.039507 | 0.15258
2021-10-18 16:45 | 0.29504 | 1.6089 | 2.93 | 1.4361 | 0.085124 | 0.10301 | 0.002916 | 0.10942
2021-10-18 17:00 | 0.24604 | 1.8223 | 1.9703 | 1.5836 | 0.060011 | 0.070311 | 0.002054 | 0.076818
2021-10-18 17:15 | 0.20112 | 1.8635 | 0.48595 | 1.1666 | 0.034898 | 0.040823 | 0.001191 | 0.044219
2021-10-18 17:30 | 0.22256 | 1.577 | 0.55537 | 1.0417 | 0.009785 | 0.00828 | 0.000329 | 0.01162
2021-10-18 17:45 | 0.23787 | 1.7027 | 0.66971 | 1.3783 | 0 | 0 | 0 | 0
2021-10-18 18:00 | 0.38079 | 1.7186 | 0.80855 | 1.1358 | 0 | 0 | 0 | 0
2021-10-18 18:15 | 0.46553 | 1.8155 | 0.8698 | 1.5454 | 0 | 0 | 0 | 0
2021-10-18 18:30 | 0.39202 | 2.0287 | 0.7718 | 1.9401 | 0 | 0 | 0 | 0
2021-10-18 18:45 | 0.38794 | 2.0591 | 0.73504 | 1.9799 | 0 | 0 | 0 | 0
2021-10-18 19:00 | 0.39509 | 1.3399 | 0.75955 | 1.2665 | 0 | 0 | 0 | 0
2021-10-18 19:15 | 0.39304 | 1.3248 | 2.0622 | 1.2388 | 0 | 0 | 0 | 0
2021-10-18 19:30 | 1.2251 | 1.2838 | 1.7457 | 1.0769 | 0 | 0 | 0 | 0
2021-10-18 19:45 | 2.9606 | 1.1523 | 1.6334 | 1.1029 | 0 | 0 | 0 | 0
2021-10-18 20:00 | 2.5727 | 1.038 | 0.71871 | 0.61239 | 0 | 0 | 0 | 0
2021-10-18 20:15 | 2.8891 | 0.81188 | 0.51045 | 0.60539 | 0 | 0 | 0 | 0
2021-10-18 20:30 | 2.8687 | 0.85894 | 0.72279 | 0.66694 | 0 | 0 | 0 | 0
2021-10-18 20:45 | 1.7559 | 0.83128 | 1.1128 | 0.65862 | 0 | 0 | 0 | 0
2021-10-18 21:00 | 0.61254 | 0.83128 | 1.4701 | 0.69231 | 0 | 0 | 0 | 0
2021-10-18 21:15 | 0.69013 | 0.63855 | 0.54312 | 0.48318 | 0 | 0 | 0 | 0
2021-10-18 21:30 | 0.7963 | 0.6706 | 0.342 | 0.47399 | 0 | 0 | 0 | 0
2021-10-18 21:45 | 0.39815 | 0.65563 | 0.49003 | 0.41988 | 0 | 0 | 0 | 0
2021-10-18 22:00 | 3.2873 | 1.9373 | 3.4404 | 2.4977 | 0 | 0 | 0 | 0
2021-10-18 22:15 | 3.4915 | 2.0709 | 3.6548 | 2.5546 | 0 | 0 | 0 | 0
2021-10-18 22:30 | 3.4915 | 1.6295 | 3.5323 | 2.2719 | 0 | 0 | 0 | 0
2021-10-18 22:45 | 3.4813 | 1.5845 | 3.4915 | 2.2305 | 0 | 0 | 0 | 0
2021-10-18 23:00 | 3.4813 | 1.4325 | 3.5731 | 2.1869 | 0 | 0 | 0 | 0
2021-10-18 23:15 | 3.5119 | 1.2237 | 3.5936 | 2.1134 | 0 | 0 | 0 | 0
2021-10-18 23:30 | 3.5017 | 1.1642 | 3.5119 | 2.0911 | 0 | 0 | 0 | 0
2021-10-18 23:45 | 3.4915 | 1.2237 | 3.5119 | 2.1095 | 0 | 0 | 0 | 0
2021-10-19 | 3.4915 | 1.2624 | 3.4506 | 2.1424 | 0 | 0 | 0 | 0
2021-10-19 00:15 | 3.471 | 1.2305 | 3.3894 | 2.0972 | 0 | 0 | 0 | 0
2021-10-19 00:30 | 3.4098 | 1.3612 | 3.3383 | 2.1051 | 0 | 0 | 0 | 0
2021-10-19 00:45 | 3.3996 | 1.3016 | 3.3792 | 2.0861 | 0 | 0 | 0 | 0
2021-10-19 01:00 | 3.3792 | 1.2305 | 3.3894 | 2.08 | 0 | 0 | 0 | 0
2021-10-19 01:15 | 3.3792 | 1.2305 | 3.3077 | 2.0351 | 0 | 0 | 0 | 0
2021-10-19 01:30 | 3.4302 | 1.2305 | 3.3383 | 2.072 | 0 | 0 | 0 | 0
2021-10-19 01:45 | 3.4404 | 1.2901 | 3.5119 | 2.1249 | 0 | 0 | 0 | 0
2021-10-19 02:00 | 3.4404 | 1.3543 | 3.42 | 1.8943 | 0 | 0 | 0 | 0
2021-10-19 02:15 | 3.4302 | 1.3624 | 3.369 | 1.7431 | 0 | 0 | 0 | 0
2021-10-19 02:30 | 3.4608 | 1.2231 | 3.175 | 1.5149 | 0 | 0 | 0 | 0
2021-10-19 02:45 | 3.5527 | 1.0511 | 1.7764 | 1.1298 | 0 | 0 | 0 | 0
2021-10-19 03:00 | 3.5629 | 1.0559 | 1.2047 | 0.93631 | 0 | 0 | 0 | 0
2021-10-19 03:15 | 3.5629 | 1.0559 | 0.86164 | 0.90976 | 0 | 0 | 0 | 0
2021-10-19 03:30 | 3.4813 | 1.0915 | 0.51862 | 0.80053 | 0 | 0 | 0 | 0
2021-10-19 03:45 | 3.4302 | 1.0915 | 0.22664 | 0.75109 | 0 | 0 | 0 | 0
2021-10-19 04:00 | 3.4506 | 1.0915 | 0.26543 | 0.76626 | 0 | 0 | 0 | 0
2021-10-19 04:15 | 3.4506 | 1.0813 | 0.29912 | 0.7769 | 0 | 0 | 0 | 0
2021-10-19 04:30 | 3.4302 | 1.0813 | 0.21847 | 0.73242 | 0 | 0 | 0 | 0
2021-10-19 04:45 | 3.4404 | 1.0813 | 0.23378 | 0.7419 | 0 | 0 | 0 | 0
2021-10-19 05:00 | 3.5017 | 1.0507 | 0.31444 | 0.76392 | 0 | 0 | 0 | 0
2021-10-19 05:15 | 3.5629 | 1.1298 | 0.24502 | 0.72717 | 0 | 0 | 0 | 0
2021-10-19 05:30 | 3.4506 | 0.75181 | 0.21949 | 0.55201 | 0 | 0 | 0 | 0
2021-10-19 05:45 | 3.369 | 0.64765 | 0.24706 | 0.44249 | 0 | 0.000991 | 0 | 0.00135
2021-10-19 06:00 | 0.52678 | 0.61587 | 0.31954 | 0.31006 | 0 | 0.002443 | 0 | 0.003401
2021-10-19 06:15 | 0.30525 | 0.61196 | 0.28993 | 0.29679 | 0 | 0.003089 | 0 | 0.005452
2021-10-19 06:30 | 0.35425 | 1.6954 | 0.26748 | 1.2372 | 0 | 0.004633 | 0 | 0.007504
2021-10-19 06:45 | 0.68196 | 1.1844 | 0.27973 | 0.96475 | 0.001086 | 0.056072 | 0.053954 | 0.043344
2021-10-19 07:00 | 3.7773 | 1.2105 | 0.84938 | 0.92202 | 0.002878 | 0.072661 | 0.14181 | 0.098459
2021-10-19 07:15 | 3.8794 | 1.2254 | 0.44511 | 0.62216 | 0.004671 | 0.11581 | 0.22967 | 0.15357
2021-10-19 07:30 | 3.7569 | 1.1696 | 0.23174 | 0.64156 | 0.006463 | 0.18183 | 0.31753 | 0.20869
2021-10-19 07:45 | 3.665 | 1.218 | 0.30627 | 0.67875 | 0.009215 | 0.19741 | 0.36357 | 0.23908
2021-10-19 08:00 | 2.103 | 1.437 | 0.40019 | 0.8822 | 0.012592 | 0.21312 | 0.38331 | 0.25516
2021-10-19 08:15 | 0.66971 | 1.364 | 1.7151 | 0.79222 | 0.015969 | 0.23009 | 0.40305 | 0.27125
2021-10-19 08:30 | 0.49411 | 1.0345 | 0.55537 | 0.54983 | 0.019347 | 0.24034 | 0.42279 | 0.28733
2021-10-19 08:45 | 0.76363 | 1.0052 | 0.63704 | 0.54647 | 0.022477 | 0.24899 | 0.44869 | 0.29901
2021-10-19 09:00 | 0.69829 | 1.2065 | 0.87389 | 0.55653 | 0.025447 | 0.22959 | 0.47847 | 0.30821
2021-10-19 09:15 | 0.5227 | 1.0988 | 0.82897 | 0.55464 | 0.028417 | 0.23206 | 0.50825 | 0.31741
2021-10-19 09:30 | 0.48595 | 1.3401 | 0.76363 | 0.60306 | 0.031387 | 0.24277 | 0.53804 | 0.32661
2021-10-19 09:45 | 0.42878 | 1.3325 | 1.858 | 0.71929 | 0.071206 | 0.25858 | 0.56145 | 0.34189
2021-10-19 10:00 | 0.38386 | 1.4363 | 1.8989 | 0.66767 | 0.1351 | 0.29521 | 0.58083 | 0.3609
2021-10-19 10:15 | 0.40019 | 1.42 | 1.8376 | 0.62727 | 0.19899 | 0.2697 | 0.60022 | 0.37992
2021-10-19 10:30 | 2.3481 | 1.3214 | 1.8376 | 0.6086 | 0.26288 | 0.25279 | 0.61961 | 0.39894
2021-10-19 10:45 | 1.0005 | 1.3264 | 0.40019 | 0.68633 | 0.29091 | 0.29099 | 0.60599 | 0.39426
2021-10-19 11:00 | 0.41653 | 1.413 | 0.25012 | 0.68648 | 0.29546 | 0.31637 | 0.57152 | 0.37641
2021-10-19 11:15 | 0.51045 | 0.91805 | 0.18785 | 0.49338 | 0.30002 | 0.31181 | 0.53704 | 0.35856
2021-10-19 11:30 | 0.61662 | 1.3714 | 0.17457 | 0.65308 | 0.30458 | 0.30738 | 0.50256 | 0.34071
2021-10-19 11:45 | 0.57578 | 1.464 | 0.18172 | 1.1318 | 0.28361 | 0.31785 | 0.51355 | 0.34358
2021-10-19 12:00 | 2.0928 | 1.4435 | 1.0046 | 1.1809 | 0.24592 | 0.33472 | 0.55332 | 0.35835
2021-10-19 12:15 | 2.8381 | 1.6006 | 2.7768 | 1.5719 | 0.20823 | 0.3215 | 0.59309 | 0.37313
2021-10-19 12:30 | 0.5962 | 1.4782 | 0.57578 | 1.6032 | 0.17054 | 0.31609 | 0.63286 | 0.3879
2021-10-19 12:45 | 0.25727 | 1.6647 | 2.8279 | 1.5039 | 0.15805 | 0.29818 | 0.64576 | 0.39875
2021-10-19 13:00 | 0.28075 | 1.6333 | 3.471 | 1.2856 | 0.16209 | 0.29079 | 0.64162 | 0.40708
2021-10-19 13:15 | 0.2787 | 1.4866 | 3.5221 | 1.2878 | 0.16612 | 0.29332 | 0.63748 | 0.4154
2021-10-19 13:30 | 0.36038 | 1.7402 | 3.2669 | 1.6683 | 0.17016 | 0.26519 | 0.63335 | 0.42373
2021-10-19 13:45 | 0.44103 | 1.6333 | 1.5824 | 1.2882 | 0.18072 | 0.26467 | 0.61518 | 0.41661
2021-10-19 14:00 | 0.42878 | 1.3538 | 0.64521 | 0.84005 | 0.19556 | 0.27005 | 0.58811 | 0.39999
2021-10-19 14:15 | 0.35323 | 1.3785 | 1.6641 | 0.72775 | 0.21041 | 0.27675 | 0.56104 | 0.38337
2021-10-19 14:30 | 0.342 | 1.3785 | 1.9805 | 0.8154 | 0.22525 | 0.27383 | 0.53397 | 0.36675
2021-10-19 14:45 | 0.34608 | 1.3401 | 0.35731 | 0.59825 | 0.26698 | 0.26585 | 0.48834 | 0.36597
2021-10-19 15:00 | 0.3369 | 1.309 | 0.39202 | 0.60947 | 0.3264 | 0.26737 | 0.43091 | 0.37434
2021-10-19 15:15 | 0.34302 | 1.3062 | 0.37977 | 0.95871 | 0.38582 | 0.25891 | 0.37348 | 0.38271
2021-10-19 15:30 | 0.34506 | 1.2383 | 0.31239 | 0.58454 | 0.44524 | 0.25044 | 0.31605 | 0.39108
2021-10-19 15:45 | 0.62887 | 1.3467 | 0.31852 | 0.64375 | 0.40929 | 0.21968 | 0.26419 | 0.35315
2021-10-19 16:00 | 0.49411 | 0.88306 | 0.27666 | 0.47107 | 0.3105 | 0.1842 | 0.21588 | 0.28876
2021-10-19 16:15 | 0.40427 | 0.82043 | 0.40019 | 0.44044 | 0.21171 | 0.15494 | 0.16758 | 0.22437
2021-10-19 16:30 | 0.38182 | 1.0189 | 0.36854 | 0.53232 | 0.11291 | 0.10814 | 0.11927 | 0.15997
2021-10-19 16:45 | 0.38386 | 1.2854 | 0.29504 | 0.98677 | 0.06255 | 0.082315 | 0.085124 | 0.11453
2021-10-19 17:00 | 0.42878 | 1.1583 | 0.24604 | 0.88395 | 0.044141 | 0.057546 | 0.060011 | 0.080458
2021-10-19 17:15 | 0.41653 | 0.95397 | 0.20112 | 0.43213 | 0.025733 | 0.033578 | 0.034898 | 0.046387
2021-10-19 17:30 | 0.51453 | 0.95397 | 0.22256 | 0.43432 | 0.007324 | 0.008083 | 0.009785 | 0.012316
2021-10-19 17:45 | 0.48595 | 1.3367 | 0.23787 | 0.6102 | 0 | 0 | 0 | 0
2021-10-19 18:00 | 2.7768 | 1.238 | 0.38079 | 0.58818 | 0 | 0 | 0 | 0
2021-10-19 18:15 | 5.7396 | 1.2016 | 0.46553 | 0.88351 | 0 | 0 | 0 | 0
2021-10-19 18:30 | 6.2471 | 1.5465 | 0.39202 | 1.3307 | 0 | 0 | 0 | 0
2021-10-19 18:45 | 6.1722 | 1.6994 | 0.38794 | 1.3508 | 0 | 0 | 0 | 0
2021-10-19 19:00 | 1.9091 | 1.146 | 0.39509 | 1.0808 | 0 | 0 | 0 | 0
2021-10-19 19:15 | 1.2557 | 1.2629 | 0.39304 | 1.0864 | 0 | 0 | 0 | 0
2021-10-19 19:30 | 0.91472 | 1.1967 | 1.2251 | 1.0244 | 0 | 0 | 0 | 0
2021-10-19 19:45 | 0.64929 | 1.2084 | 2.9606 | 1.1918 | 0 | 0 | 0 | 0
2021-10-19 20:00 | 1.0719 | 1.0754 | 2.5727 | 0.88133 | 0 | 0 | 0 | 0
2021-10-19 20:15 | 1.0005 | 1.1417 | 2.8891 | 0.94054 | 0 | 0 | 0 | 0
2021-10-19 20:30 | 0.46961 | 1.0497 | 2.8687 | 0.99742 | 0 | 0 | 0 | 0
2021-10-19 20:45 | 0.38386 | 0.86066 | 1.7559 | 0.83013 | 0 | 0 | 0 | 0
2021-10-19 21:00 | 0.45328 | 0.83796 | 0.61254 | 0.71156 | 0 | 0 | 0 | 0
2021-10-19 21:15 | 0.57987 | 0.61886 | 0.69013 | 0.51176 | 0 | 0 | 0 | 0
2021-10-19 21:30 | 0.5227 | 0.65059 | 0.7963 | 0.5297 | 0 | 0 | 0 | 0
2021-10-19 21:45 | 0.43694 | 0.60561 | 0.39815 | 0.42528 | 0 | 0 | 0 | 0
2021-10-19 22:00 | 3.3485 | 2.2208 | 3.2873 | 2.4948 | 0 | 0 | 0 | 0
2021-10-19 22:15 | 3.5221 | 2.2607 | 3.4915 | 2.6654 | 0 | 0 | 0 | 0
2021-10-19 22:30 | 3.4302 | 2.2513 | 3.4915 | 2.6045 | 0 | 0 | 0 | 0
2021-10-19 22:45 | 3.3894 | 2.3177 | 3.4813 | 2.5995 | 0 | 0 | 0 | 0
2021-10-19 23:00 | 3.3792 | 2.1732 | 3.4813 | 2.5862 | 0 | 0 | 0 | 0
2021-10-19 23:15 | 3.4506 | 2.2253 | 3.5119 | 2.5734 | 0 | 0 | 0 | 0
2021-10-19 23:30 | 3.5323 | 2.1275 | 3.5017 | 2.5565 | 0 | 0 | 0 | 0
2021-10-19 23:45 | 3.4098 | 2.1631 | 3.4915 | 2.5732 | 0 | 0 | 0 | 0
2021-10-20 | 3.4404 | 2.1708 | 3.4915 | 2.5912 | 0 | 0 | 0 | 0
2021-10-20 00:15 | 3.3996 | 2.1044 | 3.471 | 2.5412 | 0 | 0 | 0 | 0
2021-10-20 00:30 | 3.3894 | 2.0974 | 3.4098 | 2.5461 | 0 | 0 | 0 | 0
2021-10-20 00:45 | 3.5425 | 2.1276 | 3.3996 | 2.5371 | 0 | 0 | 0 | 0
2021-10-20 01:00 | 3.4915 | 2.1633 | 3.3792 | 2.5277 | 0 | 0 | 0 | 0
2021-10-20 01:15 | 3.3996 | 2.0974 | 3.3792 | 2.4808 | 0 | 0 | 0 | 0
2021-10-20 01:30 | 3.42 | 2.066 | 3.4302 | 2.518 | 0 | 0 | 0 | 0
2021-10-20 01:45 | 3.3792 | 1.8809 | 3.4404 | 2.5627 | 0 | 0 | 0 | 0
2021-10-20 02:00 | 3.5323 | 1.7349 | 3.4404 | 2.3419 | 0 | 0 | 0 | 0
2021-10-20 02:15 | 2.5216 | 1.7242 | 3.4302 | 2.1903 | 0 | 0 | 0 | 0
2021-10-20 02:30 | 1.1434 | 1.0904 | 3.4608 | 1.9743 | 0 | 0 | 0 | 0
2021-10-20 02:45 | 0.78813 | 1.277 | 3.5527 | 1.6022 | 0 | 0 | 0 | 0
2021-10-20 03:00 | 0.65746 | 1.277 | 3.5629 | 1.4075 | 0 | 0 | 0 | 0
2021-10-20 03:15 | 0.24399 | 1.1582 | 3.5629 | 1.373 | 0 | 0 | 0 | 0
2021-10-20 03:30 | 0.26135 | 0.94656 | 3.4813 | 1.2448 | 0 | 0 | 0 | 0
2021-10-20 03:45 | 0.25829 | 0.84914 | 3.4302 | 1.1997 | 0 | 0 | 0 | 0
2021-10-20 04:00 | 0.3226 | 1.0675 | 3.4506 | 1.2189 | 0 | 0 | 0 | 0
2021-10-20 04:15 | 0.2491 | 1.0051 | 3.4506 | 1.2281 | 0 | 0 | 0 | 0
2021-10-20 04:30 | 0.23072 | 0.78679 | 3.4302 | 1.1873 | 0 | 0 | 0 | 0
2021-10-20 04:45 | 0.35935 | 0.78679 | 3.4404 | 1.1963 | 0 | 0 | 0 | 0
2021-10-20 05:00 | 0.26952 | 0.78679 | 3.5017 | 1.2118 | 0 | 0 | 0 | 0
2021-10-20 05:15 | 0.24706 | 0.76724 | 3.5629 | 1.1856 | 0 | 0 | 0 | 0
2021-10-20 05:30 | 0.25012 | 0.75959 | 3.4506 | 1.0081 | 0 | 0 | 0 | 0
2021-10-20 05:45 | 0.34506 | 0.81771 | 3.369 | 0.88949 | 0 | 0.002007 | 0 | 0.000939
2021-10-20 06:00 | 0.31035 | 0.65429 | 0.52678 | 0.34448 | 0 | 0.004814 | 0 | 0.002372
2021-10-20 06:15 | 0.26033 | 0.64289 | 0.30525 | 0.30073 | 0 | 0.005781 | 0 | 0.003805
2021-10-20 06:30 | 0.30423 | 0.86425 | 0.35425 | 0.89839 | 0 | 0.009132 | 0 | 0.005237
2021-10-20 06:45 | 0.36956 | 1.1475 | 0.68196 | 0.97116 | 0.001206 | 0.06209 | 0.001086 | 0.040465
2021-10-20 07:00 | 0.94331 | 1.4832 | 3.7773 | 1.3143 | 0.003223 | 0.10419 | 0.002878 | 0.094992
2021-10-20 07:15 | 1.1434 | 1.0859 | 3.8794 | 1.1058 | 0.00524 | 0.15018 | 0.004671 | 0.14952
2021-10-20 07:30 | 0.51453 | 1.0517 | 3.7569 | 1.0633 | 0.007258 | 0.20914 | 0.006463 | 0.20405
2021-10-20 07:45 | 0.30627 | 1.0517 | 3.665 | 1.1294 | 0.026109 | 0.24068 | 0.009215 | 0.23115
2021-10-20 08:00 | 0.44511 | 1.2979 | 2.103 | 1.1288 | 0.056309 | 0.24803 | 0.012592 | 0.24259
2021-10-20 08:15 | 0.72688 | 1.0518 | 0.66971 | 0.81672 | 0.086509 | 0.2569 | 0.015969 | 0.25403
2021-10-20 08:30 | 0.73913 | 0.91282 | 0.49411 | 0.54866 | 0.11671 | 0.26251 | 0.019347 | 0.26547
2021-10-20 08:45 | 0.69013 | 0.8965 | 0.76363 | 0.57797 | 0.11517 | 0.26826 | 0.022477 | 0.27277
2021-10-20 09:00 | 0.77997 | 0.92561 | 0.69829 | 0.5962 | 0.092212 | 0.27117 | 0.025447 | 0.27772
2021-10-20 09:15 | 1.3986 | 0.92561 | 0.5227 | 0.56864 | 0.069252 | 0.30099 | 0.028417 | 0.28266
2021-10-20 09:30 | 0.58804 | 1.0499 | 0.48595 | 0.59664 | 0.046291 | 0.30419 | 0.031387 | 0.28761
2021-10-20 09:45 | 0.63296 | 1.1682 | 0.42878 | 0.71404 | 0.070899 | 0.30832 | 0.071206 | 0.30517
2021-10-20 10:00 | 0.35833 | 0.93865 | 0.38386 | 0.68269 | 0.12766 | 0.31112 | 0.1351 | 0.33058
2021-10-20 10:15 | 0.57987 | 0.93673 | 0.40019 | 0.62843 | 0.18443 | 0.3201 | 0.19899 | 0.35598
2021-10-20 10:30 | 0.53903 | 1.0609 | 2.3481 | 0.89139 | 0.24119 | 0.32282 | 0.26288 | 0.38138
2021-10-20 10:45 | 0.51862 | 0.91094 | 1.0005 | 0.79017 | 0.23947 | 0.32273 | 0.29091 | 0.38905
2021-10-20 11:00 | 0.47778 | 1.0368 | 0.41653 | 0.7104 | 0.19814 | 0.32136 | 0.29546 | 0.38586
2021-10-20 11:15 | 0.38794 | 1.0248 | 0.51045 | 0.5278 | 0.15681 | 0.31998 | 0.30002 | 0.38267
2021-10-20 11:30 | 0.39611 | 0.91254 | 0.61662 | 0.68969 | 0.11549 | 0.31861 | 0.30458 | 0.37948
2021-10-20 11:45 | 0.44103 | 1.1739 | 0.57578 | 1.1666 | 0.087259 | 0.31523 | 0.28361 | 0.38106
2021-10-20 12:00 | 0.42469 | 1.4193 | 2.0928 | 1.4434 | 0.067911 | 0.33953 | 0.24592 | 0.38586
2021-10-20 12:15 | 0.49003 | 1.2995 | 2.8381 | 1.9328 | 0.048563 | 0.33978 | 0.20823 | 0.39066
2021-10-20 12:30 | 1.4905 | 1.3346 | 0.5962 | 1.6242 | 0.029214 | 0.34004 | 0.17054 | 0.39546
2021-10-20 12:45 | 0.79222 | 1.5279 | 0.25727 | 1.492 | 0.053497 | 0.32208 | 0.15805 | 0.40544
2021-10-20 13:00 | 0.43286 | 1.4901 | 0.28075 | 1.2767 | 0.1074 | 0.32492 | 0.16209 | 0.41808
2021-10-20 13:15 | 0.48186 | 1.299 | 0.2787 | 1.2669 | 0.16131 | 0.32775 | 0.16612 | 0.43073
2021-10-20 13:30 | 0.51862 | 1.4834 | 0.36038 | 1.68 | 0.21521 | 0.32689 | 0.17016 | 0.44337
2021-10-20 13:45 | 0.43694 | 1.3937 | 0.44103 | 1.3067 | 0.20635 | 0.3176 | 0.18072 | 0.43891
2021-10-20 14:00 | 0.44511 | 0.93634 | 0.42878 | 0.84749 | 0.15482 | 0.31432 | 0.19556 | 0.42423
2021-10-20 14:15 | 0.43694 | 1.0945 | 0.35323 | 0.74117 | 0.10328 | 0.31104 | 0.21041 | 0.40954
2021-10-20 14:30 | 0.45736 | 0.9894 | 0.342 | 0.82634 | 0.051745 | 0.30776 | 0.22525 | 0.39486
2021-10-20 14:45 | 0.44103 | 1.0871 | 0.34608 | 0.60977 | 0.030082 | 0.30041 | 0.26698 | 0.39802
2021-10-20 15:00 | 0.51862 | 1.0603 | 0.3369 | 0.60991 | 0.028757 | 0.29345 | 0.3264 | 0.4119
2021-10-20 15:15 | 0.5717 | 0.87216 | 0.34302 | 0.9679 | 0.027432 | 0.28416 | 0.38582 | 0.42578
2021-10-20 15:30 | 0.5227 | 0.99565 | 0.34506 | 0.58964 | 0.026107 | 0.27487 | 0.44524 | 0.43966
2021-10-20 15:45 | 0.46553 | 0.92091 | 0.62887 | 0.69275 | 0.021954 | 0.24834 | 0.40929 | 0.39601
2021-10-20 16:00 | 0.4982 | 0.89059 | 0.49411 | 0.48697 | 0.015872 | 0.21087 | 0.3105 | 0.31815
2021-10-20 16:15 | 0.43694 | 0.76739 | 0.40427 | 0.45984 | 0.00979 | 0.17852 | 0.21171 | 0.24028
2021-10-20 16:30 | 0.37773 | 1.0147 | 0.38182 | 0.54924 | 0.003708 | 0.14951 | 0.11291 | 0.16241
2021-10-20 16:45 | 0.4737 | 1.0784 | 0.38386 | 0.87826 | 0.001056 | 0.10908 | 0.06255 | 0.11221
2021-10-20 17:00 | 0.66154 | 1.1643 | 0.42878 | 0.75998 | 0.000746 | 0.069056 | 0.044141 | 0.078882
2021-10-20 17:15 | 0.53903 | 1.1041 | 0.41653 | 0.43738 | 0.000436 | 0.034278 | 0.025733 | 0.045549
2021-10-20 17:30 | 0.3471 | 1.0851 | 0.51453 | 0.45678 | 0.000126 | 0.008471 | 0.007324 | 0.012216
2021-10-20 17:45 | 0.43694 | 1.2098 | 0.48595 | 0.64316 | 0 | 0 | 0 | 0
2021-10-20 18:00 | 2.787 | 1.0674 | 2.7768 | 0.93412 | 0 | 0 | 0 | 0
2021-10-20 18:15 | 2.9912 | 1.25 | 5.7396 | 1.3345 | 0 | 0 | 0 | 0
2021-10-20 18:30 | 3.369 | 1.2398 | 6.2471 | 1.7418 | 0 | 0 | 0 | 0
2021-10-20 18:45 | 3.3485 | 1.485 | 6.1722 | 1.7542 | 0 | 0 | 0 | 0
2021-10-20 19:00 | 1.1434 | 1.0359 | 1.9091 | 1.0604 | 0 | 0 | 0 | 0
2021-10-20 19:15 | 0.73096 | 1.0282 | 1.2557 | 1.0645 | 0 | 0 | 0 | 0
2021-10-20 19:30 | 1.123 | 1.0094 | 0.91472 | 0.97131 | 0 | 0 | 0 | 0
2021-10-20 19:45 | 3.0831 | 1.0222 | 0.64929 | 1.1895 | 0 | 0 | 0 | 0
2021-10-20 20:00 | 2.542 | 1.0152 | 1.0719 | 0.93704 | 0 | 0 | 0 | 0
2021-10-20 20:15 | 1.9907 | 0.97023 | 1.0005 | 0.95104 | 0 | 0 | 0 | 0
2021-10-20 20:30 | 1.174 | 1.0474 | 0.46961 | 0.97466 | 0 | 0 | 0 | 0
2021-10-20 20:45 | 3.2362 | 0.9622 | 0.38386 | 0.80855 | 0 | 0 | 0 | 0
2021-10-20 21:00 | 0.7718 | 0.99488 | 0.45328 | 0.7069 | 0 | 0 | 0 | 0
2021-10-20 21:15 | 0.4982 | 0.64151 | 0.57987 | 0.51993 | 0 | 0 | 0 | 0
2021-10-20 21:30 | 0.60029 | 0.63551 | 0.5227 | 0.53087 | 0 | 0 | 0 | 0
2021-10-20 21:45 | 0.56354 | 0.60656 | 0.43694 | 0.42003 | 0 | 0 | 0 | 0
2021-10-20 22:00 | 0.55537 | 1.5988 | 3.3485 | 2.4817 | 0 | 0 | 0 | 0
2021-10-20 22:15 | 0.5717 | 1.9394 | 3.5221 | 2.6217 | 0 | 0 | 0 | 0
2021-10-20 22:30 | 0.44511 | 2.2218 | 3.4302 | 2.5986 | 0 | 0 | 0 | 0
2021-10-20 22:45 | 0.4053 | 2.2002 | 3.3894 | 2.5922 | 0 | 0 | 0 | 0
2021-10-20 23:00 | 0.35731 | 2.137 | 3.3792 | 2.5833 | 0 | 0 | 0 | 0
2021-10-20 23:15 | 0.26339 | 2.1964 | 3.4506 | 2.5719 | 0 | 0 | 0 | 0
2021-10-20 23:30 | 0.23378 | 2.1581 | 3.5323 | 2.5521 | 0 | 0 | 0 | 0
2021-10-20 23:45 | 0.23481 | 2.1581 | 3.4098 | 2.5499 | 0 | 0 | 0 | 0
2021-10-21 | 0.25931 | 2.5673 | 3.4404 | 2.5635 | 0 | 0 | 0 | 0
2021-10-21 00:15 | 0.37365 | 2.5673 | 3.3996 | 2.5178 | 0 | 0 | 0 | 0
2021-10-21 00:30 | 0.36854 | 2.5673 | 3.3894 | 2.533 | 0 | 0 | 0 | 0
2021-10-21 00:45 | 0.36446 | 2.5673 | 3.5425 | 2.5589 | 0 | 0 | 0 | 0
2021-10-21 01:00 | 0.2736 | 2.5673 | 3.4915 | 2.5365 | 0 | 0 | 0 | 0
2021-10-21 01:15 | 0.25012 | 2.5673 | 3.3996 | 2.4779 | 0 | 0 | 0 | 0
2021-10-21 01:30 | 0.24706 | 2.5673 | 3.42 | 2.5063 | 0 | 0 | 0 | 0
2021-10-21 01:45 | 0.24502 | 2.4502 | 3.3792 | 2.5467 | 0 | 0 | 0 | 0
2021-10-21 02:00 | 0.2685 | 2.4324 | 3.5323 | 2.5826 | 0 | 0 | 0 | 0
2021-10-21 02:15 | 0.24808 | 2.4324 | 2.5216 | 2.4198 | 0 | 0 | 0 | 0
2021-10-21 02:30 | 0.33485 | 2.1313 | 1.1434 | 2.0873 | 0 | 0 | 0 | 0
2021-10-21 02:45 | 0.36752 | 1.8238 | 0.78813 | 1.653 | 0 | 0 | 0 | 0
2021-10-21 03:00 | 0.35119 | 1.6123 | 0.65746 | 1.4402 | 0 | 0 | 0 | 0
2021-10-21 03:15 | 0.24706 | 1.699 | 0.24399 | 1.3627 | 0 | 0 | 0 | 0
2021-10-21 03:30 | 0.25829 | 1.1636 | 0.26135 | 1.2395 | 0 | 0 | 0 | 0
2021-10-21 03:45 | 0.25931 | 1.1801 | 0.25829 | 1.1934 | 0 | 0 | 0 | 0
2021-10-21 04:00 | 0.25522 | 1.1801 | 0.3226 | 1.2003 | 0 | 0 | 0 | 0
2021-10-21 04:15 | 0.26135 | 1.145 | 0.2491 | 1.2013 | 0 | 0 | 0 | 0
2021-10-21 04:30 | 0.33894 | 1.1362 | 0.23072 | 1.1689 | 0 | 0 | 0 | 0
2021-10-21 04:45 | 0.36344 | 1.1654 | 0.35935 | 1.2045 | 0 | 0 | 0 | 0
2021-10-21 05:00 | 0.26952 | 1.1348 | 0.26952 | 1.2074 | 0 | 0 | 0 | 0
2021-10-21 05:15 | 0.23991 | 1.146 | 0.24706 | 1.1761 | 0 | 0 | 0 | 0
2021-10-21 05:30 | 0.2491 | 1.0596 | 0.25012 | 0.9961 | 0 | 0 | 0 | 0
2021-10-21 05:45 | 0.24093 | 1.0627 | 0.34506 | 0.8787 | 0 | 0.000487 | 0 | 0
2021-10-21 06:00 | 0.39202 | 0.68824 | 0.31035 | 0.33194 | 0 | 0.001075 | 0 | 0
2021-10-21 06:15 | 0.37773 | 0.70693 | 0.26033 | 0.29475 | 0 | 0.001849 | 0 | 0
2021-10-21 06:30 | 0.391 | 1.231 | 0.30423 | 0.62537 | 0 | 0.003414 | 0 | 0
2021-10-21 06:45 | 0.6207 | 1.2603 | 0.36956 | 0.6681 | 0.009206 | 0.066881 | 0.001206 | 0.027446
2021-10-21 07:00 | 0.84938 | 1.4575 | 0.94331 | 1.2843 | 0.024825 | 0.10785 | 0.003223 | 0.070875
2021-10-21 07:15 | 0.64521 | 1.2058 | 1.1434 | 1.1087 | 0.040444 | 0.15275 | 0.00524 | 0.11431
2021-10-21 07:30 | 0.65337 | 1.1733 | 0.51453 | 1.0628 | 0.056062 | 0.16158 | 0.007258 | 0.15773
2021-10-21 07:45 | 0.48595 | 1.2269 | 0.30627 | 1.0973 | 0.082676 | 0.17664 | 0.026109 | 0.18041
2021-10-21 08:00 | 0.5962 | 1.1873 | 0.44511 | 0.89197 | 0.11696 | 0.17855 | 0.056309 | 0.19128
2021-10-21 08:15 | 0.73504 | 1.2871 | 0.72688 | 0.83247 | 0.15124 | 0.17382 | 0.086509 | 0.20216
2021-10-21 08:30 | 0.45328 | 1.2217 | 0.73913 | 0.58658 | 0.18552 | 0.17338 | 0.11671 | 0.21303
2021-10-21 08:45 | 0.46144 | 1.1169 | 0.69013 | 0.60072 | 0.18554 | 0.16626 | 0.11517 | 0.21493
2021-10-21 09:00 | 0.51453 | 1.1155 | 0.77997 | 0.63004 | 0.16163 | 0.16806 | 0.092212 | 0.21126
2021-10-21 09:15 | 0.51453 | 1.11 | 1.3986 | 0.69202 | 0.13772 | 0.17057 | 0.069252 | 0.20759
2021-10-21 09:30 | 0.5962 | 1.0702 | 0.58804 | 0.60714 | 0.11381 | 0.17238 | 0.046291 | 0.20393
2021-10-21 09:45 | 0.68196 | 1.1922 | 0.63296 | 0.74088 | 0.18486 | 0.23585 | 0.070899 | 0.22759
2021-10-21 10:00 | 0.57578 | 1.1489 | 0.35833 | 0.66737 | 0.32234 | 0.31358 | 0.12766 | 0.26788
2021-10-21 10:15 | 0.39611 | 1.1922 | 0.57987 | 0.6436 | 0.45981 | 0.32974 | 0.18443 | 0.30816
2021-10-21 10:30 | 0.33485 | 1.1922 | 0.53903 | 0.90364 | 0.59728 | 0.33254 | 0.24119 | 0.34845
2021-10-21 10:45 | 0.3471 | 1.1052 | 0.51862 | 0.79484 | 0.61901 | 0.33245 | 0.23947 | 0.35872
2021-10-21 11:00 | 0.3471 | 1.1439 | 0.47778 | 0.69115 | 0.55966 | 0.33104 | 0.19814 | 0.3504
2021-10-21 11:15 | 0.50228 | 0.8727 | 0.38794 | 0.49338 | 0.50031 | 0.32962 | 0.15681 | 0.34208
2021-10-21 11:30 | 0.57578 | 1.1247 | 0.39611 | 0.67102 | 0.44096 | 0.31101 | 0.11549 | 0.33376
2021-10-21 11:45 | 0.44919 | 1.1413 | 0.44103 | 1.1403 | 0.42224 | 0.31075 | 0.087259 | 0.33718
2021-10-21 12:00 | 0.41244 | 1.1243 | 0.42469 | 1.1409 | 0.43203 | 0.30984 | 0.067911 | 0.34778
2021-10-21 12:15 | 0.27156 | 1.2896 | 0.49003 | 1.8089 | 0.44182 | 0.31736 | 0.048563 | 0.35839
2021-10-21 12:30 | 0.23072 | 1.2643 | 1.4905 | 1.7205 | 0.45161 | 0.3176 | 0.029214 | 0.36899
2021-10-21 12:45 | 0.33077 | 1.0303 | 0.79222 | 1.4418 | 0.41986 | 0.31739 | 0.053497 | 0.38277
2021-10-21 13:00 | 0.3471 | 0.8891 | 0.43286 | 1.209 | 0.35892 | 0.31399 | 0.1074 | 0.39905
2021-10-21 13:15 | 0.24604 | 0.95491 | 0.48186 | 1.2617 | 0.29799 | 0.33424 | 0.16131 | 0.41534
2021-10-21 13:30 | 0.2297 | 1.2383 | 0.51862 | 1.5061 | 0.23705 | 0.33273 | 0.21521 | 0.43162
2021-10-21 13:45 | 0.23685 | 1.1164 | 0.43694 | 0.99727 | 0.20646 | 0.32389 | 0.20635 | 0.42489
2021-10-21 14:00 | 0.2246 | 1.0511 | 0.44511 | 0.84457 | 0.19722 | 0.32127 | 0.15482 | 0.40347
2021-10-21 14:15 | 0.33894 | 1.1036 | 0.43694 | 0.74525 | 0.18798 | 0.3013 | 0.10328 | 0.38204
2021-10-21 14:30 | 0.28789 | 1.0368 | 0.45736 | 0.83976 | 0.17873 | 0.29703 | 0.051745 | 0.36062
2021-10-21 14:45 | 0.2246 | 1.0561 | 0.44103 | 0.62333 | 0.15276 | 0.29855 | 0.030082 | 0.35585
2021-10-21 15:00 | 0.23378 | 1.0725 | 0.51862 | 0.61108 | 0.11499 | 0.28939 | 0.028757 | 0.36183
2021-10-21 15:15 | 0.2297 | 1.0401 | 0.5717 | 0.98948 | 0.077231 | 0.28023 | 0.027432 | 0.3678
2021-10-21 15:30 | 0.30014 | 1.0226 | 0.5227 | 0.60743 | 0.039469 | 0.27108 | 0.026107 | 0.37377
2021-10-21 15:45 | 0.32158 | 1.0516 | 0.46553 | 0.70383 | 0.022528 | 0.25559 | 0.021954 | 0.33341
2021-10-21 16:00 | 0.22051 | 0.8304 | 0.4982 | 0.48813 | 0.020273 | 0.21932 | 0.015872 | 0.26474
2021-10-21 16:15 | 0.2246 | 0.86474 | 0.43694 | 0.45051 | 0.018018 | 0.19822 | 0.00979 | 0.19607
2021-10-21 16:30 | 0.22562 | 0.91606 | 0.37773 | 0.54078 | 0.015763 | 0.14908 | 0.003708 | 0.12741
2021-10-21 16:45 | 0.27973 | 1.0073 | 0.4737 | 0.8806 | 0.012657 | 0.10585 | 0.001056 | 0.085555
2021-10-21 17:00 | 0.33792 | 1.0409 | 0.66154 | 0.77865 | 0.00895 | 0.080386 | 0.000746 | 0.060184
2021-10-21 17:15 | 0.21949 | 0.93667 | 0.53903 | 0.43038 | 0.005243 | 0.047205 | 0.000436 | 0.034814
2021-10-21 17:30 | 0.21439 | 0.93667 | 0.3471 | 0.43344 | 0.001536 | 0.011453 | 0.000126 | 0.009443
2021-10-21 17:45 | 0.21235 | 1.0638 | 0.43694 | 0.6385 | 0 | 0 | 0 | 0
2021-10-21 18:00 | 0.26952 | 1.1766 | 2.787 | 1.2663 | 0 | 0 | 0 | 0
2021-10-21 18:15 | 0.32771 | 1.2383 | 2.9912 | 1.6819 | 0 | 0 | 0 | 0
2021-10-21 18:30 | 0.23174 | 1.4558 | 3.369 | 1.8672 | 0 | 0 | 0 | 0
2021-10-21 18:45 | 0.24706 | 1.361 | 3.3485 | 1.706 | 0 | 0 | 0 | 0
2021-10-21 19:00 | 0.22051 | 0.89444 | 1.1434 | 1.0225 | 0 | 0 | 0 | 0
2021-10-21 19:15 | 0.24399 | 0.87801 | 0.73096 | 1.0027 | 0 | 0 | 0 | 0
2021-10-21 19:30 | 0.3614 | 0.95591 | 1.123 | 0.9611 | 0 | 0 | 0 | 0
2021-10-21 19:45 | 0.25727 | 1.4006 | 3.0831 | 1.5313 | 0 | 0 | 0 | 0
2021-10-21 20:00 | 0.25522 | 1.005 | 2.542 | 1.1993 | 0 | 0 | 0 | 0
2021-10-21 20:15 | 0.23889 | 1.0173 | 1.9907 | 1.1351 | 0 | 0 | 0 | 0
2021-10-21 20:30 | 0.24604 | 0.95046 | 1.174 | 0.96008 | 0 | 0 | 0 | 0
2021-10-21 20:45 | 0.3471 | 0.99738 | 3.2362 | 1.1177 | 0 | 0 | 0 | 0
2021-10-21 21:00 | 0.25727 | 0.85995 | 0.7718 | 0.6611 | 0 | 0 | 0 | 0
2021-10-21 21:15 | 0.25114 | 0.71087 | 0.4982 | 0.51059 | 0 | 0 | 0 | 0
2021-10-21 21:30 | 0.37161 | 0.75636 | 0.60029 | 0.53262 | 0 | 0 | 0 | 0
2021-10-21 21:45 | 0.34098 | 0.70864 | 0.56354 | 0.4438 | 0 | 0 | 0 | 0
2021-10-21 22:00 | 0.34302 | 1.912 | 0.55537 | 2.106 | 0 | 0 | 0 | 0
2021-10-21 22:15 | 0.2297 | 2.1478 | 0.5717 | 2.2221 | 0 | 0 | 0 | 0
2021-10-21 22:30 | 0.23889 | 2.3191 | 0.44511 | 2.1766 | 0 | 0 | 0 | 0
2021-10-21 22:45 | 0.24195 | 2.3191 | 0.4053 | 2.1644 | 0 | 0 | 0 | 0
2021-10-21 23:00 | 0.29402 | 2.4078 | 0.35731 | 2.1341 | 0 | 0 | 0 | 0
2021-10-21 23:15 | 0.30014 | 2.4616 | 0.26339 | 2.1079 | 0 | 0 | 0 | 0
2021-10-21 23:30 | 0.21439 | 2.4616 | 0.23378 | 2.1071 | 0 | 0 | 0 | 0
2021-10-21 23:45 | 0.23481 | 2.4616 | 0.23481 | 2.1051 | 0 | 0 | 0 | 0
2021-10-22 | 0.25522 | 2.2232 | 0.25931 | 2.109 | 0 | 0 | 0 | 0
2021-10-22 00:15 | 0.33179 | 2.0115 | 0.37365 | 2.0812 | 0 | 0 | 0 | 0
2021-10-22 00:30 | 0.23583 | 2.0115 | 0.36854 | 2.0766 | 0 | 0 | 0 | 0
2021-10-22 00:45 | 0.23787 | 2.0444 | 0.36446 | 2.1195 | 0 | 0 | 0 | 0
2021-10-22 01:00 | 0.23685 | 2.1161 | 0.2736 | 2.0899 | 0 | 0 | 0 | 0
2021-10-22 01:15 | 0.29606 | 2.1161 | 0.25012 | 2.0323 | 0 | 0 | 0 | 0
2021-10-22 01:30 | 0.32056 | 2.1161 | 0.24706 | 2.0545 | 0 | 0 | 0 | 0
2021-10-22 01:45 | 0.23481 | 2.2817 | 0.24502 | 2.08 | 0 | 0 | 0 | 0
2021-10-22 02:00 | 0.24093 | 2.3001 | 0.2685 | 2.1222 | 0 | 0 | 0 | 0
2021-10-22 02:15 | 0.22664 | 2.1547 | 0.24808 | 1.9623 | 0 | 0 | 0 | 0
2021-10-22 02:30 | 0.5962 | 2.0117 | 0.33485 | 1.718 | 0 | 0 | 0 | 0
2021-10-22 02:45 | 0.46553 | 2.0173 | 0.36752 | 1.4984 | 0 | 0 | 0 | 0
2021-10-22 03:00 | 0.32975 | 2.0173 | 0.35119 | 1.3929 | 0 | 0 | 0 | 0
2021-10-22 03:15 | 0.34608 | 1.8222 | 0.24706 | 1.2796 | 0 | 0 | 0 | 0
2021-10-22 03:30 | 0.35731 | 1.7243 | 0.25829 | 1.237 | 0 | 0 | 0 | 0
2021-10-22 03:45 | 0.34915 | 1.6227 | 0.25931 | 1.1923 | 0 | 0 | 0 | 0
2021-10-22 04:00 | 0.23685 | 1.636 | 0.25522 | 1.1936 | 0 | 0 | 0 | 0
2021-10-22 04:15 | 0.22051 | 1.6586 | 0.26135 | 1.1815 | 0 | 0 | 0 | 0
2021-10-22 04:30 | 0.3369 | 1.6173 | 0.33894 | 1.1756 | 0 | 0 | 0 | 0
2021-10-22 04:45 | 0.23481 | 1.6979 | 0.36344 | 1.2133 | 0 | 0 | 0 | 0
2021-10-22 05:00 | 0.21541 | 1.5773 | 0.26952 | 1.2006 | 0 | 0 | 0 | 0
2021-10-22 05:15 | 0.33281 | 1.5169 | 0.23991 | 1.1651 | 0 | 0 | 0 | 0
2021-10-22 05:30 | 0.2246 | 0.98053 | 0.2491 | 0.97641 | 0 | 0 | 0 | 0
2021-10-22 05:45 | 0.20214 | 0.99653 | 0.24093 | 0.87535 | 0 | 0.000487 | 0 | 0
2021-10-22 06:00 | 0.30423 | 0.52955 | 0.39202 | 0.34754 | 0 | 0.001782 | 0 | 0
2021-10-22 06:15 | 0.35221 | 0.52757 | 0.37773 | 0.30306 | 0 | 0.003425 | 0 | 0
2021-10-22 06:30 | 0.293 | 0.52757 | 0.391 | 0.356 | 0 | 0.005896 | 0 | 0
2021-10-22 06:45 | 0.27564 | 0.88065 | 0.6207 | 0.53072 | 0.018438 | 0.097784 | 0.009206 | 0.021357
2021-10-22 07:00 | 0.78813 | 1.4877 | 0.84938 | 1.2907 | 0.05016 | 0.14497 | 0.024825 | 0.055575
2021-10-22 07:15 | 0.91472 | 1.2918 | 0.64521 | 1.1449 | 0.081883 | 0.18595 | 0.040444 | 0.089792
2021-10-22 07:30 | 0.68196 | 1.2685 | 0.65337 | 1.0925 | 0.1136 | 0.23501 | 0.056062 | 0.12401
2021-10-22 07:45 | 0.58395 | 1.0026 | 0.48595 | 1.0851 | 0.13541 | 0.27725 | 0.082676 | 0.14654
2021-10-22 08:00 | 0.43694 | 1.3623 | 0.5962 | 0.89314 | 0.15006 | 0.28261 | 0.11696 | 0.16246
2021-10-22 08:15 | 0.5962 | 1.6763 | 0.73504 | 0.82955 | 0.16471 | 0.34813 | 0.15124 | 0.17839
2021-10-22 08:30 | 0.50228 | 1.5947 | 0.45328 | 0.58074 | 0.17936 | 0.37982 | 0.18552 | 0.19431
2021-10-22 08:45 | 2.9912 | 1.4764 | 0.46144 | 0.57914 | 0.18924 | 0.38813 | 0.18554 | 0.19556
2021-10-22 09:00 | 3.8488 | 1.6792 | 0.51453 | 0.64054 | 0.19566 | 0.38197 | 0.16163 | 0.18737
2021-10-22 09:15 | 3.8182 | 1.6837 | 0.51453 | 0.70894 | 0.20208 | 0.38006 | 0.13772 | 0.17918
2021-10-22 09:30 | 3.8386 | 1.6252 | 0.5962 | 0.63529 | 0.2085 | 0.31123 | 0.11381 | 0.17098
2021-10-22 09:45 | 3.665 | 1.775 | 0.68196 | 0.76305 | 0.26056 | 0.39099 | 0.18486 | 0.19808
2021-10-22 10:00 | 3.7671 | 1.6099 | 0.57578 | 0.67029 | 0.34565 | 0.41848 | 0.32234 | 0.2482
2021-10-22 10:15 | 3.5731 | 1.5939 | 0.39611 | 0.6331 | 0.43073 | 0.42153 | 0.45981 | 0.29832
2021-10-22 10:30 | 3.5323 | 1.4863 | 0.33485 | 0.87564 | 0.51581 | 0.4315 | 0.59728 | 0.34843
2021-10-22 10:45 | 3.5833 | 1.5795 | 0.3471 | 0.77326 | 0.54079 | 0.43138 | 0.61901 | 0.35763
2021-10-22 11:00 | 3.6446 | 1.6616 | 0.3471 | 0.68006 | 0.52221 | 0.42004 | 0.55966 | 0.33975
2021-10-22 11:15 | 3.5731 | 1.1092 | 0.50228 | 0.50213 | 0.50362 | 0.43806 | 0.50031 | 0.32186
2021-10-22 11:30 | 3.5527 | 1.4904 | 0.57578 | 0.6891 | 0.48504 | 0.42534 | 0.44096 | 0.30397
2021-10-22 11:45 | 3.5936 | 1.5885 | 0.44919 | 1.1528 | 0.48599 | 0.40796 | 0.42224 | 0.30414
2021-10-22 12:00 | 3.5323 | 1.5449 | 0.41244 | 1.166 | 0.50111 | 0.39567 | 0.43203 | 0.31585
2021-10-22 12:15 | 4.2036 | 1.7601 | 0.27156 | 1.8156 | 0.51623 | 0.36301 | 0.44182 | 0.32756
2021-10-22 12:30 | 3.614 | 1.8704 | 0.23072 | 1.7173 | 0.53136 | 0.35037 | 0.45161 | 0.33927
2021-10-22 12:45 | 3.5323 | 1.4215 | 0.33077 | 1.4545 | 0.50271 | 0.36672 | 0.41986 | 0.34877
2021-10-22 13:00 | 3.5936 | 1.5937 | 0.3471 | 1.2182 | 0.44226 | 0.4331 | 0.35892 | 0.3569
2021-10-22 13:15 | 3.3996 | 1.6529 | 0.24604 | 1.2475 | 0.3818 | 0.43688 | 0.29799 | 0.36504
2021-10-22 13:30 | 3.4608 | 1.503 | 0.2297 | 1.4944 | 0.32135 | 0.42813 | 0.23705 | 0.37317
2021-10-22 13:45 | 3.5936 | 1.5776 | 0.23685 | 0.99698 | 0.30864 | 0.42042 | 0.20646 | 0.36299
2021-10-22 14:00 | 3.5425 | 1.5433 | 0.2246 | 0.84341 | 0.33066 | 0.40951 | 0.19722 | 0.34137
2021-10-22 14:15 | 3.471 | 1.5433 | 0.33894 | 0.76028 | 0.35269 | 0.39587 | 0.18798 | 0.31975
2021-10-22 14:30 | 3.4302 | 1.5433 | 0.28789 | 0.84501 | 0.37472 | 0.33969 | 0.17873 | 0.29813
2021-10-22 14:45 | 3.369 | 1.5469 | 0.2246 | 0.60437 | 0.3478 | 0.29483 | 0.15276 | 0.29185
2021-10-22 15:00 | 3.3485 | 1.5602 | 0.23378 | 0.60204 | 0.28521 | 0.27567 | 0.11499 | 0.29522
2021-10-22 15:15 | 3.42 | 1.5613 | 0.2297 | 0.9905 | 0.22263 | 0.26254 | 0.077231 | 0.29858
2021-10-22 15:30 | 3.5017 | 1.4897 | 0.30014 | 0.61866 | 0.16004 | 0.236 | 0.039469 | 0.30195
2021-10-22 15:45 | 3.6752 | 1.6271 | 0.32158 | 0.71915 | 0.11433 | 0.21067 | 0.022528 | 0.26854
2021-10-22 16:00 | 2.9504 | 1.2648 | 0.22051 | 0.47705 | 0.080919 | 0.19418 | 0.020273 | 0.21256
2021-10-22 16:15 | 2.4297 | 1.1151 | 0.2246 | 0.43213 | 0.047511 | 0.18156 | 0.018018 | 0.15657
2021-10-22 16:30 | 1.7968 | 1.1381 | 0.22562 | 0.53743 | 0.014104 | 0.15303 | 0.015763 | 0.10059
2021-10-22 16:45 | 1.613 | 1.1731 | 0.27973 | 0.88978 | 0 | 0.12099 | 0.012657 | 0.066862
2021-10-22 17:00 | 1.6641 | 1.1731 | 0.33792 | 0.78988 | 0 | 0.079899 | 0.00895 | 0.047069
2021-10-22 17:15 | 1.4088 | 1.047 | 0.21949 | 0.42936 | 0 | 0.041228 | 0.005243 | 0.027277
2021-10-22 17:30 | 1.1638 | 1.0507 | 0.21439 | 0.41361 | 0 | 0.009458 | 0.001536 | 0.007484
2021-10-22 17:45 | 1.7866 | 1.1731 | 0.21235 | 0.62377 | 0 | 0 | 0 | 0
2021-10-22 18:00 | 1.3374 | 1.259 | 0.26952 | 1.2704 | 0 | 0 | 0 | 0
2021-10-22 18:15 | 0.56762 | 1.6526 | 0.32771 | 1.6914 | 0 | 0 | 0 | 0
2021-10-22 18:30 | 1.2761 | 1.6142 | 0.23174 | 1.8665 | 0 | 0 | 0 | 0
2021-10-22 18:45 | 1.0924 | 1.3587 | 0.24706 | 1.6988 | 0 | 0 | 0 | 0
2021-10-22 19:00 | 0.88614 | 1.4197 | 0.22051 | 1.0035 | 0 | 0 | 0 | 0
2021-10-22 19:15 | 0.64929 | 1.3777 | 0.24399 | 1.0014 | 0 | 0 | 0 | 0
2021-10-22 19:30 | 0.61254 | 1.09 | 0.3614 | 0.94214 | 0 | 0 | 0 | 0
2021-10-22 19:45 | 0.66562 | 1.2619 | 0.25727 | 1.4135 | 0 | 0 | 0 | 0
2021-10-22 20:00 | 0.60845 | 1.1992 | 0.25522 | 1.2009 | 0 | 0 | 0 | 0
2021-10-22 20:15 | 0.57987 | 1.3393 | 0.23889 | 1.1192 | 0 | 0 | 0 | 0
2021-10-22 20:30 | 0.58395 | 1.1768 | 0.24604 | 0.94987 | 0 | 0 | 0 | 0
2021-10-22 20:45 | 0.57578 | 0.96493 | 0.3471 | 1.1317 | 0 | 0 | 0 | 0
2021-10-22 21:00 | 0.58395 | 1.0228 | 0.25727 | 0.66212 | 0 | 0 | 0 | 0
2021-10-22 21:15 | 0.55537 | 0.75996 | 0.25114 | 0.49907 | 0 | 0 | 0 | 0
2021-10-22 21:30 | 0.51045 | 0.68065 | 0.37161 | 0.5278 | 0 | 0 | 0 | 0
2021-10-22 21:45 | 0.40325 | 0.64487 | 0.34098 | 0.43753 | 0 | 0 | 0 | 0
2021-10-22 22:00 | 1.1536 | 1.1302 | 0.34302 | 1.6926 | 0 | 0 | 0 | 0
2021-10-22 22:15 | 0.59212 | 1.0024 | 0.2297 | 1.775 | 0 | 0 | 0 | 0
2021-10-22 22:30 | 0.39304 | 1.0006 | 0.23889 | 1.725 | 0 | 0 | 0 | 0
2021-10-22 22:45 | 0.37058 | 1.0006 | 0.24195 | 1.6973 | 0 | 0 | 0 | 0
2021-10-22 23:00 | 0.40632 | 1.0006 | 0.29402 | 1.6832 | 0 | 0 | 0 | 0
2021-10-22 23:15 | 0.38079 | 0.78458 | 0.30014 | 1.6665 | 0 | 0 | 0 | 0
2021-10-22 23:30 | 0.2736 | 0.78227 | 0.21439 | 1.6594 | 0 | 0 | 0 | 0
2021-10-22 23:45 | 0.27768 | 0.77263 | 0.23481 | 1.6471 | 0 | 0 | 0 | 0
2021-10-23 | 0.28789 | 1.1425 | 0.25522 | 1.6423 | 0 | 0 | 0 | 0
2021-10-23 00:15 | 0.37365 | 1.2377 | 0.33179 | 1.6444 | 0 | 0 | 0 | 0
2021-10-23 00:30 | 0.41653 | 1.2377 | 0.23583 | 1.6261 | 0 | 0 | 0 | 0
2021-10-23 00:45 | 0.33894 | 1.2377 | 0.23787 | 1.6664 | 0 | 0 | 0 | 0
2021-10-23 01:00 | 0.28891 | 1.1702 | 0.23685 | 1.6264 | 0 | 0 | 0 | 0
2021-10-23 01:15 | 0.27666 | 1.006 | 0.29606 | 1.5919 | 0 | 0 | 0 | 0
2021-10-23 01:30 | 0.33077 | 1.006 | 0.32056 | 1.6132 | 0 | 0 | 0 | 0
2021-10-23 01:45 | 0.39713 | 1.006 | 0.23481 | 1.6294 | 0 | 0 | 0 | 0
2021-10-23 02:00 | 0.32873 | 0.99647 | 0.24093 | 1.6665 | 0 | 0 | 0 | 0
2021-10-23 02:15 | 0.27258 | 0.98984 | 0.22664 | 1.4959 | 0 | 0 | 0 | 0
2021-10-23 02:30 | 0.26748 | 1.0044 | 0.5962 | 1.319 | 0 | 0 | 0 | 0
2021-10-23 02:45 | 0.35323 | 1.0658 | 0.46553 | 1.0807 | 0 | 0 | 0 | 0
2021-10-23 03:00 | 0.38386 | 0.9951 | 0.32975 | 0.95585 | 0 | 0 | 0 | 0
2021-10-23 03:15 | 0.3175 | 0.9834 | 0.34608 | 0.82882 | 0 | 0 | 0 | 0
2021-10-23 03:30 | 0.26339 | 0.95022 | 0.35731 | 0.79222 | 0 | 0 | 0 | 0
2021-10-23 03:45 | 0.27462 | 0.95022 | 0.34915 | 0.75794 | 0 | 0 | 0 | 0
2021-10-23 04:00 | 0.30933 | 0.95022 | 0.23685 | 0.73738 | 0 | 0 | 0 | 0
2021-10-23 04:15 | 0.38488 | 0.94007 | 0.22051 | 0.71711 | 0 | 0 | 0 | 0
2021-10-23 04:30 | 0.26135 | 0.94007 | 0.3369 | 0.72352 | 0 | 0 | 0 | 0
2021-10-23 04:45 | 0.25931 | 0.94007 | 0.23481 | 0.76261 | 0 | 0 | 0 | 0
2021-10-23 05:00 | 0.26748 | 0.90951 | 0.21541 | 0.74715 | 0 | 0 | 0 | 0
2021-10-23 05:15 | 0.38794 | 0.88995 | 0.33281 | 0.74015 | 0 | 0 | 0 | 0
2021-10-23 05:30 | 0.35323 | 0.88995 | 0.2246 | 0.71681 | 0 | 0 | 0 | 0
2021-10-23 05:45 | 0.25216 | 0.88995 | 0.20214 | 0.72046 | 0 | 0.000454 | 0 | 0
2021-10-23 06:00 | 0.29198 | 0.64745 | 0.30423 | 0.34929 | 0 | 0.001672 | 0 | 0
2021-10-23 06:15 | 0.27768 | 0.63816 | 0.35221 | 0.31604 | 0 | 0.003219 | 0 | 0
2021-10-23 06:30 | 0.43286 | 0.63351 | 0.293 | 0.34973 | 0 | 0.005547 | 0 | 0
2021-10-23 06:45 | 0.68604 | 0.691 | 0.27564 | 0.43826 | 0.037354 | 0.081113 | 0.018438 | 0.014923
2021-10-23 07:00 | 1.174 | 1.2446 | 0.78813 | 1.1641 | 0.10254 | 0.1189 | 0.05016 | 0.039477
2021-10-23 07:15 | 0.83713 | 1.0433 | 0.91472 | 1.0976 | 0.16773 | 0.18404 | 0.081883 | 0.064031
2021-10-23 07:30 | 0.91064 | 1.1399 | 0.68196 | 1.0861 | 0.23292 | 0.26612 | 0.1136 | 0.088584
2021-10-23 07:45 | 0.56762 | 1.1556 | 0.58395 | 1.0921 | 0.30781 | 0.32563 | 0.13541 | 0.10736
2021-10-23 08:00 | 0.64112 | 1.0388 | 0.43694 | 0.85405 | 0.38994 | 0.39643 | 0.15006 | 0.12267
2021-10-23 08:15 | 0.58395 | 1.028 | 0.5962 | 0.82722 | 0.47207 | 0.41978 | 0.16471 | 0.13797
2021-10-23 08:30 | 0.47778 | 1.0472 | 0.50228 | 0.57724 | 0.5542 | 0.45443 | 0.17936 | 0.15328
2021-10-23 08:45 | 0.38692 | 1.0546 | 2.9912 | 0.94943 | 0.59657 | 0.46437 | 0.18924 | 0.15847
2021-10-23 09:00 | 0.37467 | 1.0954 | 3.8488 | 1.1151 | 0.60923 | 0.46941 | 0.19566 | 0.15671
2021-10-23 09:15 | 0.3859 | 1.2268 | 3.8182 | 1.1739 | 0.62188 | 0.47445 | 0.20208 | 0.15495
2021-10-23 09:30 | 0.38692 | 1.2244 | 3.8386 | 1.0938 | 0.63453 | 0.46331 | 0.2085 | 0.15319
2021-10-23 09:45 | 0.40632 | 1.1907 | 3.665 | 1.1944 | 0.64204 | 0.46391 | 0.26056 | 0.18487
2021-10-23 10:00 | 0.51862 | 1.1001 | 3.7671 | 1.1227 | 0.64571 | 0.47233 | 0.34565 | 0.23953
2021-10-23 10:15 | 0.46961 | 1.1108 | 3.5731 | 1.0805 | 0.64937 | 0.4775 | 0.43073 | 0.2942
2021-10-23 10:30 | 0.28381 | 1.0645 | 3.5323 | 1.3253 | 0.65303 | 0.48804 | 0.51581 | 0.34886
2021-10-23 10:45 | 0.23072 | 1.053 | 3.5833 | 0.93514 | 0.60581 | 0.4879 | 0.54079 | 0.3595
2021-10-23 11:00 | 0.23583 | 1.061 | 3.6446 | 1.084 | 0.52047 | 0.48583 | 0.52221 | 0.33994
2021-10-23 11:15 | 1.2761 | 1.3033 | 3.5731 | 0.94725 | 0.43513 | 0.47267 | 0.50362 | 0.32039
2021-10-23 11:30 | 1.8682 | 1.2077 | 3.5527 | 1.122 | 0.34979 | 0.48056 | 0.48504 | 0.30083
2021-10-23 11:45 | 0.43694 | 1.2764 | 3.5936 | 1.6032 | 0.30749 | 0.48016 | 0.48599 | 0.29936
2021-10-23 12:00 | 0.42878 | 1.1515 | 3.5323 | 1.6181 | 0.2975 | 0.48052 | 0.50111 | 0.30988
2021-10-23 12:15 | 0.33281 | 1.1252 | 4.2036 | 2.1084 | 0.28751 | 0.47791 | 0.51623 | 0.3204
2021-10-23 12:30 | 0.28993 | 1.3774 | 3.614 | 1.7625 | 0.27752 | 0.46458 | 0.53136 | 0.33093
2021-10-23 12:45 | 0.85347 | 1.1889 | 3.5323 | 1.9283 | 0.24505 | 0.47795 | 0.50271 | 0.33864
2021-10-23 13:00 | 3.0729 | 1.1096 | 3.5936 | 1.689 | 0.1957 | 0.47854 | 0.44226 | 0.34367
2021-10-23 13:15 | 0.68196 | 1.0852 | 3.3996 | 1.6852 | 0.14635 | 0.47261 | 0.3818 | 0.34871
2021-10-23 13:30 | 0.34915 | 1.0774 | 3.4608 | 1.9404 | 0.096992 | 0.45416 | 0.32135 | 0.35374
2021-10-23 13:45 | 0.25931 | 1.0618 | 3.5936 | 1.4672 | 0.13021 | 0.45487 | 0.30864 | 0.34462
2021-10-23 14:00 | 0.23276 | 1.0618 | 3.5425 | 1.3006 | 0.22556 | 0.43283 | 0.33066 | 0.32748
2021-10-23 14:15 | 0.23174 | 1.0694 | 3.471 | 1.2066 | 0.32091 | 0.44077 | 0.35269 | 0.31034
2021-10-23 14:30 | 0.23276 | 1.0559 | 3.4302 | 1.2868 | 0.41626 | 0.44592 | 0.37472 | 0.2932
2021-10-23 14:45 | 0.34506 | 1.0626 | 3.369 | 1.0191 | 0.46898 | 0.42011 | 0.3478 | 0.2831
2021-10-23 15:00 | 0.30933 | 1.0501 | 3.3485 | 1.0261 | 0.48957 | 0.38013 | 0.28521 | 0.2768
2021-10-23 15:15 | 2.3889 | 1.0134 | 3.42 | 1.4213 | 0.51016 | 0.3586 | 0.22263 | 0.2705
2021-10-23 15:30 | 2.0826 | 1.0472 | 3.5017 | 1.0419 | 0.53075 | 0.30721 | 0.16004 | 0.26419
2021-10-23 15:45 | 0.70646 | 1.0629 | 3.6752 | 1.0838 | 0.47115 | 0.23615 | 0.11433 | 0.22967
2021-10-23 16:00 | 0.61662 | 1.0652 | 2.9504 | 0.77369 | 0.35104 | 0.20943 | 0.080919 | 0.17787
2021-10-23 16:15 | 0.55128 | 1.0652 | 2.4297 | 0.65731 | 0.23094 | 0.16587 | 0.047511 | 0.12607
2021-10-23 16:30 | 0.52678 | 0.96813 | 1.7968 | 0.56076 | 0.11084 | 0.13363 | 0.014104 | 0.074266
2021-10-23 16:45 | 0.5717 | 0.97128 | 1.613 | 0.93062 | 0.050719 | 0.10709 | 0 | 0.045767
2021-10-23 17:00 | 0.57987 | 1.07 | 1.6641 | 0.8453 | 0.035936 | 0.077477 | 0 | 0.032243
2021-10-23 17:15 | 0.5962 | 0.90721 | 1.4088 | 0.53962 | 0.021152 | 0.048617 | 0 | 0.018719
2021-10-23 17:30 | 0.37671 | 0.94951 | 1.1638 | 0.50111 | 0.006368 | 0.011022 | 0 | 0.005195
2021-10-23 17:45 | 0.33587 | 1.1088 | 1.7866 | 0.61939 | 0 | 0 | 0 | 0
2021-10-23 18:00 | 0.41653 | 1.0643 | 1.3374 | 1.2806 | 0 | 0 | 0 | 0
2021-10-23 18:15 | 0.63296 | 1.1546 | 0.56762 | 1.6424 | 0 | 0 | 0 | 0
2021-10-23 18:30 | 0.73913 | 1.2823 | 1.2761 | 1.9829 | 0 | 0 | 0 | 0
2021-10-23 18:45 | 2.4706 | 1.2809 | 1.0924 | 1.7953 | 0 | 0 | 0 | 0
2021-10-23 19:00 | 2.0826 | 0.99769 | 0.88614 | 0.85303 | 0 | 0 | 0 | 0
2021-10-23 19:15 | 2.052 | 1.002 | 0.64929 | 0.8666 | 0 | 0 | 0 | 0
2021-10-23 19:30 | 0.98823 | 1.0491 | 0.61254 | 0.95847 | 0 | 0 | 0 | 0
2021-10-23 19:45 | 1.1638 | 1.3246 | 0.66562 | 1.4258 | 0 | 0 | 0 | 0
2021-10-23 20:00 | 0.72279 | 1.0711 | 0.60845 | 1.1979 | 0 | 0 | 0 | 0
2021-10-23 20:15 | 0.69421 | 1.0619 | 0.57987 | 1.1069 | 0 | 0 | 0 | 0
2021-10-23 20:30 | 2.3174 | 1.015 | 0.58395 | 0.93879 | 0 | 0 | 0 | 0
2021-10-23 20:45 | 2.2766 | 1.0809 | 0.57578 | 1.1393 | 0 | 0 | 0 | 0
2021-10-23 21:00 | 2.1235 | 0.84052 | 0.58395 | 0.67379 | 0 | 0 | 0 | 0
2021-10-23 21:15 | 2.001 | 0.66935 | 0.55537 | 0.51949 | 0 | 0 | 0 | 0
2021-10-23 21:30 | 1.7457 | 0.77447 | 0.51045 | 0.54997 | 0 | 0 | 0 | 0
2021-10-23 21:45 | 0.5717 | 0.64826 | 0.40325 | 0.44788 | 0 | 0 | 0 | 0
2021-10-23 22:00 | 4.1166 | 1.1055 | 1.1536 | 1.8131 | 0 | 0 | 0 | 0
2021-10-23 22:15 | 3.4404 | 1.1187 | 0.59212 | 1.8036 | 0 | 0 | 0 | 0
2021-10-23 22:30 | 3.4404 | 1.0579 | 0.39304 | 1.7272 | 0 | 0 | 0 | 0
2021-10-23 22:45 | 3.5221 | 1.0778 | 0.37058 | 1.7144 | 0 | 0 | 0 | 0
2021-10-23 23:00 | 3.5425 | 1.1593 | 0.40632 | 1.7017 | 0 | 0 | 0 | 0
2021-10-23 23:15 | 3.4915 | 1.1826 | 0.38079 | 1.6881 | 0 | 0 | 0 | 0
2021-10-23 23:30 | 3.4506 | 1.1826 | 0.2736 | 1.6534 | 0 | 0 | 0 | 0
2021-10-23 23:45 | 3.4608 | 1.1826 | 0.27768 | 1.6336 | 0 | 0 | 0 | 0
2021-10-24 | 3.4608 | 0.90161 | 0.28789 | 1.6425 | 0 | 0 | 0 | 0
2021-10-24 00:15 | 3.5017 | 0.94638 | 0.37365 | 1.663 | 0 | 0 | 0 | 0
2021-10-24 00:30 | 3.4302 | 0.9688 | 0.41653 | 1.6536 | 0 | 0 | 0 | 0
2021-10-24 00:45 | 3.3894 | 0.9827 | 0.33894 | 1.6638 | 0 | 0 | 0 | 0
2021-10-24 01:00 | 3.369 | 0.9827 | 0.28891 | 1.6191 | 0 | 0 | 0 | 0
2021-10-24 01:15 | 3.4302 | 0.91368 | 0.27666 | 1.5983 | 0 | 0 | 0 | 0
2021-10-24 01:30 | 3.5017 | 0.91368 | 0.33077 | 1.6251 | 0 | 0 | 0 | 0
2021-10-24 01:45 | 3.3996 | 0.91368 | 0.39713 | 1.6406 | 0 | 0 | 0 | 0
2021-10-24 02:00 | 3.3894 | 1.0378 | 0.32873 | 1.6645 | 0 | 0 | 0 | 0
2021-10-24 02:15 | 3.4098 | 0.96864 | 0.27258 | 1.4984 | 0 | 0 | 0 | 0
2021-10-24 02:30 | 3.42 | 1.1038 | 0.26748 | 1.3193 | 0 | 0 | 0 | 0
2021-10-24 02:45 | 2.981 | 1.0144 | 0.35323 | 1.0854 | 0 | 0 | 0 | 0
2021-10-24 03:00 | 1.368 | 1.0069 | 0.38386 | 0.96664 | 0 | 0 | 0 | 0
2021-10-24 03:15 | 0.69013 | 0.98959 | 0.3175 | 0.84253 | 0 | 0 | 0 | 0
2021-10-24 03:30 | 0.3859 | 1.0227 | 0.26339 | 0.7944 | 0 | 0 | 0 | 0
2021-10-24 03:45 | 0.38998 | 0.89718 | 0.27462 | 0.74292 | 0 | 0 | 0 | 0
2021-10-24 04:00 | 0.33894 | 0.88834 | 0.30933 | 0.73082 | 0 | 0 | 0 | 0
2021-10-24 04:15 | 0.27054 | 0.91518 | 0.38488 | 0.7365 | 0 | 0 | 0 | 0
2021-10-24 04:30 | 0.27258 | 0.94382 | 0.26135 | 0.72775 | 0 | 0 | 0 | 0
2021-10-24 04:45 | 0.29096 | 0.91518 | 0.25931 | 0.75036 | 0 | 0 | 0 | 0
2021-10-24 05:00 | 0.40019 | 0.88691 | 0.26748 | 0.75065 | 0 | 0 | 0 | 0
2021-10-24 05:15 | 0.30525 | 0.90997 | 0.38794 | 0.76348 | 0 | 0 | 0 | 0
2021-10-24 05:30 | 0.27768 | 0.95739 | 0.35323 | 0.71959 | 0 | 0 | 0 | 0
2021-10-24 05:45 | 0.27973 | 0.92875 | 0.25216 | 0.70661 | 0 | 0.000283 | 0 | 0
2021-10-24 06:00 | 0.36956 | 0.59278 | 0.29198 | 0.34958 | 0 | 0.000765 | 0 | 0
2021-10-24 06:15 | 0.35731 | 0.61147 | 0.27768 | 0.31881 | 0 | 0.001737 | 0 | 0
2021-10-24 06:30 | 0.32465 | 0.62056 | 0.43286 | 0.35367 | 0 | 0.003437 | 0 | 0
2021-10-24 06:45 | 0.27973 | 0.67915 | 0.68604 | 0.46334 | 0.031429 | 0.077317 | 0.037354 | 0.018954
2021-10-24 07:00 | 1.0821 | 1.1888 | 1.174 | 1.2385 | 0.087077 | 0.15242 | 0.10254 | 0.050749
2021-10-24 07:15 | 0.66971 | 1.0505 | 0.83713 | 1.1656 | 0.14272 | 0.23133 | 0.16773 | 0.082545
2021-10-24 07:30 | 0.30218 | 1.2977 | 0.91064 | 1.1508 | 0.19837 | 0.28177 | 0.23292 | 0.11434
2021-10-24 07:45 | 0.29198 | 1.1983 | 0.56762 | 1.1061 | 0.22556 | 0.32296 | 0.30781 | 0.1426
2021-10-24 08:00 | 0.37773 | 1.1777 | 0.64112 | 0.87039 | 0.23078 | 0.35274 | 0.38994 | 0.16892
2021-10-24 08:15 | 0.44919 | 1.2003 | 0.58395 | 0.8453 | 0.236 | 0.35991 | 0.47207 | 0.19524
2021-10-24 08:30 | 0.5472 | 1.1271 | 0.47778 | 0.59329 | 0.24122 | 0.38816 | 0.5542 | 0.22156
2021-10-24 08:45 | 0.98414 | 1.2264 | 0.38692 | 0.95045 | 0.24224 | 0.39909 | 0.59657 | 0.23258
2021-10-24 09:00 | 0.61254 | 1.2998 | 0.37467 | 1.115 | 0.23999 | 0.40415 | 0.60923 | 0.23268
2021-10-24 09:15 | 0.45736 | 1.3431 | 0.3859 | 1.1737 | 0.23775 | 0.43315 | 0.62188 | 0.23279
2021-10-24 09:30 | 0.49411 | 1.2966 | 0.38692 | 1.0773 | 0.23551 | 0.46772 | 0.63453 | 0.23289
2021-10-24 09:45 | 0.47778 | 1.3431 | 0.40632 | 1.1912 | 0.26367 | 0.44305 | 0.64204 | 0.26489
2021-10-24 10:00 | 0.32465 | 1.2674 | 0.51862 | 1.1622 | 0.31536 | 0.40493 | 0.64571 | 0.31886
2021-10-24 10:15 | 0.26135 | 1.3586 | 0.46961 | 1.1166 | 0.36705 | 0.42568 | 0.64937 | 0.37282
2021-10-24 10:30 | 0.26033 | 1.4536 | 0.28381 | 1.3345 | 0.41873 | 0.41607 | 0.65303 | 0.42679
2021-10-24 10:45 | 0.31852 | 1.2687 | 0.23072 | 0.92756 | 0.47315 | 0.41922 | 0.60581 | 0.43111
2021-10-24 11:00 | 0.29912 | 1.312 | 0.23583 | 0.83334 | 0.52967 | 0.42068 | 0.52047 | 0.40076
2021-10-24 11:15 | 0.32975 | 1.3483 | 1.2761 | 0.9662 | 0.5862 | 0.41233 | 0.43513 | 0.37041
2021-10-24 11:30 | 1.1332 | 1.3732 | 1.8682 | 1.3442 | 0.64272 | 0.42363 | 0.34979 | 0.34006
2021-10-24 11:45 | 0.85755 | 1.6625 | 0.43694 | 1.6229 | 0.66709 | 0.42432 | 0.30749 | 0.33385
2021-10-24 12:00 | 0.83713 | 1.7319 | 0.42878 | 1.634 | 0.66652 | 0.43137 | 0.2975 | 0.34419
2021-10-24 12:15 | 0.50228 | 1.9062 | 0.33281 | 2.103 | 0.66594 | 0.42319 | 0.28751 | 0.35453
2021-10-24 12:30 | 0.68196 | 1.6535 | 0.28993 | 1.5895 | 0.66536 | 0.42501 | 0.27752 | 0.36488
2021-10-24 12:45 | 0.40836 | 1.7069 | 0.85347 | 1.7206 | 0.66254 | 0.436 | 0.24505 | 0.36018
2021-10-24 13:00 | 0.38998 | 1.79 | 3.0729 | 2.0985 | 0.65796 | 0.41937 | 0.1957 | 0.34506
2021-10-24 13:15 | 0.31546 | 1.8225 | 0.68196 | 1.7507 | 0.65339 | 0.42302 | 0.14635 | 0.32995
2021-10-24 13:30 | 0.27564 | 1.7957 | 0.34915 | 1.939 | 0.64881 | 0.40864 | 0.096992 | 0.31484
2021-10-24 13:45 | 0.31648 | 1.5838 | 0.25931 | 1.4695 | 0.64306 | 0.40973 | 0.13021 | 0.3023
2021-10-24 14:00 | 0.40325 | 1.5838 | 0.23276 | 1.3032 | 0.63639 | 0.37214 | 0.22556 | 0.29357
2021-10-24 14:15 | 0.46553 | 1.2699 | 0.23174 | 1.208 | 0.62973 | 0.37098 | 0.32091 | 0.28483
2021-10-24 14:30 | 0.46961 | 1.4464 | 0.23276 | 1.2751 | 0.62306 | 0.39409 | 0.41626 | 0.2761
2021-10-24 14:45 | 2.9198 | 1.2948 | 0.34506 | 1.0237 | 0.60519 | 0.38425 | 0.46898 | 0.27266
2021-10-24 15:00 | 1.7968 | 1.2381 | 0.30933 | 1.0404 | 0.57859 | 0.37432 | 0.48957 | 0.27101
2021-10-24 15:15 | 0.41244 | 1.8937 | 2.3889 | 1.7304 | 0.55198 | 0.36174 | 0.51016 | 0.26935
2021-10-24 15:30 | 0.41244 | 1.3944 | 2.0826 | 1.3067 | 0.52538 | 0.3349 | 0.53075 | 0.2677
2021-10-24 15:45 | 0.49003 | 1.2873 | 0.70646 | 1.1392 | 0.44172 | 0.29152 | 0.47115 | 0.2324
2021-10-24 16:00 | 0.75546 | 1.2112 | 0.61662 | 0.8227 | 0.31355 | 0.23119 | 0.35104 | 0.17475
2021-10-24 16:15 | 0.4982 | 1.1762 | 0.55128 | 0.69115 | 0.18537 | 0.20588 | 0.23094 | 0.11709
2021-10-24 16:30 | 0.48595 | 1.1569 | 0.52678 | 0.57068 | 0.057193 | 0.15976 | 0.11084 | 0.059442
2021-10-24 16:45 | 0.43694 | 1.1802 | 0.5717 | 0.93529 | 0.000834 | 0.1251 | 0.050719 | 0.030717
2021-10-24 17:00 | 0.26952 | 1.1589 | 0.57987 | 0.84122 | 0.000591 | 0.088866 | 0.035936 | 0.021691
2021-10-24 17:15 | 0.35323 | 1.0286 | 0.5962 | 0.55245 | 0.000349 | 0.033713 | 0.021152 | 0.012665
2021-10-24 17:30 | 0.33996 | 0.88525 | 0.37671 | 0.48493 | 0.000106 | 0.008903 | 0.006368 | 0.003638
2021-10-24 17:45 | 0.27156 | 1.2445 | 0.33587 | 0.59504 | 0 | 0 | 0 | 0
2021-10-24 18:00 | 0.26543 | 1.2421 | 0.41653 | 1.2538 | 0 | 0 | 0 | 0
2021-10-24 18:15 | 0.31852 | 1.5121 | 0.63296 | 1.6564 | 0 | 0 | 0 | 0
2021-10-24 18:30 | 0.5717 | 1.6714 | 0.73913 | 1.861 | 0 | 0 | 0 | 0
2021-10-24 18:45 | 0.71463 | 1.5487 | 2.4706 | 2.0648 | 0 | 0 | 0 | 0
2021-10-24 19:00 | 1.9907 | 1.1138 | 2.0826 | 1.0566 | 0 | 0 | 0 | 0
2021-10-24 19:15 | 1.8784 | 1.0554 | 2.052 | 1.0553 | 0 | 0 | 0 | 0
2021-10-24 19:30 | 1.6743 | 1.0704 | 0.98823 | 0.99581 | 0 | 0 | 0 | 0
2021-10-24 19:45 | 2.4297 | 1.3163 | 1.1638 | 1.4876 | 0 | 0 | 0 | 0
2021-10-24 20:00 | 2.2051 | 1.1991 | 0.72279 | 1.2131 | 0 | 0 | 0 | 0
2021-10-24 20:15 | 2.1541 | 1.0433 | 0.69421 | 1.1291 | 0 | 0 | 0 | 0
2021-10-24 20:30 | 4.0121 | 1.1899 | 2.3174 | 1.1975 | 0 | 0 | 0 | 0
2021-10-24 20:45 | 2.0724 | 1.2871 | 2.2766 | 1.384 | 0 | 0 | 0 | 0
2021-10-24 21:00 | 0.5962 | 0.94752 | 2.1235 | 0.89606 | 0 | 0 | 0 | 0
2021-10-24 21:15 | 0.53495 | 0.81512 | 2.001 | 0.73125 | 0 | 0 | 0 | 0
2021-10-24 21:30 | 0.70238 | 0.83005 | 1.7457 | 0.69844 | 0 | 0 | 0 | 0
2021-10-24 21:45 | 0.52678 | 0.5819 | 0.5717 | 0.4578 | 0 | 0 | 0 | 0
2021-10-24 22:00 | 1.3578 | 2.1141 | 4.1166 | 2.3207 | 0 | 0 | 0 | 0
2021-10-24 22:15 | 3.0831 | 2.1571 | 3.4404 | 2.2146 | 0 | 0 | 0 | 0
2021-10-24 22:30 | 0.54312 | 2.1516 | 3.4404 | 2.1388 | 0 | 0 | 0 | 0
2021-10-24 22:45 | 0.54312 | 2.0864 | 3.5221 | 2.1289 | 0 | 0 | 0 | 0
2021-10-24 23:00 | 0.42878 | 2.0793 | 3.5425 | 2.1477 | 0 | 0 | 0 | 0
2021-10-24 23:15 | 0.37977 | 2.086 | 3.4915 | 2.1417 | 0 | 0 | 0 | 0
2021-10-24 23:30 | 0.27564 | 1.928 | 3.4506 | 2.1026 | 0 | 0 | 0 | 0
2021-10-24 23:45 | 0.2787 | 1.8684 | 3.4608 | 2.0888 | 0 | 0 | 0 | 0
2021-10-25 | 0.28381 | 2.1811 | 3.4608 | 2.0923 | 0 | 0 | 0 | 0
2021-10-25 00:15 | 0.28789 | 2.3555 | 3.5017 | 2.1201 | 0 | 0 | 0 | 0
2021-10-25 00:30 | 0.27973 | 2.2302 | 3.4302 | 2.0841 | 0 | 0 | 0 | 0
2021-10-25 00:45 | 0.39407 | 2.2802 | 3.3894 | 2.0931 | 0 | 0 | 0 | 0
2021-10-25 01:00 | 0.40836 | 2.1811 | 3.369 | 2.0612 | 0 | 0 | 0 | 0
2021-10-25 01:15 | 0.32669 | 2.041 | 3.4302 | 2.0485 | 0 | 0 | 0 | 0
2021-10-25 01:30 | 0.2787 | 2.2145 | 3.5017 | 2.0841 | 0 | 0 | 0 | 0
2021-10-25 01:45 | 0.27564 | 2.3599 | 3.3996 | 2.0869 | 0 | 0 | 0 | 0
2021-10-25 02:00 | 0.27462 | 2.3398 | 3.3894 | 2.0886 | 0 | 0 | 0 | 0
2021-10-25 02:15 | 0.33179 | 2.202 | 3.4098 | 1.9254 | 0 | 0 | 0 | 0
2021-10-25 02:30 | 0.37161 | 1.6498 | 3.42 | 1.7711 | 0 | 0 | 0 | 0
2021-10-25 02:45 | 0.2736 | 1.2551 | 2.981 | 1.4692 | 0 | 0 | 0 | 0
2021-10-25 03:00 | 0.2736 | 1.2064 | 1.368 | 1.1225 | 0 | 0 | 0 | 0
2021-10-25 03:15 | 0.28993 | 0.95497 | 0.69013 | 0.89562 | 0 | 0 | 0 | 0
2021-10-25 03:30 | 0.40632 | 0.86087 | 0.3859 | 0.78944 | 0 | 0 | 0 | 0
2021-10-25 03:45 | 0.32056 | 0.8344 | 0.38998 | 0.74117 | 0 | 0 | 0 | 0
2021-10-25 04:00 | 0.28993 | 0.8344 | 0.33894 | 0.73986 | 0 | 0 | 0 | 0
2021-10-25 04:15 | 0.28789 | 0.7446 | 0.27054 | 0.73373 | 0 | 0 | 0 | 0
2021-10-25 04:30 | 0.34813 | 0.7446 | 0.27258 | 0.72702 | 0 | 0 | 0 | 0
2021-10-25 04:45 | 0.36344 | 0.75968 | 0.29096 | 0.7403 | 0 | 0 | 0 | 0
2021-10-25 05:00 | 0.28789 | 0.75946 | 0.40019 | 0.74832 | 0 | 0 | 0 | 0
2021-10-25 05:15 | 0.28891 | 0.7339 | 0.30525 | 0.76013 | 0 | 0 | 0 | 0
2021-10-25 05:30 | 0.33996 | 0.76375 | 0.27768 | 0.71784 | 0 | 0 | 0 | 0
2021-10-25 05:45 | 0.35323 | 0.74866 | 0.27973 | 0.70515 | 0 | 9e-05 | 0 | 0
2021-10-25 06:00 | 0.29504 | 0.62911 | 0.36956 | 0.35921 | 0 | 0.000248 | 0 | 0
2021-10-25 06:15 | 0.2981 | 0.6478 | 0.35731 | 0.31721 | 0 | 0.000435 | 0 | 0
2021-10-25 06:30 | 0.35935 | 0.6478 | 0.32465 | 0.33821 | 0 | 0.000689 | 0 | 0
2021-10-25 06:45 | 0.35221 | 0.65899 | 0.27973 | 0.4562 | 0.058342 | 0.03274 | 0.031429 | 0.021811
2021-10-25 07:00 | 0.27666 | 1.3733 | 1.0821 | 1.352 | 0.16317 | 0.078727 | 0.087077 | 0.058931
2021-10-25 07:15 | 0.28993 | 1.1341 | 0.66971 | 1.2192 | 0.26799 | 0.1256 | 0.14272 | 0.096052
2021-10-25 07:30 | 0.3471 | 1.0986 | 0.30218 | 1.0073 | 0.37281 | 0.18697 | 0.19837 | 0.13317
2021-10-25 07:45 | 0.40019 | 0.99024 | 0.29198 | 0.88672 | 0.4445 | 0.19842 | 0.22556 | 0.16434
2021-10-25 08:00 | 0.35323 | 1.2084 | 0.37773 | 0.71434 | 0.48977 | 0.21221 | 0.23078 | 0.19142
2021-10-25 08:15 | 0.46144 | 1.2065 | 0.44919 | 0.7823 | 0.53503 | 0.23799 | 0.236 | 0.21851
2021-10-25 08:30 | 1.1536 | 1.1606 | 0.5472 | 0.53845 | 0.58029 | 0.28879 | 0.24122 | 0.24559
2021-10-25 08:45 | 0.76363 | 1.2819 | 0.98414 | 0.98779 | 0.60639 | 0.31086 | 0.24224 | 0.25713
2021-10-25 09:00 | 0.83305 | 1.2539 | 0.61254 | 1.1004 | 0.61719 | 0.31745 | 0.23999 | 0.25752
2021-10-25 09:15 | 0.94739 | 1.3295 | 0.45736 | 1.1323 | 0.62799 | 0.32405 | 0.23775 | 0.25791
2021-10-25 09:30 | 1.0168 | 1.2562 | 0.49411 | 1.0219 | 0.63879 | 0.33064 | 0.23551 | 0.2583
2021-10-25 09:45 | 0.89431 | 1.2907 | 0.47778 | 1.1644 | 0.64326 | 0.33714 | 0.26367 | 0.29353
2021-10-25 10:00 | 0.81263 | 1.2533 | 0.32465 | 1.1182 | 0.64268 | 0.33955 | 0.31536 | 0.35324
2021-10-25 10:15 | 0.77997 | 1.1848 | 0.26135 | 1.074 | 0.64209 | 0.34147 | 0.36705 | 0.41294
2021-10-25 10:30 | 0.84122 | 1.0463 | 0.26033 | 1.3051 | 0.6415 | 0.3434 | 0.41873 | 0.47265
2021-10-25 10:45 | 0.80447 | 1.179 | 0.31852 | 0.91414 | 0.64139 | 0.32951 | 0.47315 | 0.48216
2021-10-25 11:00 | 0.77588 | 1.1456 | 0.29912 | 0.81015 | 0.64167 | 0.33352 | 0.52967 | 0.45673
2021-10-25 11:15 | 0.78813 | 1.3055 | 0.32975 | 0.96679 | 0.64195 | 0.34459 | 0.5862 | 0.4313
2021-10-25 11:30 | 0.72688 | 1.3637 | 1.1332 | 1.1882 | 0.64223 | 0.35344 | 0.64272 | 0.40588
2021-10-25 11:45 | 2.5624 | 1.4457 | 0.85755 | 0.93368 | 0.64009 | 0.36301 | 0.66709 | 0.39532
2021-10-25 12:00 | 0.66562 | 1.2317 | 0.83713 | 1.2475 | 0.63602 | 0.3668 | 0.66652 | 0.3949
2021-10-25 12:15 | 0.65337 | 1.4913 | 0.50228 | 1.6307 | 0.63195 | 0.36649 | 0.66594 | 0.39448
2021-10-25 12:30 | 0.72688 | 1.1323 | 0.68196 | 1.0684 | 0.62788 | 0.36617 | 0.66536 | 0.39407
2021-10-25 12:45 | 0.82897 | 1.3564 | 0.40836 | 1.286 | 0.6238 | 0.36461 | 0.66254 | 0.38392
2021-10-25 13:00 | 0.7963 | 1.7146 | 0.38998 | 1.6555 | 0.61971 | 0.3621 | 0.65796 | 0.36656
2021-10-25 13:15 | 0.88205 | 1.3056 | 0.31546 | 1.2751 | 0.61562 | 0.35958 | 0.65339 | 0.3492
2021-10-25 13:30 | 1.4599 | 1.2256 | 0.27564 | 1.2087 | 0.61152 | 0.34896 | 0.64881 | 0.33185
2021-10-25 13:45 | 0.8453 | 1.0775 | 0.31648 | 0.98094 | 0.60836 | 0.3539 | 0.64306 | 0.32723
2021-10-25 14:00 | 0.99231 | 1.1096 | 0.40325 | 0.84603 | 0.60594 | 0.34311 | 0.63639 | 0.33262
2021-10-25 14:15 | 0.70646 | 1.0865 | 0.46553 | 0.9945 | 0.60351 | 0.33491 | 0.62973 | 0.338
2021-10-25 14:30 | 0.51862 | 1.0865 | 0.46961 | 1.0286 | 0.60109 | 0.33137 | 0.62306 | 0.34339
2021-10-25 14:45 | 0.53087 | 1.2848 | 2.9198 | 1.1433 | 0.58229 | 0.32186 | 0.60519 | 0.33716
2021-10-25 15:00 | 0.40632 | 1.1907 | 1.7968 | 0.99085 | 0.5503 | 0.30912 | 0.57859 | 0.32206
2021-10-25 15:15 | 0.47778 | 1.404 | 0.41244 | 1.1065 | 0.51831 | 0.29256 | 0.55198 | 0.30696
2021-10-25 15:30 | 0.50636 | 1.3499 | 0.41244 | 1.0681 | 0.48632 | 0.31055 | 0.52538 | 0.29186
2021-10-25 15:45 | 0.55128 | 1.2015 | 0.49003 | 0.94374 | 0.40673 | 0.26492 | 0.44172 | 0.24931
2021-10-25 16:00 | 0.53903 | 1.2521 | 0.75546 | 0.83028 | 0.28873 | 0.20978 | 0.31355 | 0.18686
2021-10-25 16:15 | 0.67788 | 1.2448 | 0.4982 | 0.70646 | 0.17073 | 0.16266 | 0.18537 | 0.12441
2021-10-25 16:30 | 0.7473 | 1.1262 | 0.48595 | 0.59474 | 0.052729 | 0.12425 | 0.057193 | 0.061969
2021-10-25 16:45 | 0.77997 | 1.2577 | 0.43694 | 0.57914 | 0 | 0.06733 | 0.000834 | 0.03042
2021-10-25 17:00 | 0.74321 | 1.1935 | 0.26952 | 0.59825 | 0 | 0.04232 | 0.000591 | 0.021482
2021-10-25 17:15 | 0.52678 | 1.1753 | 0.35323 | 0.53349 | 0 | 0.024269 | 0.000349 | 0.012544
2021-10-25 17:30 | 0.49003 | 1.1148 | 0.33996 | 0.45415 | 0 | 0.005435 | 0.000106 | 0.003607
2021-10-25 17:45 | 0.40632 | 1.1753 | 0.27156 | 0.53816 | 0 | 0 | 0 | 0
2021-10-25 18:00 | 0.38386 | 1.3067 | 0.26543 | 1.1762 | 0 | 0 | 0 | 0
2021-10-25 18:15 | 0.48186 | 1.457 | 0.31852 | 1.5776 | 0 | 0 | 0 | 0
2021-10-25 18:30 | 1.7662 | 1.64 | 0.5717 | 1.8324 | 0 | 0 | 0 | 0
2021-10-25 18:45 | 1.4088 | 1.5588 | 0.71463 | 2.0619 | 0 | 0 | 0 | 0
2021-10-25 19:00 | 1.3067 | 1.0606 | 1.9907 | 1.2325 | 0 | 0 | 0 | 0
2021-10-25 19:15 | 1.2761 | 0.9226 | 1.8784 | 1.0291 | 0 | 0 | 0 | 0
2021-10-25 19:30 | 1.2863 | 1.0885 | 1.6743 | 0.9856 | 0 | 0 | 0 | 0
2021-10-25 19:45 | 0.67379 | 1.6476 | 2.4297 | 1.6013 | 0 | 0 | 0 | 0
2021-10-25 20:00 | 0.54312 | 1.3653 | 2.2051 | 1.4255 | 0 | 0 | 0 | 0
2021-10-25 20:15 | 0.56354 | 1.4228 | 2.1541 | 1.3639 | 0 | 0 | 0 | 0
2021-10-25 20:30 | 0.51453 | 2.0718 | 4.0121 | 1.6674 | 0 | 0 | 0 | 0
2021-10-25 20:45 | 0.55128 | 1.3526 | 2.0724 | 1.5211 | 0 | 0 | 0 | 0
2021-10-25 21:00 | 0.51862 | 0.81953 | 0.5962 | 0.77121 | 0 | 0 | 0 | 0
2021-10-25 21:15 | 0.48595 | 0.92771 | 0.53495 | 0.73009 | 0 | 0 | 0 | 0
2021-10-25 21:30 | 0.50636 | 0.9082 | 0.70238 | 0.74992 | 0 | 0 | 0 | 0
2021-10-25 21:45 | 0.49003 | 0.72674 | 0.52678 | 0.46305 | 0 | 0 | 0 | 0
2021-10-25 22:00 | 0.49003 | 1.9509 | 1.3578 | 2.0232 | 0 | 0 | 0 | 0
2021-10-25 22:15 | 0.44511 | 2.4653 | 3.0831 | 2.1329 | 0 | 0 | 0 | 0
2021-10-25 22:30 | 0.34098 | 2.1923 | 0.54312 | 1.7118 | 0 | 0 | 0 | 0
2021-10-25 22:45 | 0.45328 | 2.1923 | 0.54312 | 1.7077 | 0 | 0 | 0 | 0
2021-10-25 23:00 | 0.43286 | 2.202 | 0.42878 | 1.6985 | 0 | 0 | 0 | 0
2021-10-25 23:15 | 0.44919 | 2.2893 | 0.37977 | 1.6826 | 0 | 0 | 0 | 0
2021-10-25 23:30 | 0.44511 | 2.4228 | 0.27564 | 1.6403 | 0 | 0 | 0 | 0
2021-10-25 23:45 | 0.42878 | 2.3913 | 0.2787 | 1.6269 | 0 | 0 | 0 | 0
2021-10-26 | 0.43694 | 1.4789 | 0.28381 | 1.6399 | 0 | 0 | 0 | 0
2021-10-26 00:15 | 0.42878 | 1.3768 | 0.28789 | 1.677 | 0 | 0 | 0 | 0
2021-10-26 00:30 | 0.43286 | 1.4432 | 0.27973 | 1.6471 | 0 | 0 | 0 | 0
2021-10-26 00:45 | 0.37773 | 1.4432 | 0.39407 | 1.6667 | 0 | 0 | 0 | 0
2021-10-26 01:00 | 0.33485 | 1.4789 | 0.40836 | 1.6353 | 0 | 0 | 0 | 0
2021-10-26 01:15 | 0.34608 | 1.4125 | 0.32669 | 1.6226 | 0 | 0 | 0 | 0
2021-10-26 01:30 | 0.34506 | 1.3768 | 0.2787 | 1.647 | 0 | 0 | 0 | 0
2021-10-26 01:45 | 0.34098 | 1.6088 | 0.27564 | 1.6245 | 0 | 0 | 0 | 0
2021-10-26 02:00 | 0.33281 | 1.6898 | 0.27462 | 1.6393 | 0 | 0 | 0 | 0
2021-10-26 02:15 | 0.41244 | 1.5859 | 0.33179 | 1.4915 | 0 | 0 | 0 | 0
2021-10-26 02:30 | 0.49411 | 1.3785 | 0.37161 | 1.3706 | 0 | 0 | 0 | 0
2021-10-26 02:45 | 0.49003 | 1.1579 | 0.2736 | 1.2545 | 0 | 0 | 0 | 0
2021-10-26 03:00 | 0.47778 | 0.94658 | 0.2736 | 0.98954 | 0 | 0 | 0 | 0
2021-10-26 03:15 | 0.4737 | 0.92924 | 0.28993 | 0.81395 | 0 | 0 | 0 | 0
2021-10-26 03:30 | 0.36854 | 0.92924 | 0.40632 | 0.7734 | 0 | 0 | 0 | 0
2021-10-26 03:45 | 0.29198 | 0.92924 | 0.32056 | 0.75459 | 0 | 0 | 0 | 0
2021-10-26 04:00 | 0.29504 | 0.92924 | 0.28993 | 0.74336 | 0 | 0 | 0 | 0
2021-10-26 04:15 | 0.30627 | 0.93836 | 0.28789 | 0.73213 | 0 | 0 | 0 | 0
2021-10-26 04:30 | 0.29198 | 0.89705 | 0.34813 | 0.74555 | 0 | 0 | 0 | 0
2021-10-26 04:45 | 0.29096 | 0.84123 | 0.36344 | 0.75882 | 0 | 0 | 0 | 0
2021-10-26 05:00 | 0.30014 | 0.89705 | 0.28789 | 0.74452 | 0 | 0 | 0 | 0
2021-10-26 05:15 | 0.29504 | 0.91477 | 0.28891 | 0.7664 | 0 | 0 | 0 | 0
2021-10-26 05:30 | 0.37875 | 0.84123 | 0.33996 | 0.73504 | 0 | 0 | 0 | 0
2021-10-26 05:45 | 0.40836 | 0.84123 | 0.35323 | 0.72032 | 0 | 6e-05 | 0 | 0
2021-10-26 06:00 | 0.42878 | 0.52006 | 0.29504 | 0.35571 | 0 | 0.000171 | 0 | 0
2021-10-26 06:15 | 0.41653 | 0.48417 | 0.2981 | 0.31837 | 0 | 0.000792 | 0 | 0
2021-10-26 06:30 | 0.33485 | 0.48417 | 0.35935 | 0.35133 | 0 | 0.00118 | 0 | 0
2021-10-26 06:45 | 0.29708 | 0.63895 | 0.35221 | 0.46655 | 0.021772 | 0.035908 | 0.058342 | 0.022437
2021-10-26 07:00 | 0.35425 | 1.0455 | 0.27666 | 1.2701 | 0.061476 | 0.074172 | 0.16317 | 0.061982
2021-10-26 07:15 | 0.34506 | 1.0088 | 0.28993 | 1.1971 | 0.10118 | 0.1214 | 0.26799 | 0.10153
2021-10-26 07:30 | 0.37161 | 1.0968 | 0.3471 | 1.0238 | 0.14088 | 0.17409 | 0.37281 | 0.14107
2021-10-26 07:45 | 0.8453 | 1.0559 | 0.40019 | 0.90014 | 0.14221 | 0.22291 | 0.4445 | 0.1759
2021-10-26 08:00 | 0.81672 | 0.98079 | 0.35323 | 0.70763 | 0.11189 | 0.25085 | 0.48977 | 0.20663
2021-10-26 08:15 | 0.63296 | 0.99053 | 0.46144 | 0.6032 | 0.081568 | 0.26762 | 0.53503 | 0.23736
2021-10-26 08:30 | 0.71463 | 0.94066 | 1.1536 | 0.62391 | 0.051246 | 0.29786 | 0.58029 | 0.26809
2021-10-26 08:45 | 0.62887 | 1.0837 | 0.76363 | 1.0059 | 0.039652 | 0.31126 | 0.60639 | 0.27966
2021-10-26 09:00 | 0.48186 | 1.0539 | 0.83305 | 1.0945 | 0.043527 | 0.3168 | 0.61719 | 0.27734
2021-10-26 09:15 | 0.44919 | 0.85251 | 0.94739 | 1.1492 | 0.047401 | 0.32234 | 0.62799 | 0.27501
2021-10-26 09:30 | 0.75546 | 0.85251 | 1.0168 | 1.0581 | 0.051276 | 0.33649 | 0.63879 | 0.27269
2021-10-26 09:45 | 0.52678 | 0.89459 | 0.89431 | 1.0267 | 0.054108 | 0.36531 | 0.64326 | 0.30522
2021-10-26 10:00 | 0.55128 | 0.77343 | 0.81263 | 0.963 | 0.056078 | 0.37676 | 0.64268 | 0.36207
2021-10-26 10:15 | 0.5962 | 0.80319 | 0.77997 | 0.92289 | 0.058048 | 0.39816 | 0.64209 | 0.41892
2021-10-26 10:30 | 0.71463 | 0.96206 | 0.84122 | 1.1628 | 0.060018 | 0.4004 | 0.6415 | 0.47578
2021-10-26 10:45 | 0.77588 | 1.0359 | 0.80447 | 0.97189 | 0.086872 | 0.39327 | 0.64139 | 0.48722
2021-10-26 11:00 | 3.3587 | 0.84858 | 0.77588 | 0.88526 | 0.13434 | 0.39344 | 0.64167 | 0.46675
2021-10-26 11:15 | 0.74321 | 0.85763 | 0.78813 | 1.0525 | 0.1818 | 0.39361 | 0.64195 | 0.44629
2021-10-26 11:30 | 0.70646 | 0.871 | 0.72688 | 1.2671 | 0.22926 | 0.38856 | 0.64223 | 0.42583
2021-10-26 11:45 | 0.56354 | 0.93267 | 2.5624 | 1.2738 | 0.27363 | 0.40084 | 0.64009 | 0.4134
2021-10-26 12:00 | 0.53903 | 1.0845 | 0.66562 | 1.1991 | 0.31544 | 0.40049 | 0.63602 | 0.40672
2021-10-26 12:15 | 0.52678 | 1.2251 | 0.65337 | 1.3274 | 0.35725 | 0.40014 | 0.63195 | 0.40004
2021-10-26 12:30 | 3.0933 | 0.93693 | 0.72688 | 1.09 | 0.39906 | 0.39083 | 0.62788 | 0.39336
2021-10-26 12:45 | 1.5518 | 0.83664 | 0.82897 | 1.0005 | 0.40715 | 0.38917 | 0.6238 | 0.38078
2021-10-26 13:00 | 0.55945 | 0.86816 | 0.7963 | 1.2733 | 0.38724 | 0.38648 | 0.61971 | 0.36343
2021-10-26 13:15 | 0.8208 | 0.76526 | 0.88205 | 0.89795 | 0.36733 | 0.39353 | 0.61562 | 0.34608
2021-10-26 13:30 | 0.41244 | 0.7423 | 1.4599 | 0.9506 | 0.34742 | 0.40204 | 0.61152 | 0.32873
2021-10-26 13:45 | 0.37875 | 0.82562 | 0.8453 | 0.87564 | 0.3257 | 0.39848 | 0.60836 | 0.32626
2021-10-26 14:00 | 0.38692 | 0.90968 | 0.99231 | 0.89562 | 0.30248 | 0.38555 | 0.60594 | 0.33516
2021-10-26 14:15 | 0.42878 | 0.82637 | 0.70646 | 0.8577 | 0.27926 | 0.36511 | 0.60351 | 0.34407
2021-10-26 14:30 | 0.50636 | 0.80004 | 0.51862 | 0.81978 | 0.25604 | 0.36125 | 0.60109 | 0.35298
2021-10-26 14:45 | 0.59212 | 0.8666 | 0.53087 | 1.1681 | 0.24694 | 0.35089 | 0.58229 | 0.35058
2021-10-26 15:00 | 0.58804 | 0.81369 | 0.40632 | 0.99289 | 0.24959 | 0.337 | 0.5503 | 0.33912
2021-10-26 15:15 | 0.51045 | 0.80351 | 0.47778 | 1.1205 | 0.25225 | 0.32009 | 0.51831 | 0.32765
2021-10-26 15:30 | 0.47778 | 0.80637 | 0.50636 | 1.0959 | 0.2549 | 0.30896 | 0.48632 | 0.31619
2021-10-26 15:45 | 0.42469 | 0.9199 | 0.55128 | 0.977 | 0.2212 | 0.26343 | 0.40673 | 0.26967
2021-10-26 16:00 | 0.47778 | 0.91942 | 0.53903 | 0.86776 | 0.15718 | 0.21551 | 0.28873 | 0.19727
2021-10-26 16:15 | 0.45736 | 0.8569 | 0.67788 | 0.74613 | 0.093157 | 0.16502 | 0.17073 | 0.12487
2021-10-26 16:30 | 0.5227 | 0.84719 | 0.7473 | 0.64885 | 0.029135 | 0.10731 | 0.052729 | 0.052464
2021-10-26 16:45 | 0.73913 | 0.86697 | 0.77997 | 0.64841 | 0 | 0.042212 | 0 | 0.018259
2021-10-26 17:00 | 0.71871 | 0.91319 | 0.74321 | 0.66927 | 0 | 0.012069 | 0 | 0.012909
2021-10-26 17:15 | 0.72279 | 1.0012 | 0.52678 | 0.58001 | 0 | 0.010239 | 0 | 0.007559
2021-10-26 17:30 | 0.64521 | 0.78484 | 0.49003 | 0.49236 | 0 | 0.002774 | 0 | 0.002209
2021-10-26 17:45 | 0.61662 | 0.78708 | 0.40632 | 0.56222 | 0 | 0 | 0 | 0
2021-10-26 18:00 | 0.64521 | 1.0588 | 0.38386 | 1.1767 | 0 | 0 | 0 | 0
2021-10-26 18:15 | 0.70238 | 1.5461 | 0.48186 | 1.5799 | 0 | 0 | 0 | 0
2021-10-26 18:30 | 0.71054 | 1.7713 | 1.7662 | 2.0287 | 0 | 0 | 0 | 0
2021-10-26 18:45 | 3.7875 | 1.9119 | 1.4088 | 2.2077 | 0 | 0 | 0 | 0
2021-10-26 19:00 | 3.9611 | 1.0688 | 1.3067 | 1.3627 | 0 | 0 | 0 | 0
2021-10-26 19:15 | 3.9407 | 1.0452 | 1.2761 | 1.1552 | 0 | 0 | 0 | 0
2021-10-26 19:30 | 3.8896 | 1.0517 | 1.2863 | 0.99435 | 0 | 0 | 0 | 0
2021-10-26 19:45 | 4.7146 | 1.1025 | 0.67379 | 1.2747 | 0 | 0 | 0 | 0
2021-10-26 20:00 | 1.2047 | 1.053 | 0.54312 | 1.1355 | 0 | 0 | 0 | 0
2021-10-26 20:15 | 1.0046 | 1.0439 | 0.56354 | 1.0317 | 0 | 0 | 0 | 0
2021-10-26 20:30 | 0.69829 | 0.87984 | 0.51453 | 1.3311 | 0 | 0 | 0 | 0
2021-10-26 20:45 | 0.57578 | 0.81036 | 0.55128 | 1.349 | 0 | 0 | 0 | 0
2021-10-26 21:00 | 0.62479 | 0.78304 | 0.51862 | 0.7578 | 0 | 0 | 0 | 0
2021-10-26 21:15 | 0.63704 | 0.80131 | 0.48595 | 0.70092 | 0 | 0 | 0 | 0
2021-10-26 21:30 | 0.60845 | 0.7939 | 0.50636 | 0.7085 | 0 | 0 | 0 | 0
2021-10-26 21:45 | 0.56762 | 0.58127 | 0.49003 | 0.47618 | 0 | 0 | 0 | 0
2021-10-26 22:00 | 0.60029 | 1.7071 | 0.49003 | 1.6236 | 0 | 0 | 0 | 0
2021-10-26 22:15 | 0.44919 | 1.7406 | 0.44511 | 1.6978 | 0 | 0 | 0 | 0
2021-10-26 22:30 | 0.44511 | 2.1443 | 0.34098 | 1.2617 | 0 | 0 | 0 | 0
2021-10-26 22:45 | 0.42878 | 1.8643 | 0.45328 | 1.2751 | 0 | 0 | 0 | 0
2021-10-26 23:00 | 3.3383 | 1.7917 | 0.43286 | 1.263 | 0 | 0 | 0 | 0
2021-10-26 23:15 | 3.5425 | 1.7725 | 0.44919 | 1.2451 | 0 | 0 | 0 | 0
2021-10-26 23:30 | 3.5425 | 1.7181 | 0.44511 | 1.2036 | 0 | 0 | 0 | 0
2021-10-26 23:45 | 3.4302 | 1.7181 | 0.42878 | 1.1893 | 0 | 0 | 0 | 0
2021-10-27 | 3.42 | 2.0072 | 0.43694 | 1.2035 | 0 | 0 | 0 | 0
2021-10-27 00:15 | 3.42 | 2.0778 | 0.42878 | 1.2424 | 0 | 0 | 0 | 0
2021-10-27 00:30 | 3.4813 | 1.9955 | 0.43286 | 1.2219 | 0 | 0 | 0 | 0
2021-10-27 00:45 | 3.5833 | 2.076 | 0.37773 | 1.235 | 0 | 0 | 0 | 0
2021-10-27 01:00 | 3.614 | 2.0779 | 0.33485 | 1.2004 | 0 | 0 | 0 | 0
2021-10-27 01:15 | 3.5017 | 2.0712 | 0.34608 | 1.1893 | 0 | 0 | 0 | 0
2021-10-27 01:30 | 3.471 | 2.0072 | 0.34506 | 1.2063 | 0 | 0 | 0 | 0
2021-10-27 01:45 | 3.4813 | 1.9314 | 0.34098 | 1.1818 | 0 | 0 | 0 | 0
2021-10-27 02:00 | 3.4506 | 1.8698 | 0.33281 | 1.1953 | 0 | 0 | 0 | 0
2021-10-27 02:15 | 3.4915 | 1.1446 | 0.41244 | 1.0604 | 0 | 0 | 0 | 0
2021-10-27 02:30 | 3.5731 | 1.2402 | 0.49411 | 0.94681 | 0 | 0 | 0 | 0
2021-10-27 02:45 | 3.5629 | 1.1601 | 0.49003 | 0.81701 | 0 | 0 | 0 | 0
2021-10-27 03:00 | 3.4813 | 0.97598 | 0.47778 | 0.5488 | 0 | 0 | 0 | 0
2021-10-27 03:15 | 3.471 | 0.63542 | 0.4737 | 0.37263 | 0 | 0 | 0 | 0
2021-10-27 03:30 | 3.4506 | 0.61864 | 0.36854 | 0.32873 | 0 | 0 | 0 | 0
2021-10-27 03:45 | 3.4404 | 0.59582 | 0.29198 | 0.30627 | 0 | 0 | 0 | 0
2021-10-27 04:00 | 3.4404 | 0.59582 | 0.29504 | 0.29256 | 0 | 0 | 0 | 0
2021-10-27 04:15 | 3.4506 | 0.58621 | 0.30627 | 0.28293 | 0 | 0 | 0 | 0
2021-10-27 04:30 | 3.5323 | 0.58621 | 0.29198 | 0.29723 | 0 | 0 | 0 | 0
2021-10-27 04:45 | 3.5527 | 0.58621 | 0.29096 | 0.30889 | 0 | 0 | 0 | 0
2021-10-27 05:00 | 3.5527 | 0.58621 | 0.30014 | 0.28716 | 0 | 0 | 0 | 0
2021-10-27 05:15 | 3.4506 | 0.60393 | 0.29504 | 0.29956 | 0 | 0 | 0 | 0
2021-10-27 05:30 | 3.4302 | 0.58621 | 0.37875 | 0.29621 | 0 | 0 | 0 | 0
2021-10-27 05:45 | 3.42 | 0.58621 | 0.40836 | 0.29737 | 0 | 0.000454 | 0 | 0
2021-10-27 06:00 | 3.4404 | 0.58621 | 0.42878 | 0.34171 | 0 | 0.000301 | 0 | 0
2021-10-27 06:15 | 3.4608 | 0.58081 | 0.41653 | 0.33427 | 0 | 0.000521 | 0 | 0
2021-10-27 06:30 | 3.4506 | 0.58081 | 0.33485 | 0.34856 | 0 | 0.000806 | 0 | 0
2021-10-27 06:45 | 3.5527 | 0.61581 | 0.29708 | 0.41157 | 0.012168 | 0.032211 | 0.021772 | 0.025392
2021-10-27 07:00 | 0.69829 | 1.1355 | 0.35425 | 0.78113 | 0.034696 | 0.068874 | 0.061476 | 0.070353
2021-10-27 07:15 | 0.40019 | 1.1664 | 0.34506 | 0.69217 | 0.057224 | 0.1087 | 0.10118 | 0.11531
2021-10-27 07:30 | 0.33587 | 0.99555 | 0.37161 | 0.5402 | 0.079752 | 0.15916 | 0.14088 | 0.16027
2021-10-27 07:45 | 0.3226 | 0.7771 | 0.8453 | 0.49732 | 0.11642 | 0.19234 | 0.14221 | 0.1949
2021-10-27 08:00 | 3.226 | 0.8236 | 0.81672 | 0.52387 | 0.16515 | 0.21945 | 0.11189 | 0.22082
2021-10-27 08:15 | 3.4608 | 1.047 | 0.63296 | 0.59795 | 0.21387 | 0.24524 | 0.081568 | 0.24673
2021-10-27 08:30 | 3.9611 | 1.083 | 0.71463 | 0.65541 | 0.2626 | 0.25653 | 0.051246 | 0.27265
2021-10-27 08:45 | 3.8386 | 1.2281 | 0.62887 | 0.98662 | 0.3033 | 0.26806 | 0.039652 | 0.28212
2021-10-27 09:00 | 3.6752 | 1.3083 | 0.48186 | 1.0636 | 0.33715 | 0.27284 | 0.043527 | 0.27992
2021-10-27 09:15 | 3.7467 | 1.3606 | 0.44919 | 1.1387 | 0.37101 | 0.27761 | 0.047401 | 0.27772
2021-10-27 09:30 | 3.7263 | 1.28 | 0.75546 | 1.0966 | 0.40486 | 0.28239 | 0.051276 | 0.27553
2021-10-27 09:45 | 3.5527 | 1.2425 | 0.52678 | 1.0407 | 0.44089 | 0.28436 | 0.054108 | 0.30277
2021-10-27 10:00 | 3.614 | 1.2142 | 0.55128 | 0.98691 | 0.47879 | 0.28544 | 0.056078 | 0.35078
2021-10-27 10:15 | 3.665 | 1.2176 | 0.5962 | 0.95089 | 0.51669 | 0.28744 | 0.058048 | 0.39879
2021-10-27 10:30 | 3.665 | 1.2176 | 0.71463 | 0.92945 | 0.55459 | 0.28654 | 0.060018 | 0.4468
2021-10-27 10:45 | 3.5119 | 1.2176 | 0.77588 | 0.93981 | 0.57573 | 0.28776 | 0.086872 | 0.45807
2021-10-27 11:00 | 2.0724 | 1.4121 | 3.3587 | 1.3056 | 0.58254 | 0.288 | 0.13434 | 0.44374
2021-10-27 11:15 | 1.3476 | 1.2191 | 0.74321 | 1.0858 | 0.58934 | 0.28813 | 0.1818 | 0.4294
2021-10-27 11:30 | 1.3884 | 1.3026 | 0.70646 | 1.2799 | 0.59614 | 0.28863 | 0.22926 | 0.41507
2021-10-27 11:45 | 0.91881 | 1.4048 | 0.56354 | 1.272 | 0.5993 | 0.29645 | 0.27363 | 0.41197
2021-10-27 12:00 | 0.6207 | 1.233 | 0.53903 | 0.97714 | 0.59932 | 0.29619 | 0.31544 | 0.41665
2021-10-27 12:15 | 0.67379 | 1.2796 | 0.52678 | 0.99721 | 0.59935 | 0.29593 | 0.35725 | 0.42133
2021-10-27 12:30 | 0.66562 | 1.5358 | 3.0933 | 1.4468 | 0.59938 | 0.283 | 0.39906 | 0.426
2021-10-27 12:45 | 0.73913 | 1.2471 | 1.5518 | 1.1854 | 0.5956 | 0.29442 | 0.40715 | 0.41637
2021-10-27 13:00 | 1.0413 | 1.3122 | 0.55945 | 1.3132 | 0.58855 | 0.29239 | 0.38724 | 0.3956
2021-10-27 13:15 | 1.5518 | 1.2505 | 0.8208 | 0.97539 | 0.5815 | 0.29597 | 0.36733 | 0.37483
2021-10-27 13:30 | 1.0719 | 1.2558 | 0.41244 | 0.95804 | 0.57446 | 0.2939 | 0.34742 | 0.35405
2021-10-27 13:45 | 0.69013 | 1.2913 | 0.37875 | 0.86674 | 0.56934 | 0.29129 | 0.3257 | 0.34697
2021-10-27 14:00 | 0.81672 | 1.2793 | 0.38692 | 0.88964 | 0.56587 | 0.28827 | 0.30248 | 0.35044
2021-10-27 14:15 | 0.71463 | 1.2676 | 0.42878 | 0.86849 | 0.56241 | 0.28245 | 0.27926 | 0.35391
2021-10-27 14:30 | 0.67379 | 1.2535 | 0.50636 | 0.84326 | 0.55894 | 0.27946 | 0.25604 | 0.35738
2021-10-27 14:45 | 0.5227 | 1.2323 | 0.59212 | 1.2032 | 0.53521 | 0.25991 | 0.24694 | 0.34772
2021-10-27 15:00 | 0.50636 | 1.2247 | 0.58804 | 1.0288 | 0.49403 | 0.24963 | 0.24959 | 0.32815
2021-10-27 15:15 | 0.44511 | 1.27 | 0.51045 | 1.1444 | 0.45285 | 0.24124 | 0.25225 | 0.30857
2021-10-27 15:30 | 0.39407 | 1.2017 | 0.47778 | 1.1148 | 0.41167 | 0.23286 | 0.2549 | 0.289
2021-10-27 15:45 | 0.46553 | 1.1552 | 0.42469 | 0.94783 | 0.33989 | 0.20708 | 0.2212 | 0.2428
2021-10-27 16:00 | 0.5717 | 1.2432 | 0.47778 | 0.86543 | 0.24175 | 0.17573 | 0.15718 | 0.17537
2021-10-27 16:15 | 0.62479 | 1.298 | 0.45736 | 0.75371 | 0.14361 | 0.13888 | 0.093157 | 0.10793
2021-10-27 16:30 | 0.64521 | 1.1792 | 0.5227 | 0.66898 | 0.045469 | 0.087807 | 0.029135 | 0.040495
2021-10-27 16:45 | 0.53495 | 1.4122 | 0.73913 | 0.69917 | 0 | 0.053202 | 0 | 0.009324
2021-10-27 17:00 | 0.57578 | 1.5167 | 0.71871 | 0.71069 | 0 | 0.032075 | 0 | 0.006603
2021-10-27 17:15 | 0.51045 | 1.5371 | 0.72279 | 0.62377 | 0 | 0.019454 | 0 | 0.003883
2021-10-27 17:30 | 0.55537 | 1.1429 | 0.64521 | 0.51103 | 0 | 0.002763 | 0 | 0.001162
2021-10-27 17:45 | 0.69013 | 1.3585 | 0.61662 | 0.58089 | 0 | 0 | 0 | 0
2021-10-27 18:00 | 0.68196 | 1.3999 | 0.64521 | 0.87214 | 0 | 0 | 0 | 0
2021-10-27 18:15 | 0.61254 | 1.3241 | 0.70238 | 0.86032 | 0 | 0 | 0 | 0
2021-10-27 18:30 | 0.60845 | 1.4606 | 0.71054 | 1.2378 | 0 | 0 | 0 | 0
2021-10-27 18:45 | 0.65746 | 1.7657 | 3.7875 | 1.8671 | 0 | 0 | 0 | 0
2021-10-27 19:00 | 0.64929 | 1.3841 | 3.9611 | 1.6559 | 0 | 0 | 0 | 0
2021-10-27 19:15 | 0.66562 | 1.4185 | 3.9407 | 1.5388 | 0 | 0 | 0 | 0
2021-10-27 19:30 | 0.80038 | 1.3194 | 3.8896 | 1.4193 | 0 | 0 | 0 | 0
2021-10-27 19:45 | 1.9499 | 1.9423 | 4.7146 | 1.8554 | 0 | 0 | 0 | 0
2021-10-27 20:00 | 2.1847 | 1.2063 | 1.2047 | 1.1545 | 0 | 0 | 0 | 0
2021-10-27 20:15 | 1.5211 | 1.1988 | 1.0046 | 1.0323 | 0 | 0 | 0 | 0
2021-10-27 20:30 | 0.56762 | 1.208 | 0.69829 | 1.3638 | 0 | 0 | 0 | 0
2021-10-27 20:45 | 0.54312 | 1.4674 | 0.57578 | 1.3765 | 0 | 0 | 0 | 0
2021-10-27 21:00 | 0.65746 | 1.0925 | 0.62479 | 0.7823 | 0 | 0 | 0 | 0
2021-10-27 21:15 | 3.2669 | 1.0206 | 0.63704 | 0.70908 | 0 | 0 | 0 | 0
2021-10-27 21:30 | 0.7963 | 0.96296 | 0.60845 | 0.72075 | 0 | 0 | 0 | 0
2021-10-27 21:45 | 0.55945 | 0.70158 | 0.56762 | 0.49484 | 0 | 0 | 0 | 0
2021-10-27 22:00 | 0.53087 | 1.2001 | 0.60029 | 1.231 | 0 | 0 | 0 | 0
2021-10-27 22:15 | 0.51453 | 1.2043 | 0.44919 | 1.2588 | 0 | 0 | 0 | 0
2021-10-27 22:30 | 0.53087 | 1.0671 | 0.44511 | 0.83524 | 0 | 0 | 0 | 0
2021-10-27 22:45 | 2.4501 | 1.0205 | 0.42878 | 0.85216 | 0 | 0 | 0 | 0
2021-10-27 23:00 | 3.9611 | 1.1021 | 3.3383 | 1.2572 | 0 | 0 | 0 | 0
2021-10-27 23:15 | 0.88614 | 1.1021 | 3.5425 | 1.2582 | 0 | 0 | 0 | 0
2021-10-27 23:30 | 0.77997 | 1.1007 | 3.5425 | 1.2051 | 0 | 0 | 0 | 0
2021-10-27 23:45 | 0.40019 | 1.0721 | 3.4302 | 1.1923 | 0 | 0 | 0 | 0
2021-10-28 | 0.31648 | 0.95904 | 3.42 | 1.2006 | 0 | 0 | 0 | 0
2021-10-28 00:15 | 0.32873 | 1.0356 | 3.42 | 1.2453 | 0 | 0 | 0 | 0
2021-10-28 00:30 | 0.35731 | 0.99201 | 3.4813 | 1.235 | 0 | 0 | 0 | 0
2021-10-28 00:45 | 0.30627 | 1.0356 | 3.5833 | 1.2408 | 0 | 0 | 0 | 0
2021-10-28 01:00 | 0.31852 | 0.96474 | 3.614 | 1.2179 | 0 | 0 | 0 | 0
2021-10-28 01:15 | 0.40836 | 0.96474 | 3.5017 | 1.2039 | 0 | 0 | 0 | 0
2021-10-28 01:30 | 0.29708 | 0.95304 | 3.471 | 1.2136 | 0 | 0 | 0 | 0
2021-10-28 01:45 | 0.28993 | 0.96474 | 3.4813 | 1.1963 | 0 | 0 | 0 | 0
2021-10-28 02:00 | 0.36344 | 0.93077 | 3.4506 | 1.1837 | 0 | 0 | 0 | 0
2021-10-28 02:15 | 0.32873 | 0.92507 | 3.4915 | 1.199 | 0 | 0 | 0 | 0
2021-10-28 02:30 | 0.29912 | 1.1028 | 3.5731 | 1.2939 | 0 | 0 | 0 | 0
2021-10-28 02:45 | 0.36752 | 0.93129 | 3.5629 | 1.2134 | 0 | 0 | 0 | 0
2021-10-28 03:00 | 0.36446 | 0.89311 | 3.4813 | 0.9522 | 0 | 0 | 0 | 0
2021-10-28 03:15 | 0.29606 | 0.89311 | 3.471 | 0.83363 | 0 | 0 | 0 | 0
2021-10-28 03:30 | 0.29606 | 0.88517 | 3.4506 | 0.78434 | 0 | 0 | 0 | 0
2021-10-28 03:45 | 0.40223 | 0.88517 | 3.4404 | 0.76086 | 0 | 0 | 0 | 0
2021-10-28 04:00 | 0.37977 | 0.93618 | 3.4404 | 0.73796 | 0 | 0 | 0 | 0
2021-10-28 04:15 | 0.31341 | 0.93695 | 3.4506 | 0.7403 | 0 | 0 | 0 | 0
2021-10-28 04:30 | 0.31035 | 0.87502 | 3.5323 | 0.76888 | 0 | 0 | 0 | 0
2021-10-28 04:45 | 0.41653 | 0.92604 | 3.5527 | 0.76509 | 0 | 0 | 0 | 0
2021-10-28 05:00 | 0.41244 | 0.95467 | 3.5527 | 0.75619 | 0 | 0 | 0 | 0
2021-10-28 05:15 | 0.54312 | 0.85546 | 3.4506 | 0.75721 | 0 | 0 | 0 | 0
2021-10-28 05:30 | 0.61662 | 0.86993 | 3.4302 | 0.7505 | 0 | 0 | 0 | 0
2021-10-28 05:45 | 0.31444 | 0.89857 | 3.42 | 0.73665 | 0 | 0 | 0 | 0
2021-10-28 06:00 | 0.30116 | 0.84367 | 3.4404 | 0.78886 | 0 | 0 | 0 | 0
2021-10-28 06:15 | 0.41244 | 0.87642 | 3.4608 | 0.79149 | 0 | 0 | 0 | 0
2021-10-28 06:30 | 0.43286 | 0.85759 | 3.4506 | 0.79805 | 0 | 0 | 0 | 0
2021-10-28 06:45 | 0.43694 | 0.9352 | 3.5527 | 0.8663 | 0.039266 | 0.022648 | 0.012168 | 0.026958
2021-10-28 07:00 | 0.46961 | 0.98413 | 0.69829 | 0.74613 | 0.11309 | 0.0695 | 0.034696 | 0.074849
2021-10-28 07:15 | 0.31137 | 0.92185 | 0.40019 | 0.58599 | 0.18691 | 0.12115 | 0.057224 | 0.12274
2021-10-28 07:30 | 0.33996 | 0.74935 | 0.33587 | 0.51468 | 0.26073 | 0.18131 | 0.079752 | 0.17063
2021-10-28 07:45 | 0.3665 | 0.71278 | 0.3226 | 0.49966 | 0.32226 | 0.20774 | 0.11642 | 0.2078
2021-10-28 08:00 | 0.69421 | 1.0092 | 3.226 | 0.92114 | 0.37296 | 0.23825 | 0.16515 | 0.23636
2021-10-28 08:15 | 0.76771 | 1.1321 | 3.4608 | 0.98852 | 0.42366 | 0.249 | 0.21387 | 0.26493
2021-10-28 08:30 | 0.5962 | 1.0366 | 3.9611 | 1.1157 | 0.47435 | 0.2455 | 0.2626 | 0.29349
2021-10-28 08:45 | 0.37467 | 1.1799 | 3.8386 | 1.4364 | 0.48939 | 0.23371 | 0.3033 | 0.30899
2021-10-28 09:00 | 0.51045 | 1.2389 | 3.6752 | 1.4772 | 0.47296 | 0.23787 | 0.33715 | 0.31491
2021-10-28 09:15 | 0.48595 | 1.2278 | 3.7467 | 1.4742 | 0.45654 | 0.26569 | 0.37101 | 0.32083
2021-10-28 09:30 | 0.56354 | 1.2605 | 3.7263 | 1.5449 | 0.44011 | 0.27025 | 0.40486 | 0.32675
2021-10-28 09:45 | 0.27768 | 1.1272 | 3.5527 | 1.4578 | 0.46047 | 0.27594 | 0.44089 | 0.35563
2021-10-28 10:00 | 0.34098 | 1.0885 | 3.614 | 1.452 | 0.51333 | 0.27558 | 0.47879 | 0.40094
2021-10-28 10:15 | 0.37773 | 1.0311 | 3.665 | 1.3916 | 0.5662 | 0.29383 | 0.51669 | 0.44625
2021-10-28 10:30 | 0.41653 | 1.0771 | 3.665 | 1.376 | 0.61907 | 0.29549 | 0.55459 | 0.49157
2021-10-28 10:45 | 0.41244 | 1.0771 | 3.5119 | 1.3674 | 0.64518 | 0.2995 | 0.57573 | 0.50611
2021-10-28 11:00 | 0.34915 | 1.0771 | 2.0724 | 1.5334 | 0.64762 | 0.32167 | 0.58254 | 0.49865
2021-10-28 11:15 | 0.34098 | 1.0784 | 1.3476 | 1.2229 | 0.65006 | 0.32181 | 0.58934 | 0.49119
2021-10-28 11:30 | 0.37365 | 1.0887 | 1.3884 | 1.4217 | 0.6525 | 0.32559 | 0.59614 | 0.48373
2021-10-28 11:45 | 0.31239 | 1.0935 | 0.91881 | 1.3403 | 0.65247 | 0.33441 | 0.5993 | 0.48512
2021-10-28 12:00 | 0.38488 | 0.94098 | 0.6207 | 1.0051 | 0.65026 | 0.33412 | 0.59932 | 0.49256
2021-10-28 12:15 | 0.5472 | 0.87949 | 0.67379 | 1.0235 | 0.64806 | 0.33383 | 0.59935 | 0.50001
2021-10-28 12:30 | 0.46144 | 1.0676 | 0.66562 | 1.3289 | 0.64585 | 0.33354 | 0.59938 | 0.50745
2021-10-28 12:45 | 0.34302 | 0.92801 | 0.73913 | 1.1778 | 0.64124 | 0.33213 | 0.5956 | 0.49382
2021-10-28 13:00 | 0.43694 | 0.92604 | 1.0413 | 1.4001 | 0.6345 | 0.33124 | 0.58855 | 0.46433
2021-10-28 13:15 | 0.42469 | 0.92801 | 1.5518 | 1.1282 | 0.62776 | 0.33332 | 0.5815 | 0.43485
2021-10-28 13:30 | 0.72279 | 0.96428 | 1.0719 | 1.0371 | 0.62102 | 0.33368 | 0.57446 | 0.40537
2021-10-28 13:45 | 0.47778 | 1.018 | 0.69013 | 0.90291 | 0.62165 | 0.33072 | 0.56934 | 0.39882
2021-10-28 14:00 | 0.49411 | 1.013 | 0.81672 | 0.94273 | 0.62884 | 0.32729 | 0.56587 | 0.40916
2021-10-28 14:15 | 0.60029 | 1.013 | 0.71463 | 0.90816 | 0.63602 | 0.32386 | 0.56241 | 0.4195
2021-10-28 14:30 | 0.45736 | 1.0059 | 0.67379 | 0.87418 | 0.6432 | 0.31785 | 0.55894 | 0.42984
2021-10-28 14:45 | 0.42469 | 1.0095 | 0.5227 | 1.2149 | 0.62292 | 0.31124 | 0.53521 | 0.41988
2021-10-28 15:00 | 0.34098 | 0.967 | 0.50636 | 1.027 | 0.5782 | 0.29634 | 0.49403 | 0.39461
2021-10-28 15:15 | 0.48186 | 1.0082 | 0.44511 | 1.1263 | 0.53348 | 0.28639 | 0.45285 | 0.36934
2021-10-28 15:30 | 0.51045 | 0.95757 | 0.39407 | 1.0964 | 0.48876 | 0.2661 | 0.41167 | 0.34408
2021-10-28 15:45 | 0.5472 | 0.94841 | 0.46553 | 0.94783 | 0.40586 | 0.22767 | 0.33989 | 0.28822
2021-10-28 16:00 | 0.4737 | 0.99997 | 0.5717 | 0.87593 | 0.28895 | 0.1914 | 0.24175 | 0.20763
2021-10-28 16:15 | 0.46144 | 0.99411 | 0.62479 | 0.78055 | 0.17204 | 0.13729 | 0.14361 | 0.12705
2021-10-28 16:30 | 0.4737 | 1.0227 | 0.64521 | 0.70719 | 0.055126 | 0.085005 | 0.045469 | 0.046461
2021-10-28 16:45 | 0.55945 | 0.96878 | 0.53495 | 0.70792 | 0 | 0.023336 | 0 | 0.009173
2021-10-28 17:00 | 0.55128 | 0.96594 | 0.57578 | 0.69844 | 0 | 0.015699 | 0 | 0.006497
2021-10-28 17:15 | 0.53087 | 0.97849 | 0.51045 | 0.61968 | 0 | 0.008588 | 0 | 0.003821
2021-10-28 17:30 | 0.71871 | 1.0192 | 0.55537 | 0.54078 | 0 | 0.00171 | 0 | 0.001144
2021-10-28 17:45 | 0.72279 | 0.97849 | 0.69013 | 0.61706 | 0 | 0 | 0 | 0
2021-10-28 18:00 | 0.75138 | 1.0134 | 0.68196 | 0.57141 | 0 | 0 | 0 | 0
2021-10-28 18:15 | 0.72688 | 0.98564 | 0.61254 | 0.52051 | 0 | 0 | 0 | 0
2021-10-28 18:30 | 1.1944 | 0.97303 | 0.60845 | 0.84341 | 0 | 0 | 0 | 0
2021-10-28 18:45 | 1.3272 | 1.2493 | 0.65746 | 1.4826 | 0 | 0 | 0 | 0
2021-10-28 19:00 | 1.368 | 1.1486 | 0.64929 | 1.5853 | 0 | 0 | 0 | 0
2021-10-28 19:15 | 1.368 | 1.1475 | 0.66562 | 1.5294 | 0 | 0 | 0 | 0
2021-10-28 19:30 | 1.2251 | 1.1322 | 0.80038 | 1.3733 | 0 | 0 | 0 | 0
2021-10-28 19:45 | 1.1026 | 1.1475 | 1.9499 | 1.6935 | 0 | 0 | 0 | 0
2021-10-28 20:00 | 0.94331 | 0.93963 | 2.1847 | 1.1034 | 0 | 0 | 0 | 0
2021-10-28 20:15 | 0.86572 | 0.91781 | 1.5211 | 0.96518 | 0 | 0 | 0 | 0
2021-10-28 20:30 | 2.0622 | 1.1064 | 0.56762 | 1.2771 | 0 | 0 | 0 | 0
2021-10-28 20:45 | 1.2251 | 0.91943 | 0.54312 | 0.99173 | 0 | 0 | 0 | 0
2021-10-28 21:00 | 2.6339 | 0.88491 | 0.65746 | 0.76596 | 0 | 0 | 0 | 0
2021-10-28 21:15 | 2.491 | 0.95363 | 3.2669 | 1.1046 | 0 | 0 | 0 | 0
2021-10-28 21:30 | 2.0622 | 0.89198 | 0.7963 | 0.74875 | 0 | 0 | 0 | 0
2021-10-28 21:45 | 2.103 | 0.7829 | 0.55945 | 0.49426 | 0 | 0 | 0 | 0
2021-10-28 22:00 | 0.98414 | 0.97502 | 0.53087 | 1.2275 | 0 | 0 | 0 | 0
2021-10-28 22:15 | 0.81263 | 1.0678 | 0.51453 | 1.2506 | 0 | 0 | 0 | 0
2021-10-28 22:30 | 0.97189 | 0.90209 | 0.53087 | 0.84749 | 0 | 0 | 0 | 0
2021-10-28 22:45 | 0.66971 | 0.93622 | 2.4501 | 1.1443 | 0 | 0 | 0 | 0
2021-10-28 23:00 | 0.51045 | 1.2282 | 3.9611 | 1.772 | 0 | 0 | 0 | 0
2021-10-28 23:15 | 0.44103 | 1.2036 | 0.88614 | 1.3471 | 0 | 0 | 0 | 0
2021-10-28 23:30 | 0.44919 | 1.2036 | 0.77997 | 1.2831 | 0 | 0 | 0 | 0
2021-10-28 23:45 | 0.31444 | 1.0059 | 0.40019 | 1.2159 | 0 | 0 | 0 | 0
2021-10-29 | 0.30831 | 0.62936 | 0.31648 | 1.2087 | 0 | 0 | 0 | 0
2021-10-29 00:15 | 0.32975 | 0.73088 | 0.32873 | 1.2389 | 0 | 0 | 0 | 0
2021-10-29 00:30 | 0.36548 | 0.67266 | 0.35731 | 1.2334 | 0 | 0 | 0 | 0
2021-10-29 00:45 | 0.42061 | 0.67266 | 0.30627 | 1.2325 | 0 | 0 | 0 | 0
2021-10-29 01:00 | 0.45736 | 0.68235 | 0.31852 | 1.2243 | 0 | 0 | 0 | 0
2021-10-29 01:15 | 0.35425 | 0.62936 | 0.40836 | 1.2265 | 0 | 0 | 0 | 0
2021-10-29 01:30 | 0.31035 | 0.62936 | 0.29708 | 1.2207 | 0 | 0 | 0 | 0
2021-10-29 01:45 | 0.33894 | 0.62936 | 0.28993 | 1.2028 | 0 | 0 | 0 | 0
2021-10-29 02:00 | 0.32669 | 0.63006 | 0.36344 | 1.1972 | 0 | 0 | 0 | 0
2021-10-29 02:15 | 0.31546 | 0.63006 | 0.32873 | 1.2105 | 0 | 0 | 0 | 0
2021-10-29 02:30 | 0.30729 | 0.94678 | 0.29912 | 1.2888 | 0 | 0 | 0 | 0
2021-10-29 02:45 | 0.42061 | 0.73378 | 0.36752 | 1.2134 | 0 | 0 | 0 | 0
2021-10-29 03:00 | 0.45328 | 0.56002 | 0.36446 | 0.9541 | 0 | 0 | 0 | 0
2021-10-29 03:15 | 0.3859 | 0.56002 | 0.29606 | 0.84064 | 0 | 0 | 0 | 0
2021-10-29 03:30 | 0.35935 | 0.56002 | 0.29606 | 0.78974 | 0 | 0 | 0 | 0
2021-10-29 03:45 | 0.30831 | 0.56002 | 0.40223 | 0.78128 | 0 | 0 | 0 | 0
2021-10-29 04:00 | 0.30729 | 0.56002 | 0.37977 | 0.75575 | 0 | 0 | 0 | 0
2021-10-29 04:15 | 0.32873 | 0.56914 | 0.31341 | 0.74773 | 0 | 0 | 0 | 0
2021-10-29 04:30 | 0.35935 | 0.58686 | 0.31035 | 0.7648 | 0 | 0 | 0 | 0
2021-10-29 04:45 | 0.43694 | 0.58686 | 0.41653 | 0.77267 | 0 | 0 | 0 | 0
2021-10-29 05:00 | 0.41653 | 0.58686 | 0.41244 | 0.77661 | 0 | 0 | 0 | 0
2021-10-29 05:15 | 0.32873 | 0.61436 | 0.54312 | 0.80053 | 0 | 0 | 0 | 0
2021-10-29 05:30 | 0.35935 | 0.56056 | 0.61662 | 0.80301 | 0 | 0 | 0 | 0
2021-10-29 05:45 | 0.33792 | 0.54426 | 0.31444 | 0.74715 | 0 | 0 | 0 | 0
2021-10-29 06:00 | 0.30831 | 0.54426 | 0.30116 | 0.77588 | 0 | 0 | 0 | 0
2021-10-29 06:15 | 0.35935 | 0.60688 | 0.41244 | 0.79644 | 0 | 0 | 0 | 0
2021-10-29 06:30 | 0.44919 | 0.5708 | 0.43286 | 0.80403 | 0 | 0 | 0 | 0
2021-10-29 06:45 | 0.391 | 0.72907 | 0.43694 | 0.84005 | 0.046466 | 0.032412 | 0.039266 | 0.031253
2021-10-29 07:00 | 0.36956 | 0.9712 | 0.46961 | 0.69188 | 0.13519 | 0.10249 | 0.11309 | 0.087458
2021-10-29 07:15 | 0.33587 | 0.81298 | 0.31137 | 0.5383 | 0.22392 | 0.18189 | 0.18691 | 0.14366
2021-10-29 07:30 | 0.35629 | 0.77733 | 0.33996 | 0.4699 | 0.31265 | 0.26381 | 0.26073 | 0.19987
2021-10-29 07:45 | 0.35731 | 0.76624 | 0.3665 | 0.48259 | 0.35985 | 0.30573 | 0.32226 | 0.24203
2021-10-29 08:00 | 0.4982 | 0.92422 | 0.69421 | 0.93514 | 0.36923 | 0.3423 | 0.37296 | 0.27293
2021-10-29 08:15 | 0.68604 | 1.0214 | 0.76771 | 0.99319 | 0.37862 | 0.37684 | 0.42366 | 0.30384
2021-10-29 08:30 | 1.7662 | 1.1159 | 0.5962 | 1.1361 | 0.388 | 0.42145 | 0.47435 | 0.33475
2021-10-29 08:45 | 1.2149 | 1.6415 | 0.37467 | 1.424 | 0.41417 | 0.44041 | 0.48939 | 0.3524
2021-10-29 09:00 | 0.62479 | 1.468 | 0.51045 | 1.4767 | 0.45563 | 0.44825 | 0.47296 | 0.35939
2021-10-29 09:15 | 0.67788 | 1.468 | 0.48595 | 1.4701 | 0.49709 | 0.4561 | 0.45654 | 0.36638
2021-10-29 09:30 | 0.85347 | 1.468 | 0.56354 | 1.5402 | 0.53856 | 0.46394 | 0.44011 | 0.37337
2021-10-29 09:45 | 0.75546 | 1.468 | 0.27768 | 1.4001 | 0.56678 | 0.46719 | 0.46047 | 0.395
2021-10-29 10:00 | 0.77997 | 1.4578 | 0.34098 | 1.4185 | 0.58292 | 0.46896 | 0.51333 | 0.42823
2021-10-29 10:15 | 0.44103 | 1.4578 | 0.37773 | 1.389 | 0.59906 | 0.47033 | 0.5662 | 0.46145
2021-10-29 10:30 | 0.45736 | 1.3867 | 0.41653 | 1.3877 | 0.61519 | 0.47298 | 0.61907 | 0.49468
2021-10-29 10:45 | 0.43694 | 1.3867 | 0.41244 | 1.3768 | 0.62202 | 0.47491 | 0.64518 | 0.50985
2021-10-29 11:00 | 0.39611 | 1.5961 | 0.34915 | 1.5337 | 0.62034 | 0.4767 | 0.64762 | 0.51122
2021-10-29 11:15 | 0.53087 | 1.1306 | 0.34098 | 1.1998 | 0.61866 | 0.46951 | 0.65006 | 0.51258
2021-10-29 11:30 | 0.59212 | 1.0383 | 0.37365 | 1.3928 | 0.61697 | 0.47113 | 0.6525 | 0.51395
2021-10-29 11:45 | 0.79222 | 1.084 | 0.31239 | 1.3207 | 0.61938 | 0.48167 | 0.65247 | 0.51801
2021-10-29 12:00 | 0.51045 | 1.0782 | 0.38488 | 1.0012 | 0.62551 | 0.48125 | 0.65026 | 0.52374
2021-10-29 12:15 | 0.56762 | 1.1043 | 0.5472 | 1.0628 | 0.63165 | 0.48084 | 0.64806 | 0.52947
2021-10-29 12:30 | 0.53495 | 1.4082 | 0.46144 | 1.3619 | 0.63779 | 0.48042 | 0.64585 | 0.5352
2021-10-29 12:45 | 0.62479 | 1.0961 | 0.34302 | 1.1796 | 0.63598 | 0.47838 | 0.64124 | 0.52544
2021-10-29 13:00 | 0.60029 | 1.1357 | 0.43694 | 1.4129 | 0.62688 | 0.47508 | 0.6345 | 0.5037
2021-10-29 13:15 | 0.53903 | 1.0954 | 0.42469 | 1.1538 | 0.61777 | 0.46406 | 0.62776 | 0.48196
2021-10-29 13:30 | 1.1842 | 1.1265 | 0.72279 | 1.1075 | 0.60867 | 0.47073 | 0.62102 | 0.46022
2021-10-29 13:45 | 0.42061 | 1.1002 | 0.47778 | 0.93733 | 0.59307 | 0.46081 | 0.62165 | 0.45814
2021-10-29 14:00 | 0.32771 | 1.1175 | 0.49411 | 0.98123 | 0.5715 | 0.45603 | 0.62884 | 0.47082
2021-10-29 14:15 | 0.50636 | 1.0602 | 0.60029 | 0.9455 | 0.54993 | 0.46181 | 0.63602 | 0.4835
2021-10-29 14:30 | 0.71054 | 1.0602 | 0.45736 | 0.89839 | 0.52836 | 0.45852 | 0.6432 | 0.49619
2021-10-29 14:45 | 0.71871 | 1.1515 | 0.42469 | 1.2435 | 0.51545 | 0.44236 | 0.62292 | 0.48705
2021-10-29 15:00 | 0.68604 | 1.0491 | 0.34098 | 1.0423 | 0.51049 | 0.41221 | 0.5782 | 0.46078
2021-10-29 15:15 | 0.67788 | 1.1716 | 0.48186 | 1.1624 | 0.50554 | 0.39326 | 0.53348 | 0.43452
2021-10-29 15:30 | 0.67379 | 1.1083 | 0.51045 | 1.1265 | 0.50058 | 0.37813 | 0.48876 | 0.40826
2021-10-29 15:45 | 0.63704 | 1.0463 | 0.5472 | 0.98006 | 0.43337 | 0.31914 | 0.40586 | 0.34298
2021-10-29 16:00 | 0.64521 | 1.0539 | 0.4737 | 0.9121 | 0.30883 | 0.26706 | 0.28895 | 0.24602
2021-10-29 16:15 | 0.63704 | 1.0241 | 0.46144 | 0.81438 | 0.18429 | 0.20395 | 0.17204 | 0.14905
2021-10-29 16:30 | 0.64112 | 0.98109 | 0.4737 | 0.74263 | 0.059747 | 0.13265 | 0.055126 | 0.052084
2021-10-29 16:45 | 0.55128 | 1.029 | 0.55945 | 0.74788 | 0 | 0.013588 | 0 | 0.007365
2021-10-29 17:00 | 0.5962 | 0.98109 | 0.55128 | 0.72892 | 0 | 0.008242 | 0 | 0.005218
2021-10-29 17:15 | 0.60029 | 0.98109 | 0.53087 | 0.66417 | 0 | 0.003223 | 0 | 0.003072
2021-10-29 17:30 | 0.58395 | 0.99164 | 0.71871 | 0.61283 | 0 | 0.000876 | 0 | 0.000925
2021-10-29 17:45 | 0.60845 | 0.95795 | 0.72279 | 0.68998 | 0 | 0 | 0 | 0
2021-10-29 18:00 | 0.60845 | 1.0058 | 0.75138 | 0.64025 | 0 | 0 | 0 | 0
2021-10-29 18:15 | 0.62479 | 1.0579 | 0.72688 | 0.57754 | 0 | 0 | 0 | 0
2021-10-29 18:30 | 1.6334 | 1.2445 | 1.1944 | 0.98094 | 0 | 0 | 0 | 0
2021-10-29 18:45 | 0.73504 | 1.4017 | 1.3272 | 1.6369 | 0 | 0 | 0 | 0
2021-10-29 19:00 | 0.91064 | 1.3018 | 1.368 | 1.7492 | 0 | 0 | 0 | 0
2021-10-29 19:15 | 0.78813 | 1.2213 | 1.368 | 1.69 | 0 | 0 | 0 | 0
2021-10-29 19:30 | 0.64521 | 1.0645 | 1.2251 | 1.4966 | 0 | 0 | 0 | 0
2021-10-29 19:45 | 0.81672 | 1.5401 | 1.1026 | 1.8143 | 0 | 0 | 0 | 0
2021-10-29 20:00 | 0.8208 | 1.0371 | 0.94331 | 1.2017 | 0 | 0 | 0 | 0
2021-10-29 20:15 | 0.72279 | 1.0219 | 0.86572 | 1.0547 | 0 | 0 | 0 | 0
2021-10-29 20:30 | 0.76363 | 1.0668 | 2.0622 | 1.5366 | 0 | 0 | 0 | 0
2021-10-29 20:45 | 0.72279 | 1.0141 | 1.2251 | 1.1172 | 0 | 0 | 0 | 0
2021-10-29 21:00 | 0.70238 | 1.0062 | 2.6339 | 1.1055 | 0 | 0 | 0 | 0
2021-10-29 21:15 | 0.5962 | 0.99721 | 2.491 | 1.4246 | 0 | 0 | 0 | 0
2021-10-29 21:30 | 1.3884 | 0.93989 | 2.0622 | 0.99027 | 0 | 0 | 0 | 0
2021-10-29 21:45 | 1.1026 | 0.8363 | 2.103 | 0.74598 | 0 | 0 | 0 | 0
2021-10-29 22:00 | 0.63704 | 1.335 | 0.98414 | 1.319 | 0 | 0 | 0 | 0
2021-10-29 22:15 | 0.40836 | 1.0585 | 0.81263 | 1.3339 | 0 | 0 | 0 | 0
2021-10-29 22:30 | 0.54312 | 0.76279 | 0.97189 | 0.9522 | 0 | 0 | 0 | 0
2021-10-29 22:45 | 0.51045 | 0.8575 | 0.66971 | 1.2054 | 0 | 0 | 0 | 0
2021-10-29 23:00 | 0.55945 | 1.2807 | 0.51045 | 1.8029 | 0 | 0 | 0 | 0
2021-10-29 23:15 | 0.46144 | 0.80772 | 0.44103 | 1.3673 | 0 | 0 | 0 | 0
2021-10-29 23:30 | 0.56762 | 0.80772 | 0.44919 | 1.3167 | 0 | 0 | 0 | 0
2021-10-29 23:45 | 1.7662 | 0.82273 | 0.31444 | 1.2273 | 0 | 0 | 0 | 0
2021-10-30 | 1.613 | 0.579 | 0.30831 | 1.2163 | 0 | 0 | 0 | 0
2021-10-30 00:15 | 0.5472 | 0.67465 | 0.32975 | 1.2386 | 0 | 0 | 0 | 0
2021-10-30 00:30 | 0.72688 | 0.81304 | 0.36548 | 1.2519 | 0 | 0 | 0 | 0
2021-10-30 00:45 | 0.45736 | 0.61071 | 0.42061 | 1.2586 | 0 | 0 | 0 | 0
2021-10-30 01:00 | 0.49003 | 0.61071 | 0.45736 | 1.2558 | 0 | 0 | 0 | 0
2021-10-30 01:15 | 1.419 | 0.62919 | 0.35425 | 1.2348 | 0 | 0 | 0 | 0
2021-10-30 01:30 | 3.0219 | 0.526 | 0.31035 | 1.2192 | 0 | 0 | 0 | 0
2021-10-30 01:45 | 0.37875 | 0.56393 | 0.33894 | 1.2176 | 0 | 0 | 0 | 0
2021-10-30 02:00 | 0.33179 | 0.60342 | 0.32669 | 1.2095 | 0 | 0 | 0 | 0
2021-10-30 02:15 | 0.41244 | 0.64365 | 0.31546 | 1.2232 | 0 | 0 | 0 | 0
2021-10-30 02:30 | 0.39304 | 0.61141 | 0.30729 | 1.2475 | 0 | 0 | 0 | 0
2021-10-30 02:45 | 0.2736 | 0.73859 | 0.42061 | 1.207 | 0 | 0 | 0 | 0
2021-10-30 03:00 | 0.31137 | 0.67713 | 0.45328 | 0.97175 | 0 | 0 | 0 | 0
2021-10-30 03:15 | 0.39304 | 0.6598 | 0.3859 | 0.84632 | 0 | 0 | 0 | 0
2021-10-30 03:30 | 0.31341 | 0.59633 | 0.35935 | 0.79003 | 0 | 0 | 0 | 0
2021-10-30 03:45 | 0.3614 | 0.59633 | 0.30831 | 0.77544 | 0 | 0 | 0 | 0
2021-10-30 04:00 | 0.32158 | 0.59633 | 0.30729 | 0.76582 | 0 | 0 | 0 | 0
2021-10-30 04:15 | 0.342 | 0.56937 | 0.32873 | 0.76319 | 0 | 0 | 0 | 0
2021-10-30 04:30 | 0.37467 | 0.62317 | 0.35935 | 0.76801 | 0 | 0 | 0 | 0
2021-10-30 04:45 | 0.38998 | 0.62317 | 0.43694 | 0.80155 | 0 | 0 | 0 | 0
2021-10-30 05:00 | 0.28891 | 0.62317 | 0.41653 | 0.80534 | 0 | 0 | 0 | 0
2021-10-30 05:15 | 0.28075 | 0.63437 | 0.32873 | 0.79995 | 0 | 0 | 0 | 0
2021-10-30 05:30 | 0.39611 | 0.58057 | 0.35935 | 0.82226 | 0 | 0 | 0 | 0
2021-10-30 05:45 | 0.29606 | 0.64404 | 0.33792 | 0.76655 | 0 | 0 | 0 | 0
2021-10-30 06:00 | 0.36548 | 0.64404 | 0.30831 | 0.77646 | 0 | 0 | 0 | 0
2021-10-30 06:15 | 0.28789 | 0.67813 | 0.35935 | 0.79747 | 0 | 0 | 0 | 0
2021-10-30 06:30 | 0.35935 | 0.63784 | 0.44919 | 0.82634 | 0 | 0 | 0 | 0
2021-10-30 06:45 | 0.34813 | 0.92041 | 0.391 | 0.85653 | 0.003532 | 0.019364 | 0.046466 | 0.035257
2021-10-30 07:00 | 0.32669 | 0.89559 | 0.36956 | 0.63208 | 0.010384 | 0.058535 | 0.13519 | 0.099605
2021-10-30 07:15 | 0.38998 | 0.72236 | 0.33587 | 0.45561 | 0.017236 | 0.098477 | 0.22392 | 0.16395
2021-10-30 07:30 | 0.40836 | 0.7475 | 0.35629 | 0.42338 | 0.024088 | 0.14173 | 0.31265 | 0.2283
2021-10-30 07:45 | 0.30116 | 0.72915 | 0.35731 | 0.45021 | 0.027522 | 0.18302 | 0.35985 | 0.27409
2021-10-30 08:00 | 0.37875 | 1.0618 | 0.4982 | 0.94389 | 0.02774 | 0.18158 | 0.36923 | 0.30425
2021-10-30 08:15 | 0.48595 | 1.0667 | 0.68604 | 1.006 | 0.027957 | 0.18707 | 0.37862 | 0.3344
2021-10-30 08:30 | 0.94739 | 0.96669 | 1.7662 | 1.3167 | 0.028174 | 0.21264 | 0.388 | 0.36456
2021-10-30 08:45 | 0.41653 | 0.96845 | 1.2149 | 1.1702 | 0.029141 | 0.22656 | 0.41417 | 0.38453
2021-10-30 09:00 | 0.54312 | 0.88466 | 0.62479 | 1.0161 | 0.030813 | 0.23675 | 0.45563 | 0.39653
2021-10-30 09:15 | 0.50228 | 0.92756 | 0.67788 | 1.0215 | 0.032486 | 0.24089 | 0.49709 | 0.40852
2021-10-30 09:30 | 0.44103 | 0.93662 | 0.85347 | 1.1138 | 0.034158 | 0.25769 | 0.53856 | 0.42052
2021-10-30 09:45 | 0.51045 | 1.0508 | 0.75546 | 0.98443 | 0.034512 | 0.26866 | 0.56678 | 0.43875
2021-10-30 10:00 | 1.613 | 1.0098 | 0.77997 | 0.99173 | 0.033622 | 0.2782 | 0.58292 | 0.46212
2021-10-30 10:15 | 2.9708 | 1.0204 | 0.44103 | 0.94156 | 0.032732 | 0.29863 | 0.59906 | 0.4855
2021-10-30 10:30 | 1.5313 | 0.92015 | 0.45736 | 0.94841 | 0.031842 | 0.29275 | 0.61519 | 0.50888
2021-10-30 10:45 | 0.5962 | 0.92015 | 0.43694 | 0.92727 | 0.032495 | 0.27452 | 0.62202 | 0.52145
2021-10-30 11:00 | 0.65337 | 0.95918 | 0.39611 | 1.0696 | 0.034604 | 0.27556 | 0.62034 | 0.52524
2021-10-30 11:15 | 0.62887 | 1.1449 | 0.53087 | 0.76523 | 0.036714 | 0.2766 | 0.61866 | 0.52902
2021-10-30 11:30 | 0.55537 | 1.264 | 0.59212 | 0.96985 | 0.038824 | 0.285 | 0.61697 | 0.5328
2021-10-30 11:45 | 0.63704 | 1.0493 | 0.79222 | 0.92056 | 0.039671 | 0.29887 | 0.61938 | 0.53707
2021-10-30 12:00 | 0.57987 | 0.96303 | 0.51045 | 0.56951 | 0.039324 | 0.29861 | 0.62551 | 0.54151
2021-10-30 12:15 | 0.69013 | 0.87664 | 0.56762 | 0.54341 | 0.038977 | 0.29125 | 0.63165 | 0.54596
2021-10-30 12:30 | 0.48186 | 0.88372 | 0.53495 | 0.92202 | 0.038629 | 0.291 | 0.63779 | 0.55041
2021-10-30 12:45 | 0.46144 | 1.1667 | 0.62479 | 0.76421 | 0.039222 | 0.28976 | 0.63598 | 0.54448
2021-10-30 13:00 | 0.53495 | 1.1008 | 0.60029 | 0.98531 | 0.040707 | 0.29478 | 0.62688 | 0.53008
2021-10-30 13:15 | 1.174 | 1.1167 | 0.53903 | 0.74511 | 0.042192 | 0.29273 | 0.61777 | 0.51567
2021-10-30 13:30 | 3.0627 | 0.98382 | 1.1842 | 0.7823 | 0.043677 | 0.29412 | 0.60867 | 0.50127
2021-10-30 13:45 | 1.7253 | 0.93647 | 0.42061 | 0.48405 | 0.042602 | 0.29322 | 0.59307 | 0.49877
2021-10-30 14:00 | 0.90656 | 0.93419 | 0.32771 | 0.52197 | 0.039097 | 0.29301 | 0.5715 | 0.50523
2021-10-30 14:15 | 0.69829 | 0.94596 | 0.50636 | 0.52197 | 0.035592 | 0.29284 | 0.54993 | 0.51168
2021-10-30 14:30 | 0.76363 | 0.962 | 0.71054 | 0.50987 | 0.032088 | 0.2948 | 0.52836 | 0.51814
2021-10-30 14:45 | 0.54312 | 0.93305 | 0.71871 | 0.86484 | 0.050277 | 0.27914 | 0.51545 | 0.511
2021-10-30 15:00 | 0.55128 | 0.88308 | 0.68604 | 0.66198 | 0.089084 | 0.25927 | 0.51049 | 0.49297
2021-10-30 15:15 | 0.4982 | 1.1665 | 0.67788 | 0.77063 | 0.12789 | 0.24735 | 0.50554 | 0.47494
2021-10-30 15:30 | 0.46144 | 1.1225 | 0.67379 | 0.7225 | 0.1667 | 0.23783 | 0.50058 | 0.45691
2021-10-30 15:45 | 0.47778 | 0.98228 | 0.63704 | 0.54603 | 0.16184 | 0.20454 | 0.43337 | 0.38856
2021-10-30 16:00 | 0.56354 | 0.97481 | 0.64521 | 0.58279 | 0.11544 | 0.17299 | 0.30883 | 0.27858
2021-10-30 16:15 | 0.46961 | 0.91428 | 0.63704 | 0.55828 | 0.069043 | 0.14383 | 0.18429 | 0.16859
2021-10-30 16:30 | 0.45736 | 0.95767 | 0.64112 | 0.57754 | 0.022642 | 0.091225 | 0.059747 | 0.058605
2021-10-30 16:45 | 0.55945 | 0.98019 | 0.55128 | 0.5962 | 0 | 0.003122 | 0 | 0.007365
2021-10-30 17:00 | 0.68604 | 0.959 | 0.5962 | 0.57637 | 0 | 0.000879 | 0 | 0.005218
2021-10-30 17:15 | 0.57987 | 0.87672 | 0.60029 | 0.54866 | 0 | 0.001438 | 0 | 0.003072
2021-10-30 17:30 | 0.53087 | 0.90155 | 0.58395 | 0.52999 | 0 | 0.00132 | 0 | 0.000925
2021-10-30 17:45 | 0.51862 | 0.91331 | 0.60845 | 0.52168 | 0 | 0 | 0 | 0
2021-10-30 18:00 | 0.71054 | 0.95256 | 0.60845 | 0.53612 | 0 | 0 | 0 | 0
2021-10-30 18:15 | 0.68196 | 1.1451 | 0.62479 | 0.5857 | 0 | 0 | 0 | 0
2021-10-30 18:30 | 0.58395 | 1.2244 | 1.6334 | 1.032 | 0 | 0 | 0 | 0
2021-10-30 18:45 | 1.7559 | 1.5374 | 0.73504 | 1.5859 | 0 | 0 | 0 | 0
2021-10-30 19:00 | 2.4093 | 1.3142 | 0.91064 | 1.7527 | 0 | 0 | 0 | 0
2021-10-30 19:15 | 2.2766 | 1.2978 | 0.78813 | 1.7099 | 0 | 0 | 0 | 0
2021-10-30 19:30 | 2.4706 | 1.1743 | 0.64521 | 1.5013 | 0 | 0 | 0 | 0
2021-10-30 19:45 | 2.1643 | 1.4423 | 0.81672 | 1.8359 | 0 | 0 | 0 | 0
2021-10-30 20:00 | 1.9601 | 1.0876 | 0.8208 | 1.2321 | 0 | 0 | 0 | 0
2021-10-30 20:15 | 0.67788 | 1.1192 | 0.72279 | 1.0751 | 0 | 0 | 0 | 0
2021-10-30 20:30 | 0.71054 | 1.4092 | 0.76363 | 1.5623 | 0 | 0 | 0 | 0
2021-10-30 20:45 | 0.6207 | 1.1539 | 0.72279 | 1.1382 | 0 | 0 | 0 | 0
2021-10-30 21:00 | 0.8453 | 1.0993 | 0.70238 | 1.1224 | 0 | 0 | 0 | 0
2021-10-30 21:15 | 0.64112 | 1.1129 | 0.5962 | 1.4304 | 0 | 0 | 0 | 0
2021-10-30 21:30 | 0.58395 | 1.1128 | 1.3884 | 1.1157 | 0 | 0 | 0 | 0
2021-10-30 21:45 | 0.64929 | 0.88022 | 1.1026 | 0.84588 | 0 | 0 | 0 | 0
2021-10-30 22:00 | 0.54312 | 1.0136 | 0.63704 | 1.2452 | 0 | 0 | 0 | 0
2021-10-30 22:15 | 0.56354 | 1.0693 | 0.40836 | 1.3076 | 0 | 0 | 0 | 0
2021-10-30 22:30 | 0.49411 | 1.0177 | 0.54312 | 0.97364 | 0 | 0 | 0 | 0
2021-10-30 22:45 | 0.51862 | 1.3533 | 0.51045 | 1.2254 | 0 | 0 | 0 | 0
2021-10-30 23:00 | 0.48595 | 2.086 | 0.55945 | 1.8248 | 0 | 0 | 0 | 0
2021-10-30 23:15 | 0.56354 | 1.3382 | 0.46144 | 1.3788 | 0 | 0 | 0 | 0
2021-10-30 23:30 | 0.57578 | 1.3382 | 0.56762 | 1.3587 | 0 | 0 | 0 | 0
2021-10-30 23:45 | 0.39917 | 0.93934 | 1.7662 | 1.4399 | 0 | 0 | 0 | 0
2021-10-31 | 0.28177 | 1.595 | 1.613 | 1.4056 | 0 | 0 | 0 | 0
2021-10-31 00:15 | 0.26339 | 1.5387 | 0.5472 | 1.2634 | 0 | 0 | 0 | 0
2021-10-31 00:30 | 0.27564 | 1.6455 | 0.72688 | 1.2962 | 0 | 0 | 0 | 0
2021-10-31 00:45 | 0.38692 | 1.717 | 0.45736 | 1.2755 | 0 | 0 | 0 | 0
2021-10-31 01:00 | 0.35527 | 1.717 | 0.49003 | 1.2846 | 0 | 0 | 0 | 0
2021-10-31 01:15 | 0.26645 | 1.6991 | 1.419 | 1.398 | 0 | 0 | 0 | 0
2021-10-31 01:30 | 0.26645 | 1.8198 | 3.0219 | 1.6037 | 0 | 0 | 0 | 0
2021-10-31 01:45 | 0.26748 | 1.6004 | 0.37875 | 1.215 | 0 | 0 | 0 | 0
2021-10-31 02:00 | 0.26135 | 1.5388 | 0.33179 | 1.2099 | 0 | 0 | 0 | 0
2021-10-31 02:15 | 0.36854 | 1.6099 | 0.41244 | 1.2432 | 0 | 0 | 0 | 0
2021-10-31 02:30 | 0.34302 | 1.7374 | 0.39304 | 1.2655 | 0 | 0 | 0 | 0
2021-10-31 02:45 | 0.26645 | 1.1786 | 0.2736 | 1.1956 | 0 | 0 | 0 | 0
2021-10-31 03:00 | 0.26645 | 0.94097 | 0.31137 | 0.96139 | 0 | 0 | 0 | 0
2021-10-31 03:15 | 0.26339 | 0.90254 | 0.39304 | 0.85711 | 0 | 0 | 0 | 0
2021-10-31 03:30 | 0.35731 | 0.56947 | 0.31341 | 0.79717 | 0 | 0 | 0 | 0
2021-10-31 03:45 | 0.30831 | 0.56947 | 0.3614 | 0.78784 | 0 | 0 | 0 | 0
2021-10-31 04:00 | 0.26441 | 0.56947 | 0.32158 | 0.76757 | 0 | 0 | 0 | 0
2021-10-31 04:15 | 0.26441 | 0.54251 | 0.342 | 0.75707 | 0 | 0 | 0 | 0
2021-10-31 04:30 | 0.35935 | 0.66533 | 0.37467 | 0.78419 | 0 | 0 | 0 | 0
2021-10-31 04:45 | 0.42469 | 0.66533 | 0.38998 | 0.82022 | 0 | 0 | 0 | 0
2021-10-31 05:00 | 0.63704 | 0.70326 | 0.28891 | 0.8084 | 0 | 0 | 0 | 0
2021-10-31 05:15 | 0.37365 | 0.64045 | 0.28075 | 0.78463 | 0 | 0 | 0 | 0
2021-10-31 05:30 | 0.29504 | 0.58665 | 0.39611 | 0.82838 | 0 | 0 | 0 | 0
2021-10-31 05:45 | 0.41244 | 0.58665 | 0.29606 | 0.77282 | 0 | 0 | 0 | 0
2021-10-31 06:00 | 0.42061 | 0.58665 | 0.36548 | 0.78697 | 0 | 0 | 0 | 0
2021-10-31 06:15 | 0.41653 | 0.64142 | 0.28789 | 0.79892 | 0 | 0 | 0 | 0
2021-10-31 06:30 | 0.3665 | 0.60535 | 0.35935 | 0.81584 | 0 | 0 | 0 | 0
2021-10-31 06:45 | 0.29708 | 0.65795 | 0.34813 | 0.80826 | 0.016416 | 0.023014 | 0.003532 | 0.030425
2021-10-31 07:00 | 0.33383 | 0.8377 | 0.32669 | 0.51103 | 0.048778 | 0.068294 | 0.010384 | 0.08644
2021-10-31 07:15 | 0.41244 | 0.66165 | 0.38998 | 0.39173 | 0.08114 | 0.099643 | 0.017236 | 0.14245
2021-10-31 07:30 | 0.43694 | 0.68533 | 0.40836 | 0.35163 | 0.1135 | 0.14874 | 0.024088 | 0.19847
2021-10-31 07:45 | 0.31444 | 0.79182 | 0.30116 | 0.41215 | 0.12444 | 0.16654 | 0.027522 | 0.23405
2021-10-31 08:00 | 0.30218 | 0.9352 | 0.37875 | 0.90641 | 0.11453 | 0.17781 | 0.02774 | 0.2525
2021-10-31 08:15 | 0.33281 | 1.1568 | 0.48595 | 0.99202 | 0.10463 | 0.19447 | 0.027957 | 0.27096
2021-10-31 08:30 | 0.4982 | 1.3214 | 0.94739 | 1.3838 | 0.094727 | 0.21584 | 0.028174 | 0.28941
2021-10-31 08:45 | 1.0924 | 1.2338 | 0.41653 | 1.1745 | 0.084508 | 0.21436 | 0.029141 | 0.30347
2021-10-31 09:00 | 0.68196 | 1.2437 | 0.54312 | 1.0401 | 0.073981 | 0.22957 | 0.030813 | 0.3139
2021-10-31 09:15 | 0.48595 | 1.2788 | 0.50228 | 1.0381 | 0.063454 | 0.22837 | 0.032486 | 0.32432
2021-10-31 09:30 | 0.46144 | 1.2804 | 0.44103 | 1.1215 | 0.052928 | 0.23229 | 0.034158 | 0.33475
2021-10-31 09:45 | 0.55128 | 1.2349 | 0.51045 | 0.99931 | 0.064609 | 0.23392 | 0.034512 | 0.35196
2021-10-31 10:00 | 0.92697 | 1.2868 | 1.613 | 1.1481 | 0.097951 | 0.22289 | 0.033622 | 0.37468
2021-10-31 10:15 | 1.8172 | 1.3286 | 2.9708 | 1.2989 | 0.13129 | 0.24581 | 0.032732 | 0.39741
2021-10-31 10:30 | 0.55128 | 1.2027 | 1.5313 | 1.1266 | 0.16464 | 0.26006 | 0.031842 | 0.42013
2021-10-31 10:45 | 0.56762 | 1.166 | 0.5962 | 0.97948 | 0.21634 | 0.28071 | 0.032495 | 0.43955
2021-10-31 11:00 | 2.6339 | 1.1537 | 0.65337 | 1.1293 | 0.28597 | 0.27187 | 0.034604 | 0.45583
2021-10-31 11:15 | 2.2256 | 1.0997 | 0.62887 | 0.67277 | 0.35561 | 0.27289 | 0.036714 | 0.4721
2021-10-31 11:30 | 1.1128 | 1.1415 | 0.55537 | 0.7823 | 0.42524 | 0.27392 | 0.038824 | 0.48838
2021-10-31 11:45 | 1.7151 | 1.2141 | 0.63704 | 0.94914 | 0.43234 | 0.28004 | 0.039671 | 0.4988
2021-10-31 12:00 | 2.8585 | 1.1986 | 0.57987 | 0.5911 | 0.37827 | 0.2798 | 0.039324 | 0.50463
2021-10-31 12:15 | 0.42469 | 1.1418 | 0.69013 | 0.59445 | 0.3242 | 0.27956 | 0.038977 | 0.51045
2021-10-31 12:30 | 0.35119 | 1.2305 | 0.48186 | 0.94943 | 0.27013 | 0.27932 | 0.038629 | 0.51628
2021-10-31 12:45 | 0.5962 | 1.1318 | 0.46144 | 0.70821 | 0.26647 | 0.27813 | 0.039222 | 0.51508
2021-10-31 13:00 | 0.66971 | 1.0997 | 0.53495 | 0.62275 | 0.31218 | 0.27621 | 0.040707 | 0.50794
2021-10-31 13:15 | 0.5717 | 1.1068 | 1.174 | 0.8154 | 0.3579 | 0.27429 | 0.042192 | 0.50079
2021-10-31 13:30 | 0.47778 | 1.1625 | 3.0627 | 1.1699 | 0.40361 | 0.27237 | 0.043677 | 0.49365
2021-10-31 13:45 | 0.66562 | 1.1156 | 1.7253 | 0.69348 | 0.40478 | 0.26996 | 0.042602 | 0.48625
2021-10-31 14:00 | 0.57987 | 1.1262 | 0.90656 | 0.61823 | 0.36227 | 0.26782 | 0.039097 | 0.47859
2021-10-31 14:15 | 0.33383 | 1.1325 | 0.69829 | 0.58862 | 0.31976 | 0.26766 | 0.035592 | 0.47092
2021-10-31 14:30 | 0.33281 | 1.1865 | 0.76363 | 0.5857 | 0.27724 | 0.27068 | 0.032088 | 0.46325
2021-10-31 14:45 | 0.30218 | 1.1218 | 0.54312 | 0.89314 | 0.23342 | 0.26215 | 0.050277 | 0.45118
2021-10-31 15:00 | 0.30218 | 1.1225 | 0.55128 | 0.69654 | 0.18831 | 0.2286 | 0.089084 | 0.43576
2021-10-31 15:15 | 0.36344 | 1.0279 | 0.4982 | 0.50053 | 0.14319 | 0.22083 | 0.12789 | 0.42033
2021-10-31 15:30 | 0.46961 | 1.0108 | 0.46144 | 0.4909 | 0.098079 | 0.21233 | 0.1667 | 0.4049
2021-10-31 15:45 | 0.45736 | 1.041 | 0.47778 | 0.51336 | 0.066168 | 0.17811 | 0.16184 | 0.34437
2021-10-31 16:00 | 0.3471 | 1.0176 | 0.56354 | 0.5752 | 0.047242 | 0.12908 | 0.11544 | 0.24492
2021-10-31 16:15 | 0.34302 | 0.93797 | 0.46961 | 0.54662 | 0.028316 | 0.088375 | 0.069043 | 0.14546
2021-10-31 16:30 | 0.33894 | 1.0384 | 0.45736 | 0.56762 | 0.009391 | 0.05419 | 0.022642 | 0.046006
2021-10-31 16:45 | 0.34915 | 1.0389 | 0.55945 | 0.59445 | 0 | 0.002557 | 0 | 0.000119
2021-10-31 17:00 | 0.43286 | 0.99665 | 0.68604 | 0.59154 | 0 | 0.002308 | 0 | 8.4e-05
2021-10-31 17:15 | 0.42061 | 0.8844 | 0.57987 | 0.54632 | 0 | 0.000532 | 0 | 5e-05
2021-10-31 17:30 | 0.39611 | 0.8844 | 0.53087 | 0.55201 | 0 | 0.000189 | 0 | 1.5e-05
2021-10-31 17:45 | 0.37569 | 0.8844 | 0.51862 | 0.54778 | 0 | 0 | 0 | 0
2021-10-31 18:00 | 0.45736 | 1.0098 | 0.71054 | 0.57812 | 0 | 0 | 0 | 0
2021-10-31 18:15 | 0.45328 | 0.95849 | 0.68196 | 0.5927 | 0 | 0 | 0 | 0
2021-10-31 18:30 | 1.8376 | 1.1269 | 0.58395 | 1.0098 | 0 | 0 | 0 | 0
2021-10-31 18:45 | 3.8998 | 1.3884 | 1.7559 | 1.4838 | 0 | 0 | 0 | 0
2021-10-31 19:00 | 3.91 | 1.5537 | 2.4093 | 1.7994 | 0 | 0 | 0 | 0
2021-10-31 19:15 | 3.8692 | 1.3996 | 2.2766 | 1.7419 | 0 | 0 | 0 | 0
2021-10-31 19:30 | 3.7569 | 1.3996 | 2.4706 | 1.7131 | 0 | 0 | 0 | 0
2021-10-31 19:45 | 4.6528 | 1.5663 | 2.1643 | 1.9788 | 0 | 0 | 0 | 0
2021-10-31 20:00 | 1.7559 | 1.2246 | 1.9601 | 1.4088 | 0 | 0 | 0 | 0
2021-10-31 20:15 | 1.368 | 1.141 | 0.67788 | 1.0728 | 0 | 0 | 0 | 0
2021-10-31 20:30 | 1.0086 | 1.5377 | 0.71054 | 1.3327 | 0 | 0 | 0 | 0
2021-10-31 20:45 | 0.73504 | 1.0322 | 0.6207 | 0.9016 | 0 | 0 | 0 | 0
2021-10-31 21:00 | 0.65746 | 0.88005 | 0.8453 | 0.93981 | 0 | 0 | 0 | 0
2021-10-31 21:15 | 0.51862 | 1.0164 | 0.64112 | 1.2362 | 0 | 0 | 0 | 0
2021-10-31 21:30 | 0.46144 | 0.97183 | 0.58395 | 0.94973 | 0 | 0 | 0 | 0
2021-10-31 21:45 | 0.4982 | 0.79334 | 0.64929 | 0.85697 | 0 | 0 | 0 | 0
2021-10-31 22:00 | 0.50636 | 1.03 | 0.54312 | 0.73475 | 0 | 0 | 0 | 0
2021-10-31 22:15 | 0.49003 | 1.1596 | 0.56354 | 0.89664 | 0 | 0 | 0 | 0
2021-10-31 22:30 | 0.38488 | 0.72035 | 0.49411 | 0.55274 | 0 | 0 | 0 | 0
2021-10-31 22:45 | 0.42878 | 0.80977 | 0.51862 | 0.7963 | 0 | 0 | 0 | 0
2021-10-31 23:00 | 3.2975 | 1.0821 | 0.48595 | 1.3881 | 0 | 0 | 0 | 0
2021-10-31 23:15 | 3.5323 | 0.73626 | 0.56354 | 0.96052 | 0 | 0 | 0 | 0
2021-10-31 23:30 | 3.614 | 0.73626 | 0.57578 | 0.94798 | 0 | 0 | 0 | 0
2021-10-31 23:45 | 3.7569 | 0.6609 | 0.39917 | 1.0025 | 0 | 0 | 0 | 0
2021-11-01 | 3.7059 | 1.0722 | 0.28177 | 0.95147 | 0 | 0 | 0 | 0
2021-11-01 00:15 | 3.6038 | 1.0722 | 0.26339 | 0.80082 | 0 | 0 | 0 | 0
2021-11-01 00:30 | 3.4813 | 1.0722 | 0.27564 | 0.84559 | 0 | 0 | 0 | 0
2021-11-01 00:45 | 3.4098 | 1.0231 | 0.38692 | 0.84661 | 0 | 0 | 0 | 0
2021-11-01 01:00 | 3.4404 | 1.081 | 0.35527 | 0.85405 | 0 | 0 | 0 | 0
2021-11-01 01:15 | 3.4608 | 1.0722 | 0.26645 | 0.94608 | 0 | 0 | 0 | 0
2021-11-01 01:30 | 3.5221 | 1.0963 | 0.26645 | 1.1415 | 0 | 0 | 0 | 0
2021-11-01 01:45 | 3.5833 | 1.0722 | 0.26748 | 0.76757 | 0 | 0 | 0 | 0
2021-11-01 02:00 | 3.5323 | 1.0234 | 0.26135 | 0.76305 | 0 | 0 | 0 | 0
2021-11-01 02:15 | 3.471 | 0.96548 | 0.36854 | 0.8087 | 0 | 0 | 0 | 0
2021-11-01 02:30 | 3.4608 | 1.0234 | 0.34302 | 0.82591 | 0 | 0 | 0 | 0
2021-11-01 02:45 | 3.4813 | 1.0234 | 0.26645 | 0.80782 | 0 | 0 | 0 | 0
2021-11-01 03:00 | 3.4813 | 1.0234 | 0.26645 | 0.80403 | 0 | 0 | 0 | 0
2021-11-01 03:15 | 3.614 | 0.94523 | 0.26339 | 0.79615 | 0 | 0 | 0 | 0
2021-11-01 03:30 | 3.5936 | 0.90006 | 0.35731 | 0.79309 | 0 | 0 | 0 | 0
2021-11-01 03:45 | 3.5119 | 0.89122 | 0.30831 | 0.77617 | 0 | 0 | 0 | 0
2021-11-01 04:00 | 3.5323 | 0.89122 | 0.26441 | 0.75692 | 0 | 0 | 0 | 0
2021-11-01 04:15 | 3.5323 | 0.8165 | 0.26441 | 0.75619 | 0 | 0 | 0 | 0
2021-11-01 04:30 | 3.5119 | 0.80141 | 0.35935 | 0.79659 | 0 | 0 | 0 | 0
2021-11-01 04:45 | 3.5731 | 0.80141 | 0.42469 | 0.83932 | 0 | 0 | 0 | 0
2021-11-01 05:00 | 3.8488 | 0.77084 | 0.63704 | 0.84224 | 0 | 0 | 0 | 0
2021-11-01 05:15 | 3.7263 | 0.80548 | 0.37365 | 0.7944 | 0 | 0 | 0 | 0
2021-11-01 05:30 | 3.5119 | 0.83695 | 0.29504 | 0.83086 | 0 | 0 | 0 | 0
2021-11-01 05:45 | 3.614 | 0.82056 | 0.41244 | 0.79178 | 0 | 0 | 0 | 0
2021-11-01 06:00 | 3.6242 | 0.82056 | 0.42061 | 0.79426 | 0 | 0 | 0 | 0
2021-11-01 06:15 | 3.6344 | 0.80008 | 0.41653 | 0.80738 | 0 | 0 | 0 | 0
2021-11-01 06:30 | 3.5629 | 0.81517 | 0.3665 | 0.82182 | 0 | 0 | 0 | 0
2021-11-01 06:45 | 3.4506 | 0.80008 | 0.29708 | 0.81074 | 0.057251 | 0.01639 | 0.016416 | 0.02828
2021-11-01 07:00 | 0.56762 | 0.68679 | 0.33383 | 0.40413 | 0.17198 | 0.046852 | 0.048778 | 0.080968
2021-11-01 07:15 | 0.48186 | 0.73973 | 0.41244 | 0.35498 | 0.2867 | 0.080185 | 0.08114 | 0.13366
2021-11-01 07:30 | 0.53495 | 0.93258 | 0.43694 | 0.37088 | 0.40143 | 0.11441 | 0.1135 | 0.18635
2021-11-01 07:45 | 0.37671 | 0.82152 | 0.31444 | 0.41536 | 0.44993 | 0.15602 | 0.12444 | 0.2196
2021-11-01 08:00 | 3.2873 | 1.2736 | 0.30218 | 0.89562 | 0.43187 | 0.19066 | 0.11453 | 0.2359
2021-11-01 08:15 | 2.491 | 1.243 | 0.33281 | 0.97539 | 0.41381 | 0.20828 | 0.10463 | 0.25219
2021-11-01 08:30 | 1.2149 | 1.4051 | 0.4982 | 1.3768 | 0.39575 | 0.22008 | 0.094727 | 0.26848
2021-11-01 08:45 | 1.2251 | 1.3798 | 1.0924 | 1.1899 | 0.34541 | 0.22066 | 0.084508 | 0.28094
2021-11-01 09:00 | 1.4395 | 1.3238 | 0.68196 | 1.0501 | 0.26258 | 0.22232 | 0.073981 | 0.29018
2021-11-01 09:15 | 0.66154 | 1.3162 | 0.48595 | 1.0422 | 0.17975 | 0.22245 | 0.063454 | 0.29942
2021-11-01 09:30 | 0.53087 | 1.2973 | 0.46144 | 1.1169 | 0.096921 | 0.2263 | 0.052928 | 0.30867
2021-11-01 09:45 | 0.55128 | 1.2872 | 0.55128 | 1.0098 | 0.081158 | 0.22789 | 0.064609 | 0.32352
2021-11-01 10:00 | 0.77997 | 1.398 | 0.92697 | 1.2341 | 0.133 | 0.23262 | 0.097951 | 0.34363
2021-11-01 10:15 | 0.86164 | 1.5245 | 1.8172 | 1.5211 | 0.18484 | 0.23406 | 0.13129 | 0.36373
2021-11-01 10:30 | 0.76771 | 1.3073 | 0.55128 | 1.1682 | 0.23669 | 0.24025 | 0.16464 | 0.38383
2021-11-01 10:45 | 1.3067 | 1.2783 | 0.56762 | 1.0151 | 0.23509 | 0.23736 | 0.21634 | 0.40286
2021-11-01 11:00 | 2.981 | 1.4994 | 2.6339 | 1.4628 | 0.17957 | 0.23828 | 0.28597 | 0.42101
2021-11-01 11:15 | 1.3476 | 1.3465 | 2.2256 | 0.9436 | 0.12403 | 0.18466 | 0.35561 | 0.43916
2021-11-01 11:30 | 0.55945 | 1.3806 | 1.1128 | 0.77938 | 0.068504 | 0.18535 | 0.42524 | 0.45731
2021-11-01 11:45 | 0.67788 | 1.3724 | 1.7151 | 1.0716 | 0.069521 | 0.18949 | 0.43234 | 0.46527
2021-11-01 12:00 | 0.5472 | 1.3401 | 2.8585 | 0.87987 | 0.1277 | 0.18933 | 0.37827 | 0.46345
2021-11-01 12:15 | 0.56354 | 1.3947 | 0.42469 | 0.58337 | 0.18587 | 0.18917 | 0.3242 | 0.46163
2021-11-01 12:30 | 0.86572 | 1.435 | 0.35119 | 0.90218 | 0.24405 | 0.189 | 0.27013 | 0.45982
2021-11-01 12:45 | 0.57987 | 1.3425 | 0.5962 | 0.73504 | 0.32132 | 0.1882 | 0.26647 | 0.45849
2021-11-01 13:00 | 0.89431 | 1.3021 | 0.66971 | 0.66271 | 0.41793 | 0.1869 | 0.31218 | 0.45854
2021-11-01 13:15 | 0.73913 | 1.3211 | 0.5717 | 0.85201 | 0.51453 | 0.1856 | 0.3579 | 0.45858
2021-11-01 13:30 | 0.49003 | 1.2679 | 0.47778 | 1.1988 | 0.61114 | 0.1843 | 0.40361 | 0.45863
2021-11-01 13:45 | 0.41653 | 1.2506 | 0.66562 | 0.74336 | 0.62158 | 0.18267 | 0.40478 | 0.45221
2021-11-01 14:00 | 0.38386 | 1.3046 | 0.57987 | 0.64346 | 0.54469 | 0.19844 | 0.36227 | 0.43943
2021-11-01 14:15 | 0.40427 | 1.2822 | 0.33383 | 0.56981 | 0.4678 | 0.19832 | 0.31976 | 0.42664
2021-11-01 14:30 | 0.48186 | 1.2774 | 0.33281 | 0.56616 | 0.3909 | 0.20053 | 0.27724 | 0.41385
2021-11-01 14:45 | 0.45328 | 1.2521 | 0.30218 | 0.5192 | 0.37545 | 0.19909 | 0.23342 | 0.39807
2021-11-01 15:00 | 0.45328 | 1.3305 | 0.30218 | 0.48303 | 0.42235 | 0.21456 | 0.18831 | 0.38
2021-11-01 15:15 | 0.46553 | 1.1853 | 0.36344 | 0.49353 | 0.46925 | 0.22348 | 0.14319 | 0.36193
2021-11-01 15:30 | 1.5926 | 1.1675 | 0.46961 | 0.49907 | 0.51616 | 0.21478 | 0.098079 | 0.34386
2021-11-01 15:45 | 2.1643 | 1.1189 | 0.45736 | 0.5087 | 0.47288 | 0.19228 | 0.066168 | 0.29073
2021-11-01 16:00 | 1.9703 | 1.1787 | 0.3471 | 0.51687 | 0.33794 | 0.13879 | 0.047242 | 0.20688
2021-11-01 16:15 | 2.1643 | 1.0195 | 0.34302 | 0.52445 | 0.203 | 0.082823 | 0.028316 | 0.12303
2021-11-01 16:30 | 2.0826 | 1.1172 | 0.33894 | 0.54662 | 0.068062 | 0.03704 | 0.009391 | 0.039177
2021-11-01 16:45 | 0.93922 | 1.642 | 0.34915 | 0.58191 | 0 | 0.000235 | 0 | 0
2021-11-01 17:00 | 0.55537 | 1.6348 | 0.43286 | 0.61487 | 0 | 0.000166 | 0 | 0
2021-11-01 17:15 | 0.4737 | 1.4952 | 0.42061 | 0.55595 | 0 | 4.4e-05 | 0 | 0
2021-11-01 17:30 | 0.5227 | 1.4952 | 0.39611 | 0.56003 | 0 | 1.2e-05 | 0 | 0
2021-11-01 17:45 | 0.62887 | 1.4139 | 0.37569 | 0.56266 | 0 | 0 | 0 | 0
2021-11-01 18:00 | 0.71463 | 1.5824 | 0.45736 | 0.60554 | 0 | 0 | 0 | 0
2021-11-01 18:15 | 0.7963 | 1.7108 | 0.45328 | 0.61195 | 0 | 0 | 0 | 0
2021-11-01 18:30 | 0.77997 | 1.3497 | 1.8376 | 1.1907 | 0 | 0 | 0 | 0
2021-11-01 18:45 | 0.66562 | 1.7248 | 3.8998 | 1.9388 | 0 | 0 | 0 | 0
2021-11-01 19:00 | 0.66154 | 1.6471 | 3.91 | 2.0736 | 0 | 0 | 0 | 0
2021-11-01 19:15 | 1.3374 | 1.6471 | 3.8692 | 2.0263 | 0 | 0 | 0 | 0
2021-11-01 19:30 | 0.98823 | 1.6471 | 3.7569 | 2.0106 | 0 | 0 | 0 | 0
2021-11-01 19:45 | 1.0413 | 1.8886 | 4.6528 | 2.2964 | 0 | 0 | 0 | 0
2021-11-01 20:00 | 1.4395 | 1.1059 | 1.7559 | 1.3447 | 0 | 0 | 0 | 0
2021-11-01 20:15 | 1.4293 | 1.0691 | 1.368 | 0.96052 | 0 | 0 | 0 | 0
2021-11-01 20:30 | 1.1842 | 1.1625 | 1.0086 | 0.90364 | 0 | 0 | 0 | 0
2021-11-01 20:45 | 0.3859 | 1.0635 | 0.73504 | 0.71054 | 0 | 0 | 0 | 0
2021-11-01 21:00 | 0.39917 | 1.0474 | 0.65746 | 0.94856 | 0 | 0 | 0 | 0
2021-11-01 21:15 | 0.91064 | 1.1176 | 0.51862 | 1.2338 | 0 | 0 | 0 | 0
2021-11-01 21:30 | 0.68196 | 0.94453 | 0.46144 | 0.91531 | 0 | 0 | 0 | 0
2021-11-01 21:45 | 0.56762 | 0.94453 | 0.4982 | 0.85289 | 0 | 0 | 0 | 0
2021-11-01 22:00 | 1.5211 | 1.1203 | 0.50636 | 0.61312 | 0 | 0 | 0 | 0
2021-11-01 22:15 | 1.9295 | 0.78601 | 0.49003 | 0.5262 | 0 | 0 | 0 | 0
2021-11-01 22:30 | 0.53087 | 0.92908 | 0.38488 | 0.53014 | 0 | 0 | 0 | 0
2021-11-01 22:45 | 0.53087 | 1.037 | 0.42878 | 0.77997 | 0 | 0 | 0 | 0
2021-11-01 23:00 | 0.53495 | 1.2865 | 3.2975 | 1.7979 | 0 | 0 | 0 | 0
2021-11-01 23:15 | 0.4982 | 1.1566 | 3.5323 | 1.4109 | 0 | 0 | 0 | 0
2021-11-01 23:30 | 1.1638 | 1.1893 | 3.614 | 1.4249 | 0 | 0 | 0 | 0
2021-11-01 23:45 | 2.9606 | 1.2577 | 3.7569 | 1.4994 | 0 | 0 | 0 | 0
2021-11-02 | 0.40223 | 0.97005 | 3.7059 | 1.4403 | 0 | 0 | 0 | 0
2021-11-02 00:15 | 0.29096 | 0.97005 | 3.6038 | 1.2745 | 0 | 0 | 0 | 0
2021-11-02 00:30 | 0.28891 | 0.97005 | 3.4813 | 1.303 | 0 | 0 | 0 | 0
2021-11-02 00:45 | 0.28891 | 0.97362 | 3.4098 | 1.2774 | 0 | 0 | 0 | 0
2021-11-02 01:00 | 0.31852 | 0.94638 | 3.4404 | 1.2872 | 0 | 0 | 0 | 0
2021-11-02 01:15 | 0.41653 | 0.93185 | 3.4608 | 1.3938 | 0 | 0 | 0 | 0
2021-11-02 01:30 | 0.41244 | 0.91156 | 3.5221 | 1.6048 | 0 | 0 | 0 | 0
2021-11-02 01:45 | 0.31852 | 0.82974 | 3.5833 | 1.2401 | 0 | 0 | 0 | 0
2021-11-02 02:00 | 0.31546 | 0.75978 | 3.5323 | 1.2284 | 0 | 0 | 0 | 0
2021-11-02 02:15 | 0.30218 | 0.85928 | 3.471 | 1.2572 | 0 | 0 | 0 | 0
2021-11-02 02:30 | 0.3369 | 0.945 | 3.4608 | 1.2672 | 0 | 0 | 0 | 0
2021-11-02 02:45 | 0.42469 | 0.93047 | 3.4813 | 1.2661 | 0 | 0 | 0 | 0
2021-11-02 03:00 | 0.34506 | 0.91616 | 3.4813 | 1.2623 | 0 | 0 | 0 | 0
2021-11-02 03:15 | 0.31341 | 0.94611 | 3.614 | 1.271 | 0 | 0 | 0 | 0
2021-11-02 03:30 | 0.31954 | 0.8496 | 3.5936 | 1.2484 | 0 | 0 | 0 | 0
2021-11-02 03:45 | 0.30831 | 0.82615 | 3.5119 | 1.2321 | 0 | 0 | 0 | 0
2021-11-02 04:00 | 0.42878 | 0.75216 | 3.5323 | 1.2201 | 0 | 0 | 0 | 0
2021-11-02 04:15 | 0.35119 | 0.69566 | 3.5323 | 1.2197 | 0 | 0 | 0 | 0
2021-11-02 04:30 | 0.31852 | 0.8013 | 3.5119 | 1.2486 | 0 | 0 | 0 | 0
2021-11-02 04:45 | 0.30116 | 0.90341 | 3.5731 | 1.2978 | 0 | 0 | 0 | 0
2021-11-02 05:00 | 0.61254 | 1.024 | 3.8488 | 1.3509 | 0 | 0 | 0 | 0
2021-11-02 05:15 | 0.5472 | 1.0009 | 3.7263 | 1.2855 | 0 | 0 | 0 | 0
2021-11-02 05:30 | 0.40836 | 0.88282 | 3.5119 | 1.284 | 0 | 0 | 0 | 0
2021-11-02 05:45 | 0.42878 | 0.8457 | 3.614 | 1.2576 | 0 | 0 | 0 | 0
2021-11-02 06:00 | 0.43694 | 0.91132 | 3.6242 | 1.2698 | 0 | 0 | 0 | 0
2021-11-02 06:15 | 0.44511 | 1.013 | 3.6344 | 1.284 | 0 | 0 | 0 | 0
2021-11-02 06:30 | 0.35323 | 0.88933 | 3.5629 | 1.2795 | 0 | 0 | 0 | 0
2021-11-02 06:45 | 0.30729 | 0.73192 | 3.4506 | 1.2534 | 0.000504 | 0.023926 | 0.057251 | 0.028124
2021-11-02 07:00 | 0.34404 | 0.63679 | 0.56762 | 0.44569 | 0.001532 | 0.07863 | 0.17198 | 0.082227
2021-11-02 07:15 | 0.46553 | 0.6171 | 0.48186 | 0.3824 | 0.002559 | 0.14418 | 0.2867 | 0.13633
2021-11-02 07:30 | 0.42878 | 0.62704 | 0.53495 | 0.39771 | 0.003586 | 0.22323 | 0.40143 | 0.19043
2021-11-02 07:45 | 0.34506 | 0.66745 | 0.37671 | 0.412 | 0.009483 | 0.25021 | 0.44993 | 0.22038
2021-11-02 08:00 | 0.38896 | 1.1027 | 3.2873 | 1.3148 | 0.020437 | 0.25017 | 0.43187 | 0.22762
2021-11-02 08:15 | 0.84938 | 1.0283 | 2.491 | 1.2653 | 0.031391 | 0.27156 | 0.41381 | 0.23487
2021-11-02 08:30 | 1.1026 | 1.2805 | 1.2149 | 1.3855 | 0.042345 | 0.2881 | 0.39575 | 0.24212
2021-11-02 08:45 | 0.60437 | 1.0996 | 1.2251 | 1.2558 | 0.045358 | 0.28426 | 0.34541 | 0.24365
2021-11-02 09:00 | 0.46553 | 0.97402 | 1.4395 | 1.1367 | 0.040111 | 0.28932 | 0.26258 | 0.23952
2021-11-02 09:15 | 0.51453 | 0.90576 | 0.66154 | 1.0014 | 0.034864 | 0.29266 | 0.17975 | 0.23539
2021-11-02 09:30 | 0.61662 | 1.0566 | 0.53087 | 1.0474 | 0.029617 | 0.2831 | 0.096921 | 0.23126
2021-11-02 09:45 | 0.71463 | 0.85799 | 0.55128 | 0.96081 | 0.025845 | 0.30345 | 0.081158 | 0.24322
2021-11-02 10:00 | 0.83305 | 0.94984 | 0.77997 | 1.2294 | 0.023611 | 0.31791 | 0.133 | 0.27081
2021-11-02 10:15 | 0.73913 | 1.064 | 0.86164 | 1.5328 | 0.021376 | 0.34992 | 0.18484 | 0.29841
2021-11-02 10:30 | 0.72279 | 1.0323 | 0.76771 | 1.1577 | 0.019141 | 0.3519 | 0.23669 | 0.326
2021-11-02 10:45 | 0.5717 | 1.0451 | 1.3067 | 1.0868 | 0.019677 | 0.34767 | 0.23509 | 0.34482
2021-11-02 11:00 | 0.33894 | 1.5628 | 2.981 | 1.7778 | 0.023105 | 0.35186 | 0.17957 | 0.355
2021-11-02 11:15 | 0.29708 | 1.0883 | 1.3476 | 1.0235 | 0.026532 | 0.35318 | 0.12403 | 0.36517
2021-11-02 11:30 | 0.38182 | 1.0477 | 0.55945 | 0.75546 | 0.029959 | 0.36072 | 0.068504 | 0.37535
2021-11-02 11:45 | 0.33485 | 0.8568 | 0.67788 | 0.80242 | 0.056424 | 0.36879 | 0.069521 | 0.38376
2021-11-02 12:00 | 0.30014 | 0.92382 | 0.5472 | 0.86295 | 0.10695 | 0.36213 | 0.1277 | 0.39083
2021-11-02 12:15 | 0.38794 | 0.8425 | 0.56354 | 0.57054 | 0.15749 | 0.36024 | 0.18587 | 0.39791
2021-11-02 12:30 | 0.33281 | 1.1622 | 0.86572 | 0.92202 | 0.20802 | 0.35851 | 0.24405 | 0.40498
2021-11-02 12:45 | 0.29912 | 1.043 | 0.57987 | 0.69946 | 0.25297 | 0.35698 | 0.32132 | 0.41528
2021-11-02 13:00 | 0.39611 | 0.92087 | 0.89431 | 0.67671 | 0.29208 | 0.35452 | 0.41793 | 0.42971
2021-11-02 13:15 | 0.97598 | 1.0548 | 0.73913 | 0.83159 | 0.3312 | 0.35205 | 0.51453 | 0.44414
2021-11-02 13:30 | 1.0005 | 0.97398 | 0.49003 | 1.0603 | 0.37032 | 0.35251 | 0.61114 | 0.45857
2021-11-02 13:45 | 0.5472 | 0.96854 | 0.41653 | 0.6821 | 0.40089 | 0.34938 | 0.62158 | 0.4541
2021-11-02 14:00 | 0.22051 | 0.96211 | 0.38386 | 0.55653 | 0.42251 | 0.34576 | 0.54469 | 0.43068
2021-11-02 14:15 | 0.37773 | 0.92642 | 0.40427 | 0.52664 | 0.44412 | 0.34556 | 0.4678 | 0.40725
2021-11-02 14:30 | 0.42878 | 0.97504 | 0.48186 | 0.56091 | 0.46574 | 0.34946 | 0.3909 | 0.38383
2021-11-02 14:45 | 0.43694 | 0.98721 | 0.45328 | 0.50811 | 0.42656 | 0.35013 | 0.37545 | 0.36852
2021-11-02 15:00 | 0.42061 | 0.98721 | 0.45328 | 0.48974 | 0.3236 | 0.32521 | 0.42235 | 0.36172
2021-11-02 15:15 | 0.391 | 0.96377 | 0.46553 | 0.49178 | 0.22064 | 0.31026 | 0.46925 | 0.35492
2021-11-02 15:30 | 0.37569 | 0.98836 | 1.5926 | 0.65425 | 0.11768 | 0.27737 | 0.51616 | 0.34812
2021-11-02 15:45 | 0.48186 | 0.94605 | 2.1643 | 0.73913 | 0.057022 | 0.23232 | 0.47288 | 0.30017
2021-11-02 16:00 | 0.40427 | 0.92851 | 1.9703 | 0.72134 | 0.040789 | 0.16057 | 0.33794 | 0.21391
2021-11-02 16:15 | 0.42061 | 0.96625 | 2.1643 | 0.73679 | 0.024555 | 0.11116 | 0.203 | 0.12764
2021-11-02 16:30 | 0.55128 | 0.98065 | 2.0826 | 0.73738 | 0.008322 | 0.053868 | 0.068062 | 0.041367
2021-11-02 16:45 | 0.52678 | 0.95546 | 0.93922 | 0.60466 | 0 | 0.00272 | 0 | 0
2021-11-02 17:00 | 0.42878 | 0.95507 | 0.55537 | 0.58804 | 0 | 0.001919 | 0 | 0
2021-11-02 17:15 | 0.5227 | 0.81885 | 0.4737 | 0.54837 | 0 | 0.000571 | 0 | 0
2021-11-02 17:30 | 0.58395 | 0.95507 | 0.5227 | 0.5647 | 0 | 0.000163 | 0 | 0
2021-11-02 17:45 | 0.61254 | 0.91294 | 0.62887 | 0.59445 | 0 | 0 | 0 | 0
2021-11-02 18:00 | 0.78405 | 0.94231 | 0.71463 | 0.65279 | 0 | 0 | 0 | 0
2021-11-02 18:15 | 0.73504 | 1.0327 | 0.7963 | 0.65687 | 0 | 0 | 0 | 0
2021-11-02 18:30 | 0.71463 | 1.1796 | 0.77997 | 1.0498 | 0 | 0 | 0 | 0
2021-11-02 18:45 | 0.56762 | 1.5445 | 0.66562 | 1.8327 | 0 | 0 | 0 | 0
2021-11-02 19:00 | 0.61662 | 1.6222 | 0.66154 | 1.9814 | 0 | 0 | 0 | 0
2021-11-02 19:15 | 0.81672 | 1.6222 | 1.3374 | 2.0351 | 0 | 0 | 0 | 0
2021-11-02 19:30 | 1.0821 | 1.6966 | 0.98823 | 1.968 | 0 | 0 | 0 | 0
2021-11-02 19:45 | 0.96373 | 1.7552 | 1.0413 | 2.3489 | 0 | 0 | 0 | 0
2021-11-02 20:00 | 0.96781 | 1.3988 | 1.4395 | 1.4727 | 0 | 0 | 0 | 0
2021-11-02 20:15 | 1.3374 | 1.0971 | 1.4293 | 1.0842 | 0 | 0 | 0 | 0
2021-11-02 20:30 | 1.9601 | 1.0398 | 1.1842 | 0.99931 | 0 | 0 | 0 | 0
2021-11-02 20:45 | 0.55128 | 0.80416 | 0.3859 | 0.68692 | 0 | 0 | 0 | 0
2021-11-02 21:00 | 0.61662 | 0.92049 | 0.39917 | 0.93149 | 0 | 0 | 0 | 0
2021-11-02 21:15 | 0.96373 | 1.1676 | 0.91064 | 1.2945 | 0 | 0 | 0 | 0
2021-11-02 21:30 | 1.6947 | 0.80154 | 0.68196 | 0.94039 | 0 | 0 | 0 | 0
2021-11-02 21:45 | 1.2863 | 0.77223 | 0.56762 | 0.86397 | 0 | 0 | 0 | 0
2021-11-02 22:00 | 1.2761 | 0.82327 | 1.5211 | 0.76042 | 0 | 0 | 0 | 0
2021-11-02 22:15 | 0.53495 | 0.7779 | 1.9295 | 0.73825 | 0 | 0 | 0 | 0
2021-11-02 22:30 | 0.53495 | 0.69985 | 0.53087 | 0.55726 | 0 | 0 | 0 | 0
2021-11-02 22:45 | 0.51862 | 0.75034 | 0.53087 | 0.79105 | 0 | 0 | 0 | 0
2021-11-02 23:00 | 0.40836 | 1.6688 | 0.53495 | 1.8125 | 0 | 0 | 0 | 0
2021-11-02 23:15 | 0.37467 | 1.3999 | 0.4982 | 1.4179 | 0 | 0 | 0 | 0
2021-11-02 23:30 | 0.41653 | 1.3858 | 1.1638 | 1.5276 | 0 | 0 | 0 | 0
2021-11-02 23:45 | 2.9504 | 1.8698 | 2.9606 | 1.8611 | 0 | 0 | 0 | 0
2021-11-03 | 0.45736 | 1.5391 | 0.40223 | 1.4354 | 0 | 0 | 0 | 0
2021-11-03 00:15 | 0.44511 | 1.4717 | 0.29096 | 1.2548 | 0 | 0 | 0 | 0
2021-11-03 00:30 | 0.44919 | 1.5391 | 0.28891 | 1.2824 | 0 | 0 | 0 | 0
2021-11-03 00:45 | 0.39407 | 1.4284 | 0.28891 | 1.2647 | 0 | 0 | 0 | 0
2021-11-03 01:00 | 0.30014 | 1.5496 | 0.31852 | 1.2849 | 0 | 0 | 0 | 0
2021-11-03 01:15 | 2.5829 | 1.5391 | 0.41653 | 1.4039 | 0 | 0 | 0 | 0
2021-11-03 01:30 | 1.562 | 1.5737 | 0.41244 | 1.6145 | 0 | 0 | 0 | 0
2021-11-03 01:45 | 0.25931 | 1.7139 | 0.31852 | 1.2369 | 0 | 0 | 0 | 0
2021-11-03 02:00 | 0.26237 | 1.4936 | 0.31546 | 1.226 | 0 | 0 | 0 | 0
2021-11-03 02:15 | 0.25829 | 1.7593 | 0.30218 | 1.2414 | 0 | 0 | 0 | 0
2021-11-03 02:30 | 0.25522 | 1.7593 | 0.3369 | 1.2448 | 0 | 0 | 0 | 0
2021-11-03 02:45 | 0.35833 | 1.7107 | 0.42469 | 1.2567 | 0 | 0 | 0 | 0
2021-11-03 03:00 | 0.35425 | 1.7107 | 0.34506 | 1.2433 | 0 | 0 | 0 | 0
2021-11-03 03:15 | 0.25931 | 1.7949 | 0.31341 | 1.2481 | 0 | 0 | 0 | 0
2021-11-03 03:30 | 0.26033 | 1.7593 | 0.31954 | 1.2414 | 0 | 0 | 0 | 0
2021-11-03 03:45 | 0.25931 | 1.6165 | 0.30831 | 1.2344 | 0 | 0 | 0 | 0
2021-11-03 04:00 | 0.26033 | 1.7949 | 0.42878 | 1.2392 | 0 | 0 | 0 | 0
2021-11-03 04:15 | 0.29912 | 1.4788 | 0.35119 | 1.2261 | 0 | 0 | 0 | 0
2021-11-03 04:30 | 0.33996 | 1.7033 | 0.31852 | 1.2523 | 0 | 0 | 0 | 0
2021-11-03 04:45 | 0.2685 | 1.7401 | 0.30116 | 1.2993 | 0 | 0 | 0 | 0
2021-11-03 05:00 | 0.27564 | 1.7401 | 0.61254 | 1.3956 | 0 | 0 | 0 | 0
2021-11-03 05:15 | 0.33894 | 1.8244 | 0.5472 | 1.3215 | 0 | 0 | 0 | 0
2021-11-03 05:30 | 0.41244 | 1.8601 | 0.40836 | 1.2882 | 0 | 0 | 0 | 0
2021-11-03 05:45 | 0.31444 | 1.7033 | 0.42878 | 1.2605 | 0 | 0 | 0 | 0
2021-11-03 06:00 | 0.30218 | 1.742 | 0.43694 | 1.271 | 0 | 0 | 0 | 0
2021-11-03 06:15 | 0.28993 | 1.8934 | 0.44511 | 1.2881 | 0 | 0 | 0 | 0
2021-11-03 06:30 | 0.28585 | 1.8091 | 0.35323 | 1.2821 | 0 | 0 | 0 | 0
2021-11-03 06:45 | 0.34098 | 1.8079 | 0.30729 | 1.2548 | 0.00076 | 0.020858 | 0.000504 | 0.025086
2021-11-03 07:00 | 0.39815 | 0.62519 | 0.34404 | 0.44424 | 0.002335 | 0.063959 | 0.001532 | 0.073664
2021-11-03 07:15 | 0.33077 | 0.52749 | 0.46553 | 0.39961 | 0.00391 | 0.11193 | 0.002559 | 0.12224
2021-11-03 07:30 | 0.37671 | 0.53096 | 0.42878 | 0.40588 | 0.005485 | 0.17285 | 0.003586 | 0.17082
2021-11-03 07:45 | 0.35221 | 0.55534 | 0.34506 | 0.34054 | 0.008523 | 0.21149 | 0.009483 | 0.20142
2021-11-03 08:00 | 0.46961 | 1.4064 | 0.38896 | 1.2537 | 0.013133 | 0.22328 | 0.020437 | 0.21456
2021-11-03 08:15 | 0.48595 | 1.6487 | 0.84938 | 1.2962 | 0.017742 | 0.24942 | 0.031391 | 0.22771
2021-11-03 08:30 | 0.99231 | 1.4693 | 1.1026 | 1.4409 | 0.022352 | 0.26471 | 0.042345 | 0.24085
2021-11-03 08:45 | 0.80447 | 1.5856 | 0.60437 | 1.2523 | 0.041928 | 0.27272 | 0.045358 | 0.24447
2021-11-03 09:00 | 0.39202 | 1.4618 | 0.46553 | 1.1344 | 0.077595 | 0.27216 | 0.040111 | 0.23903
2021-11-03 09:15 | 0.42469 | 1.4347 | 0.51453 | 1.0107 | 0.11326 | 0.26068 | 0.034864 | 0.2336
2021-11-03 09:30 | 0.64521 | 1.4347 | 0.61662 | 1.0276 | 0.14893 | 0.23949 | 0.029617 | 0.22816
2021-11-03 09:45 | 0.80038 | 1.4347 | 0.71463 | 0.98764 | 0.15692 | 0.24041 | 0.025845 | 0.23918
2021-11-03 10:00 | 0.77997 | 1.5617 | 0.83305 | 1.2697 | 0.13511 | 0.26491 | 0.023611 | 0.26618
2021-11-03 10:15 | 0.43694 | 1.7783 | 0.73913 | 1.5532 | 0.1133 | 0.2953 | 0.021376 | 0.29317
2021-11-03 10:30 | 0.5227 | 1.4403 | 0.72279 | 1.1589 | 0.091494 | 0.29696 | 0.019141 | 0.32016
2021-11-03 10:45 | 0.49411 | 1.4403 | 0.5717 | 1.0576 | 0.10065 | 0.27676 | 0.019677 | 0.33522
2021-11-03 11:00 | 0.40325 | 1.275 | 0.33894 | 1.3464 | 0.14318 | 0.28066 | 0.023105 | 0.33911
2021-11-03 11:15 | 0.34506 | 1.1065 | 0.29708 | 0.95979 | 0.18572 | 0.31021 | 0.026532 | 0.34299
2021-11-03 11:30 | 0.30321 | 1.0977 | 0.38182 | 0.70908 | 0.22825 | 0.26885 | 0.029959 | 0.34688
2021-11-03 11:45 | 0.26543 | 1.0854 | 0.33485 | 0.76976 | 0.22242 | 0.27487 | 0.056424 | 0.35273
2021-11-03 12:00 | 0.41653 | 0.94101 | 0.30014 | 0.82882 | 0.16438 | 0.30428 | 0.10695 | 0.36105
2021-11-03 12:15 | 0.4982 | 1.0757 | 0.38794 | 0.5507 | 0.10633 | 0.30414 | 0.15749 | 0.36937
2021-11-03 12:30 | 0.36752 | 0.93269 | 0.33281 | 0.52766 | 0.048291 | 0.30388 | 0.20802 | 0.37769
2021-11-03 12:45 | 0.33077 | 0.92874 | 0.29912 | 0.52051 | 0.035128 | 0.30984 | 0.25297 | 0.39326
2021-11-03 13:00 | 0.28279 | 1.1319 | 0.39611 | 0.65337 | 0.07048 | 0.3077 | 0.29208 | 0.41612
2021-11-03 13:15 | 0.29504 | 1.1251 | 0.97598 | 0.85376 | 0.10583 | 0.30556 | 0.3312 | 0.43898
2021-11-03 13:30 | 1.3986 | 1.1217 | 1.0005 | 1.1443 | 0.14118 | 0.30342 | 0.37032 | 0.46184
2021-11-03 13:45 | 0.37773 | 1.0487 | 0.5472 | 0.70617 | 0.14547 | 0.30073 | 0.40089 | 0.46484
2021-11-03 14:00 | 0.38794 | 0.99259 | 0.22051 | 0.53276 | 0.11613 | 0.29828 | 0.42251 | 0.44782
2021-11-03 14:15 | 0.34915 | 0.88149 | 0.37773 | 0.51934 | 0.086785 | 0.2981 | 0.44412 | 0.4308
2021-11-03 14:30 | 0.31444 | 0.94379 | 0.42878 | 0.54983 | 0.057443 | 0.30146 | 0.46574 | 0.41378
2021-11-03 14:45 | 0.29708 | 0.77765 | 0.43694 | 0.48595 | 0.043771 | 0.29196 | 0.42656 | 0.39418
2021-11-03 15:00 | 0.60437 | 0.77765 | 0.42061 | 0.46582 | 0.047085 | 0.26052 | 0.3236 | 0.37229
2021-11-03 15:15 | 0.71871 | 0.75079 | 0.391 | 0.47472 | 0.0504 | 0.24854 | 0.22064 | 0.35041
2021-11-03 15:30 | 1.0005 | 0.80367 | 0.37569 | 0.63966 | 0.053715 | 0.23888 | 0.11768 | 0.32852
2021-11-03 15:45 | 0.46553 | 0.88642 | 0.48186 | 0.7473 | 0.048795 | 0.21109 | 0.057022 | 0.27672
2021-11-03 16:00 | 0.82488 | 0.90211 | 0.40427 | 0.71083 | 0.034936 | 0.16487 | 0.040789 | 0.19728
2021-11-03 16:15 | 0.35935 | 0.87628 | 0.42061 | 0.73155 | 0.021077 | 0.10717 | 0.024555 | 0.11784
2021-11-03 16:30 | 0.46553 | 0.93637 | 0.55128 | 0.74146 | 0.007218 | 0.047638 | 0.008322 | 0.038394
2021-11-03 16:45 | 0.43694 | 0.85348 | 0.52678 | 0.57433 | 0 | 0.001162 | 0 | 0
2021-11-03 17:00 | 0.40632 | 0.81667 | 0.42878 | 0.54662 | 0 | 0.000823 | 0 | 0
2021-11-03 17:15 | 0.40019 | 0.84376 | 0.5227 | 0.51978 | 0 | 0.000453 | 0 | 0
2021-11-03 17:30 | 0.54312 | 0.87561 | 0.58395 | 0.55595 | 0 | 0.000453 | 0 | 0
2021-11-03 17:45 | 0.43694 | 1.0176 | 0.61254 | 0.59387 | 0 | 0 | 0 | 0
2021-11-03 18:00 | 0.5962 | 1.0902 | 0.78405 | 0.67263 | 0 | 0 | 0 | 0
2021-11-03 18:15 | 0.58804 | 0.98222 | 0.73504 | 0.66154 | 0 | 0 | 0 | 0
2021-11-03 18:30 | 0.75546 | 0.97812 | 0.71463 | 1.0504 | 0 | 0 | 0 | 0
2021-11-03 18:45 | 0.64112 | 1.1496 | 0.56762 | 1.3727 | 0 | 0 | 0 | 0
2021-11-03 19:00 | 0.70238 | 1.1788 | 0.61662 | 1.5036 | 0 | 0 | 0 | 0
2021-11-03 19:15 | 0.64521 | 1.204 | 0.81672 | 1.5888 | 0 | 0 | 0 | 0
2021-11-03 19:30 | 0.68196 | 1.1943 | 1.0821 | 1.5669 | 0 | 0 | 0 | 0
2021-11-03 19:45 | 1.0209 | 1.371 | 0.96373 | 1.813 | 0 | 0 | 0 | 0
2021-11-03 20:00 | 0.81263 | 1.1589 | 0.96781 | 1.4389 | 0 | 0 | 0 | 0
2021-11-03 20:15 | 0.74321 | 1.0436 | 1.3374 | 1.1317 | 0 | 0 | 0 | 0
2021-11-03 20:30 | 0.70646 | 0.8966 | 1.9601 | 1.1796 | 0 | 0 | 0 | 0
2021-11-03 20:45 | 0.64521 | 0.8306 | 0.55128 | 0.68342 | 0 | 0 | 0 | 0
2021-11-03 21:00 | 0.74321 | 0.9605 | 0.61662 | 0.93033 | 0 | 0 | 0 | 0
2021-11-03 21:15 | 0.73504 | 1.1263 | 0.96373 | 1.3412 | 0 | 0 | 0 | 0
2021-11-03 21:30 | 0.67379 | 0.9984 | 1.6947 | 1.0956 | 0 | 0 | 0 | 0
2021-11-03 21:45 | 0.46553 | 0.83976 | 1.2863 | 0.96664 | 0 | 0 | 0 | 0
2021-11-03 22:00 | 0.49003 | 0.84645 | 1.2761 | 0.85697 | 0 | 0 | 0 | 0
2021-11-03 22:15 | 0.46144 | 0.81496 | 0.53495 | 0.7505 | 0 | 0 | 0 | 0
2021-11-03 22:30 | 0.44103 | 0.76249 | 0.53495 | 0.5701 | 0 | 0 | 0 | 0
2021-11-03 22:45 | 0.45736 | 0.98657 | 0.51862 | 0.80388 | 0 | 0 | 0 | 0
2021-11-03 23:00 | 0.45736 | 1.8593 | 0.40836 | 1.394 | 0 | 0 | 0 | 0
2021-11-03 23:15 | 0.45736 | 0.96115 | 0.37467 | 0.96533 | 0 | 0 | 0 | 0
2021-11-03 23:30 | 0.53903 | 1.0214 | 0.41653 | 1.081 | 0 | 0 | 0 | 0
2021-11-03 23:45 | 0.53495 | 1.2066 | 2.9504 | 1.7925 | 0 | 0 | 0 | 0
2021-11-04 | 0.38998 | 0.61777 | 0.45736 | 1.0121 | 0 | 0 | 0 | 0
2021-11-04 00:15 | 0.26952 | 0.56697 | 0.44511 | 0.82984 | 0 | 0 | 0 | 0
2021-11-04 00:30 | 0.26339 | 0.56697 | 0.44919 | 0.84924 | 0 | 0 | 0 | 0
2021-11-04 00:45 | 0.26543 | 0.56697 | 0.39407 | 0.80913 | 0 | 0 | 0 | 0
2021-11-04 01:00 | 0.25931 | 0.56697 | 0.30014 | 0.81147 | 0 | 0 | 0 | 0
2021-11-04 01:15 | 0.30218 | 0.987 | 2.5829 | 1.2726 | 0 | 0 | 0 | 0
2021-11-04 01:30 | 0.38079 | 0.89596 | 1.562 | 1.3417 | 0 | 0 | 0 | 0
2021-11-04 01:45 | 0.51453 | 0.56697 | 0.25931 | 0.77661 | 0 | 0 | 0 | 0
2021-11-04 02:00 | 0.66971 | 0.56768 | 0.26237 | 0.77048 | 0 | 0 | 0 | 0
2021-11-04 02:15 | 0.30014 | 0.56768 | 0.25829 | 0.77953 | 0 | 0 | 0 | 0
2021-11-04 02:30 | 0.30627 | 0.56768 | 0.25522 | 0.77078 | 0 | 0 | 0 | 0
2021-11-04 02:45 | 0.29912 | 0.56768 | 0.35833 | 0.79892 | 0 | 0 | 0 | 0
2021-11-04 03:00 | 0.40121 | 0.56768 | 0.35425 | 0.79659 | 0 | 0 | 0 | 0
2021-11-04 03:15 | 0.42061 | 0.56768 | 0.25931 | 0.7893 | 0 | 0 | 0 | 0
2021-11-04 03:30 | 0.43694 | 0.56768 | 0.26033 | 0.78565 | 0 | 0 | 0 | 0
2021-11-04 03:45 | 0.36854 | 0.60561 | 0.25931 | 0.77997 | 0 | 0 | 0 | 0
2021-11-04 04:00 | 0.28687 | 0.56768 | 0.26033 | 0.78492 | 0 | 0 | 0 | 0
2021-11-04 04:15 | 0.25522 | 0.59453 | 0.29912 | 0.77588 | 0 | 0 | 0 | 0
2021-11-04 04:30 | 0.33179 | 0.59453 | 0.33996 | 0.7963 | 0 | 0 | 0 | 0
2021-11-04 04:45 | 0.31035 | 0.65912 | 0.2685 | 0.83013 | 0 | 0 | 0 | 0
2021-11-04 05:00 | 0.25114 | 0.64281 | 0.27564 | 0.92741 | 0 | 0 | 0 | 0
2021-11-04 05:15 | 0.38794 | 0.77564 | 0.33894 | 0.87695 | 0 | 0 | 0 | 0
2021-11-04 05:30 | 0.36548 | 0.75787 | 0.41244 | 0.85711 | 0 | 0 | 0 | 0
2021-11-04 05:45 | 0.29198 | 0.61106 | 0.31444 | 0.81686 | 0 | 0 | 0 | 0
2021-11-04 06:00 | 0.37569 | 0.61106 | 0.30218 | 0.8227 | 0 | 0 | 0 | 0
2021-11-04 06:15 | 0.36752 | 0.62523 | 0.28993 | 0.83509 | 0 | 0 | 0 | 0
2021-11-04 06:30 | 0.26748 | 0.64122 | 0.28585 | 0.82999 | 0 | 0 | 0 | 0
2021-11-04 06:45 | 0.25829 | 0.64122 | 0.34098 | 0.79601 | 0.009785 | 0.021802 | 0.00076 | 0.023456
2021-11-04 07:00 | 0.33179 | 0.54281 | 0.39815 | 0.40136 | 0.030414 | 0.059978 | 0.002335 | 0.069041
2021-11-04 07:15 | 0.33792 | 0.50026 | 0.33077 | 0.38969 | 0.051042 | 0.09977 | 0.00391 | 0.11463
2021-11-04 07:30 | 0.46553 | 0.54454 | 0.37671 | 0.41171 | 0.07167 | 0.12662 | 0.005485 | 0.16021
2021-11-04 07:45 | 0.38488 | 0.5431 | 0.35221 | 0.34477 | 0.085499 | 0.12087 | 0.008523 | 0.186
2021-11-04 08:00 | 0.33587 | 0.93088 | 0.46961 | 0.85989 | 0.091783 | 0.15645 | 0.013133 | 0.19284
2021-11-04 08:15 | 0.33383 | 1.0363 | 0.48595 | 0.87126 | 0.098068 | 0.14694 | 0.017742 | 0.19969
2021-11-04 08:30 | 0.40836 | 0.86051 | 0.99231 | 1.0168 | 0.10435 | 0.18359 | 0.022352 | 0.20653
2021-11-04 08:45 | 0.37671 | 0.83025 | 0.80447 | 0.8189 | 0.10901 | 0.19185 | 0.041928 | 0.20713
2021-11-04 09:00 | 0.46553 | 0.8813 | 0.39202 | 0.66533 | 0.11185 | 0.20556 | 0.077595 | 0.20195
2021-11-04 09:15 | 0.40427 | 0.87568 | 0.42469 | 0.53612 | 0.11469 | 0.20927 | 0.11326 | 0.19678
2021-11-04 09:30 | 1.0515 | 0.8486 | 0.64521 | 0.58745 | 0.11753 | 0.20897 | 0.14893 | 0.1916
2021-11-04 09:45 | 0.42061 | 0.82007 | 0.80038 | 0.59445 | 0.11573 | 0.2018 | 0.15692 | 0.19861
2021-11-04 10:00 | 0.42469 | 0.8665 | 0.77997 | 0.86484 | 0.10876 | 0.226 | 0.13511 | 0.21708
2021-11-04 10:15 | 0.5472 | 0.79793 | 0.43694 | 1.0921 | 0.10179 | 0.21171 | 0.1133 | 0.23554
2021-11-04 10:30 | 0.5717 | 0.89039 | 0.5227 | 0.70996 | 0.094814 | 0.2129 | 0.091494 | 0.25401
2021-11-04 10:45 | 0.53495 | 0.83917 | 0.49411 | 0.62654 | 0.10157 | 0.21034 | 0.10065 | 0.26735
2021-11-04 11:00 | 2.9402 | 0.70282 | 0.40325 | 1.108 | 0.12362 | 0.22667 | 0.14318 | 0.27634
2021-11-04 11:15 | 1.2149 | 0.71265 | 0.34506 | 0.81657 | 0.14566 | 0.22752 | 0.18572 | 0.28533
2021-11-04 11:30 | 0.49411 | 0.83808 | 0.30321 | 0.55405 | 0.16771 | 0.20343 | 0.22825 | 0.29432
2021-11-04 11:45 | 0.73096 | 0.71956 | 0.26543 | 0.67642 | 0.20582 | 0.22132 | 0.22242 | 0.29889
2021-11-04 12:00 | 0.48595 | 0.74684 | 0.41653 | 0.79965 | 0.26183 | 0.33012 | 0.16438 | 0.29891
2021-11-04 12:15 | 2.8177 | 0.83056 | 0.4982 | 0.52562 | 0.31785 | 0.31387 | 0.10633 | 0.29894
2021-11-04 12:30 | 3.1342 | 0.77341 | 0.36752 | 0.48507 | 0.37386 | 0.30964 | 0.048291 | 0.29896
2021-11-04 12:45 | 1.1026 | 0.87431 | 0.33077 | 0.46217 | 0.41941 | 0.30832 | 0.035128 | 0.31319
2021-11-04 13:00 | 2.7973 | 0.88347 | 0.28279 | 0.54501 | 0.45328 | 0.30724 | 0.07048 | 0.34211
2021-11-04 13:15 | 0.51045 | 0.85037 | 0.29504 | 0.67423 | 0.48714 | 0.30511 | 0.10583 | 0.37103
2021-11-04 13:30 | 0.52678 | 1.091 | 1.3986 | 1.1909 | 0.521 | 0.31853 | 0.14118 | 0.39994
2021-11-04 13:45 | 0.53087 | 0.85533 | 0.37773 | 0.66154 | 0.50979 | 0.31571 | 0.14547 | 0.40429
2021-11-04 14:00 | 0.53087 | 0.78727 | 0.38794 | 0.47151 | 0.44816 | 0.29783 | 0.11613 | 0.38357
2021-11-04 14:15 | 0.60437 | 0.75101 | 0.34915 | 0.46713 | 0.38652 | 0.29766 | 0.086785 | 0.36286
2021-11-04 14:30 | 3.1954 | 0.74605 | 0.31444 | 0.49849 | 0.32489 | 0.29999 | 0.057443 | 0.34214
2021-11-04 14:45 | 0.98006 | 0.74605 | 0.29708 | 0.45371 | 0.30356 | 0.29053 | 0.043771 | 0.32398
2021-11-04 15:00 | 0.25829 | 0.70316 | 0.60437 | 0.47982 | 0.32739 | 0.26986 | 0.047085 | 0.30845
2021-11-04 15:15 | 0.24604 | 0.80595 | 0.71871 | 0.5138 | 0.35123 | 0.25745 | 0.0504 | 0.29291
2021-11-04 15:30 | 0.35323 | 0.94772 | 1.0005 | 0.7263 | 0.37506 | 0.23761 | 0.053715 | 0.27738
2021-11-04 15:45 | 0.28891 | 0.90201 | 0.46553 | 0.7473 | 0.34199 | 0.13629 | 0.048795 | 0.23514
2021-11-04 16:00 | 0.24502 | 0.9237 | 0.82488 | 0.747 | 0.24508 | 0.11322 | 0.034936 | 0.16773
2021-11-04 16:15 | 0.24399 | 0.85991 | 0.35935 | 0.69363 | 0.14818 | 0.083601 | 0.021077 | 0.10033
2021-11-04 16:30 | 0.28075 | 0.81466 | 0.46553 | 0.71579 | 0.051269 | 0.040553 | 0.007218 | 0.03293
2021-11-04 16:45 | 0.36854 | 0.82727 | 0.43694 | 0.56033 | 0 | 0.00104 | 0 | 0
2021-11-04 17:00 | 0.25012 | 0.82267 | 0.40632 | 0.52241 | 0 | 0.000737 | 0 | 0
2021-11-04 17:15 | 0.24706 | 0.8368 | 0.40019 | 0.50403 | 0 | 0.000402 | 0 | 0
2021-11-04 17:30 | 0.2491 | 0.8836 | 0.54312 | 0.5542 | 0 | 0.000437 | 0 | 0
2021-11-04 17:45 | 0.31137 | 0.94295 | 0.43694 | 0.5577 | 0 | 0 | 0 | 0
2021-11-04 18:00 | 0.36344 | 1.0322 | 0.5962 | 0.66037 | 0 | 0 | 0 | 0
2021-11-04 18:15 | 0.27564 | 1.0576 | 0.58804 | 0.65804 | 0 | 0 | 0 | 0
2021-11-04 18:30 | 0.34302 | 1.0082 | 0.75546 | 1.0714 | 0 | 0 | 0 | 0
2021-11-04 18:45 | 0.60029 | 0.9906 | 0.64112 | 1.3703 | 0 | 0 | 0 | 0
2021-11-04 19:00 | 1.8478 | 0.99605 | 0.70238 | 1.5112 | 0 | 0 | 0 | 0
2021-11-04 19:15 | 4.4186 | 1.0544 | 0.64521 | 1.5859 | 0 | 0 | 0 | 0
2021-11-04 19:30 | 5.2841 | 1.0217 | 0.68196 | 1.55 | 0 | 0 | 0 | 0
2021-11-04 19:45 | 5.3339 | 1.1566 | 1.0209 | 1.6803 | 0 | 0 | 0 | 0
2021-11-04 20:00 | 1.0617 | 0.93505 | 0.81263 | 1.2429 | 0 | 0 | 0 | 0
2021-11-04 20:15 | 1.3986 | 1.0246 | 0.74321 | 1.0206 | 0 | 0 | 0 | 0
2021-11-04 20:30 | 1.5007 | 0.99703 | 0.70646 | 1.1994 | 0 | 0 | 0 | 0
2021-11-04 20:45 | 0.56762 | 0.99356 | 0.64521 | 0.698 | 0 | 0 | 0 | 0
2021-11-04 21:00 | 0.56762 | 1.0506 | 0.74321 | 0.94258 | 0 | 0 | 0 | 0
2021-11-04 21:15 | 0.56354 | 0.98986 | 0.73504 | 0.97948 | 0 | 0 | 0 | 0
2021-11-04 21:30 | 0.60437 | 1.0413 | 0.67379 | 1.0781 | 0 | 0 | 0 | 0
2021-11-04 21:45 | 0.51862 | 0.99337 | 0.46553 | 0.95322 | 0 | 0 | 0 | 0
2021-11-04 22:00 | 0.46144 | 0.99487 | 0.49003 | 0.85114 | 0 | 0 | 0 | 0
2021-11-04 22:15 | 0.59212 | 0.96417 | 0.46144 | 0.74292 | 0 | 0 | 0 | 0
2021-11-04 22:30 | 0.43286 | 0.89761 | 0.44103 | 0.55726 | 0 | 0 | 0 | 0
2021-11-04 22:45 | 0.43286 | 0.73742 | 0.45736 | 0.5192 | 0 | 0 | 0 | 0
2021-11-04 23:00 | 3.369 | 0.78835 | 0.45736 | 0.89343 | 0 | 0 | 0 | 0
2021-11-04 23:15 | 3.5731 | 0.75606 | 0.45736 | 0.90408 | 0 | 0 | 0 | 0
2021-11-04 23:30 | 3.6854 | 0.79826 | 0.53903 | 1.0466 | 0 | 0 | 0 | 0
2021-11-04 23:45 | 3.614 | 0.92721 | 0.53495 | 1.8118 | 0 | 0 | 0 | 0
2021-11-05 | 3.4608 | 1.1101 | 0.38998 | 1.0226 | 0 | 0 | 0 | 0
2021-11-05 00:15 | 3.3894 | 1.1151 | 0.26952 | 0.82138 | 0 | 0 | 0 | 0
2021-11-05 00:30 | 3.369 | 1.1151 | 0.26339 | 0.83582 | 0 | 0 | 0 | 0
2021-11-05 00:45 | 3.369 | 1.1705 | 0.26543 | 0.8033 | 0 | 0 | 0 | 0
2021-11-05 01:00 | 3.4915 | 1.1705 | 0.25931 | 0.80301 | 0 | 0 | 0 | 0
2021-11-05 01:15 | 3.5629 | 1.1792 | 0.30218 | 1.2575 | 0 | 0 | 0 | 0
2021-11-05 01:30 | 3.5221 | 1.1178 | 0.38079 | 1.3537 | 0 | 0 | 0 | 0
2021-11-05 01:45 | 3.6344 | 1.0572 | 0.51453 | 0.8087 | 0 | 0 | 0 | 0
2021-11-05 02:00 | 3.859 | 1.0232 | 0.66971 | 0.81424 | 0 | 0 | 0 | 0
2021-11-05 02:15 | 3.4506 | 1.0811 | 0.30014 | 0.77544 | 0 | 0 | 0 | 0
2021-11-05 02:30 | 3.3894 | 1.0811 | 0.30627 | 0.7718 | 0 | 0 | 0 | 0
2021-11-05 02:45 | 3.4302 | 1.1822 | 0.29912 | 0.78915 | 0 | 0 | 0 | 0
2021-11-05 03:00 | 3.471 | 1.1126 | 0.40121 | 0.80184 | 0 | 0 | 0 | 0
2021-11-05 03:15 | 3.4915 | 1.0196 | 0.42061 | 0.80709 | 0 | 0 | 0 | 0
2021-11-05 03:30 | 3.5731 | 0.98646 | 0.43694 | 0.80578 | 0 | 0 | 0 | 0
2021-11-05 03:45 | 3.4608 | 0.98646 | 0.36854 | 0.77515 | 0 | 0 | 0 | 0
2021-11-05 04:00 | 3.4302 | 0.98646 | 0.28687 | 0.77165 | 0 | 0 | 0 | 0
2021-11-05 04:15 | 3.4098 | 1.0133 | 0.25522 | 0.76757 | 0 | 0 | 0 | 0
2021-11-05 04:30 | 3.471 | 1.0133 | 0.33179 | 0.79936 | 0 | 0 | 0 | 0
2021-11-05 04:45 | 3.3894 | 1.1027 | 0.31035 | 0.81497 | 0 | 0 | 0 | 0
2021-11-05 05:00 | 3.4608 | 1.0892 | 0.25114 | 0.90437 | 0 | 0 | 0 | 0
2021-11-05 05:15 | 3.4915 | 1.0354 | 0.38794 | 0.85478 | 0 | 0 | 0 | 0
2021-11-05 05:30 | 3.4506 | 0.9762 | 0.36548 | 0.82124 | 0 | 0 | 0 | 0
2021-11-05 05:45 | 3.5629 | 0.99393 | 0.29198 | 0.81365 | 0 | 0 | 0 | 0
2021-11-05 06:00 | 3.4608 | 0.99393 | 0.37569 | 0.83334 | 0 | 0 | 0 | 0
2021-11-05 06:15 | 3.3792 | 0.98854 | 0.36752 | 0.82868 | 0 | 0 | 0 | 0
2021-11-05 06:30 | 3.3792 | 1.078 | 0.26748 | 0.80636 | 0 | 0 | 0 | 0
2021-11-05 06:45 | 3.5221 | 0.98854 | 0.25829 | 0.77048 | 0.002022 | 0.020456 | 0.009785 | 0.019245
2021-11-05 07:00 | 0.67379 | 0.63843 | 0.33179 | 0.38167 | 0.006359 | 0.063564 | 0.030414 | 0.05723
2021-11-05 07:15 | 0.37161 | 0.65629 | 0.33792 | 0.39348 | 0.010696 | 0.10326 | 0.051042 | 0.095216
2021-11-05 07:30 | 0.37773 | 0.72317 | 0.46553 | 0.42965 | 0.015033 | 0.15035 | 0.07167 | 0.1332
2021-11-05 07:45 | 0.35527 | 0.78263 | 0.38488 | 0.3474 | 0.024704 | 0.16748 | 0.085499 | 0.15218
2021-11-05 08:00 | 3.2464 | 1.2187 | 0.33587 | 0.8087 | 0.040493 | 0.17253 | 0.091783 | 0.15268
2021-11-05 08:15 | 3.5731 | 1.2086 | 0.33383 | 0.80928 | 0.056282 | 0.18155 | 0.098068 | 0.15317
2021-11-05 08:30 | 3.5936 | 1.3915 | 0.40836 | 0.98998 | 0.07207 | 0.19626 | 0.10435 | 0.15367
2021-11-05 08:45 | 4.1734 | 1.3098 | 0.37671 | 0.8192 | 0.077253 | 0.21781 | 0.10901 | 0.15279
2021-11-05 09:00 | 3.7977 | 1.3164 | 0.46553 | 0.65892 | 0.070256 | 0.25077 | 0.11185 | 0.15037
2021-11-05 09:15 | 3.7875 | 1.1928 | 0.40427 | 0.52445 | 0.063259 | 0.27008 | 0.11469 | 0.14794
2021-11-05 09:30 | 3.8079 | 1.3437 | 1.0515 | 0.65716 | 0.056262 | 0.28945 | 0.11753 | 0.14552
2021-11-05 09:45 | 3.6038 | 1.3339 | 0.42061 | 0.61487 | 0.060969 | 0.29148 | 0.11573 | 0.14936
2021-11-05 10:00 | 3.6344 | 1.3804 | 0.42469 | 0.8768 | 0.079135 | 0.29259 | 0.10876 | 0.15928
2021-11-05 10:15 | 3.6752 | 1.2608 | 0.5472 | 1.1163 | 0.097301 | 0.27927 | 0.10179 | 0.1692
2021-11-05 10:30 | 3.7467 | 1.3553 | 0.5717 | 0.73213 | 0.11547 | 0.26302 | 0.094814 | 0.17911
2021-11-05 10:45 | 3.6446 | 1.3373 | 0.53495 | 0.64404 | 0.13129 | 0.26088 | 0.10157 | 0.18969
2021-11-05 11:00 | 3.4915 | 1.3428 | 2.9402 | 1.4781 | 0.1444 | 0.29309 | 0.12362 | 0.20148
2021-11-05 11:15 | 3.5119 | 1.3281 | 1.2149 | 0.94141 | 0.15752 | 0.29419 | 0.14566 | 0.21327
2021-11-05 11:30 | 3.5119 | 1.3055 | 0.49411 | 0.57126 | 0.17064 | 0.29529 | 0.16771 | 0.22507
2021-11-05 11:45 | 3.4506 | 1.2363 | 0.73096 | 0.73621 | 0.186 | 0.3019 | 0.20582 | 0.23508
2021-11-05 12:00 | 3.5323 | 1.3295 | 0.48595 | 0.81409 | 0.20397 | 0.30749 | 0.26183 | 0.24342
2021-11-05 12:15 | 3.665 | 1.3489 | 2.8177 | 0.84997 | 0.22194 | 0.29801 | 0.31785 | 0.25177
2021-11-05 12:30 | 3.7161 | 1.3295 | 3.1342 | 0.86689 | 0.2399 | 0.31761 | 0.37386 | 0.26011
2021-11-05 12:45 | 3.226 | 1.2942 | 1.1026 | 0.57068 | 0.25451 | 0.32479 | 0.41941 | 0.2815
2021-11-05 13:00 | 2.0724 | 1.2941 | 2.7973 | 0.8822 | 0.26524 | 0.28968 | 0.45328 | 0.31622
2021-11-05 13:15 | 1.8989 | 1.312 | 0.51045 | 0.68648 | 0.27597 | 0.30566 | 0.48714 | 0.35094
2021-11-05 13:30 | 3.7569 | 1.3804 | 0.52678 | 1.1629 | 0.2867 | 0.31229 | 0.521 | 0.38566
2021-11-05 13:45 | 1.1026 | 1.3553 | 0.53087 | 0.66912 | 0.2715 | 0.30952 | 0.50979 | 0.38831
2021-11-05 14:00 | 0.79222 | 1.1833 | 0.53087 | 0.47676 | 0.22631 | 0.29651 | 0.44816 | 0.35776
2021-11-05 14:15 | 0.66154 | 1.1878 | 0.60437 | 0.46772 | 0.18112 | 0.2814 | 0.38652 | 0.32721
2021-11-05 14:30 | 0.65337 | 1.2223 | 3.1954 | 0.88964 | 0.13593 | 0.29477 | 0.32489 | 0.29667
2021-11-05 14:45 | 0.65746 | 1.1692 | 0.98006 | 0.53305 | 0.099913 | 0.31638 | 0.30356 | 0.27836
2021-11-05 15:00 | 0.67379 | 1.102 | 0.25829 | 0.46801 | 0.07452 | 0.30276 | 0.32739 | 0.27262
2021-11-05 15:15 | 0.66154 | 1.1546 | 0.24604 | 0.48011 | 0.049127 | 0.26349 | 0.35123 | 0.26688
2021-11-05 15:30 | 0.61662 | 1.3081 | 0.35323 | 0.70383 | 0.023734 | 0.24665 | 0.37506 | 0.26114
2021-11-05 15:45 | 0.51045 | 1.3392 | 0.28891 | 0.7104 | 0.008931 | 0.1896 | 0.34199 | 0.22601
2021-11-05 16:00 | 0.40325 | 1.2879 | 0.24502 | 0.71434 | 0.006406 | 0.13703 | 0.24508 | 0.16147
2021-11-05 16:15 | 0.4982 | 1.2678 | 0.24399 | 0.66256 | 0.003881 | 0.089363 | 0.14818 | 0.096922
2021-11-05 16:30 | 0.56762 | 1.2829 | 0.28075 | 0.68823 | 0.001357 | 0.044665 | 0.051269 | 0.032379
2021-11-05 16:45 | 0.59212 | 1.1628 | 0.36854 | 0.53305 | 0 | 0.002749 | 0 | 0
2021-11-05 17:00 | 0.70646 | 1.1933 | 0.25012 | 0.47938 | 0 | 0.001948 | 0 | 0
2021-11-05 17:15 | 0.72279 | 1.189 | 0.24706 | 0.46349 | 0 | 0.001115 | 0 | 0
2021-11-05 17:30 | 0.75955 | 1.2058 | 0.2491 | 0.48711 | 0 | 0.000652 | 0 | 0
2021-11-05 17:45 | 0.80855 | 1.2058 | 0.31137 | 0.49893 | 0 | 0 | 0 | 0
2021-11-05 18:00 | 0.4982 | 1.4007 | 0.36344 | 0.60495 | 0 | 0 | 0 | 0
2021-11-05 18:15 | 0.46553 | 1.4451 | 0.27564 | 0.59358 | 0 | 0 | 0 | 0
2021-11-05 18:30 | 0.46961 | 1.2422 | 0.34302 | 0.94973 | 0 | 0 | 0 | 0
2021-11-05 18:45 | 0.63704 | 1.4917 | 0.60029 | 1.2665 | 0 | 0 | 0 | 0
2021-11-05 19:00 | 2.3991 | 1.57 | 1.8478 | 1.5798 | 0 | 0 | 0 | 0
2021-11-05 19:15 | 3.9509 | 1.7037 | 4.4186 | 2.0217 | 0 | 0 | 0 | 0
2021-11-05 19:30 | 3.9815 | 1.6137 | 5.2841 | 2.1299 | 0 | 0 | 0 | 0
2021-11-05 19:45 | 3.9611 | 1.6403 | 5.3339 | 2.2848 | 0 | 0 | 0 | 0
2021-11-05 20:00 | 0.80855 | 1.3177 | 1.0617 | 1.2598 | 0 | 0 | 0 | 0
2021-11-05 20:15 | 0.58395 | 1.1883 | 1.3986 | 1.0967 | 0 | 0 | 0 | 0
2021-11-05 20:30 | 1.5926 | 1.3523 | 1.5007 | 1.1192 | 0 | 0 | 0 | 0
2021-11-05 20:45 | 1.4395 | 1.1662 | 0.56762 | 0.60408 | 0 | 0 | 0 | 0
2021-11-05 21:00 | 2.3379 | 1.2775 | 0.56762 | 0.64739 | 0 | 0 | 0 | 0
2021-11-05 21:15 | 1.6947 | 1.1473 | 0.56354 | 0.70413 | 0 | 0 | 0 | 0
2021-11-05 21:30 | 0.57987 | 1.1538 | 0.60437 | 0.8698 | 0 | 0 | 0 | 0
2021-11-05 21:45 | 0.66971 | 1.1717 | 0.51862 | 0.72688 | 0 | 0 | 0 | 0
2021-11-05 22:00 | 2.3481 | 1.2299 | 0.46144 | 0.77646 | 0 | 0 | 0 | 0
2021-11-05 22:15 | 1.7662 | 1.066 | 0.59212 | 0.71142 | 0 | 0 | 0 | 0
2021-11-05 22:30 | 0.76363 | 0.82797 | 0.43286 | 0.48026 | 0 | 0 | 0 | 0
2021-11-05 22:45 | 0.94739 | 0.82797 | 0.43286 | 0.48536 | 0 | 0 | 0 | 0
2021-11-05 23:00 | 3.5323 | 1.3436 | 3.369 | 1.3018 | 0 | 0 | 0 | 0
2021-11-05 23:15 | 3.1954 | 1.2637 | 3.5731 | 1.3515 | 0 | 0 | 0 | 0
2021-11-05 23:30 | 2.8381 | 1.2247 | 3.6854 | 1.5089 | 0 | 0 | 0 | 0
2021-11-05 23:45 | 3.4302 | 1.8213 | 3.614 | 2.2832 | 0 | 0 | 0 | 0
2021-11-06 | 0.65337 | 1.3555 | 3.4608 | 1.473 | 0 | 0 | 0 | 0
2021-11-06 00:15 | 0.29504 | 0.98195 | 3.3894 | 1.2585 | 0 | 0 | 0 | 0
2021-11-06 00:30 | 0.29708 | 1.2713 | 3.369 | 1.2649 | 0 | 0 | 0 | 0
2021-11-06 00:45 | 0.2981 | 0.84532 | 3.369 | 1.2245 | 0 | 0 | 0 | 0
2021-11-06 01:00 | 0.41244 | 0.98195 | 3.4915 | 1.2365 | 0 | 0 | 0 | 0
2021-11-06 01:15 | 0.44511 | 1.6448 | 3.5629 | 1.7158 | 0 | 0 | 0 | 0
2021-11-06 01:30 | 0.34506 | 1.4203 | 3.5221 | 1.8125 | 0 | 0 | 0 | 0
2021-11-06 01:45 | 0.35221 | 1.0077 | 3.6344 | 1.2795 | 0 | 0 | 0 | 0
2021-11-06 02:00 | 0.39815 | 0.99862 | 3.859 | 1.3189 | 0 | 0 | 0 | 0
2021-11-06 02:15 | 0.44511 | 0.83643 | 3.4506 | 1.2233 | 0 | 0 | 0 | 0
2021-11-06 02:30 | 0.33996 | 0.83362 | 3.3894 | 1.2121 | 0 | 0 | 0 | 0
2021-11-06 02:45 | 0.35527 | 0.84533 | 3.4302 | 1.2191 | 0 | 0 | 0 | 0
2021-11-06 03:00 | 0.3859 | 0.89038 | 3.471 | 1.233 | 0 | 0 | 0 | 0
2021-11-06 03:15 | 0.42061 | 0.88355 | 3.4915 | 1.2507 | 0 | 0 | 0 | 0
2021-11-06 03:30 | 0.342 | 0.88355 | 3.5731 | 1.2649 | 0 | 0 | 0 | 0
2021-11-06 03:45 | 0.36344 | 0.82935 | 3.4608 | 1.2255 | 0 | 0 | 0 | 0
2021-11-06 04:00 | 0.40325 | 0.826 | 3.4302 | 1.2178 | 0 | 0 | 0 | 0
2021-11-06 04:15 | 0.45328 | 0.79369 | 3.4098 | 1.2077 | 0 | 0 | 0 | 0
2021-11-06 04:30 | 0.35731 | 0.86119 | 3.471 | 1.2439 | 0 | 0 | 0 | 0
2021-11-06 04:45 | 0.39407 | 0.84789 | 3.3894 | 1.2367 | 0 | 0 | 0 | 0
2021-11-06 05:00 | 0.36548 | 0.96372 | 3.4608 | 1.3393 | 0 | 0 | 0 | 0
2021-11-06 05:15 | 0.46553 | 1.0107 | 3.4915 | 1.3066 | 0 | 0 | 0 | 0
2021-11-06 05:30 | 0.38386 | 0.88588 | 3.4506 | 1.2628 | 0 | 0 | 0 | 0
2021-11-06 05:45 | 0.37161 | 0.90918 | 3.5629 | 1.2744 | 0 | 0 | 0 | 0
2021-11-06 06:00 | 0.43694 | 0.97651 | 3.4608 | 1.2837 | 0 | 0 | 0 | 0
2021-11-06 06:15 | 0.35935 | 0.91392 | 3.3792 | 1.2601 | 0 | 0 | 0 | 0
2021-11-06 06:30 | 0.38182 | 0.79238 | 3.3792 | 1.2249 | 0 | 0 | 0 | 0
2021-11-06 06:45 | 0.38488 | 0.79238 | 3.5221 | 1.2178 | 0.005831 | 0.024587 | 0.002022 | 0.012896
2021-11-06 07:00 | 0.49003 | 1.0736 | 0.67379 | 0.42513 | 0.018565 | 0.068237 | 0.006359 | 0.038825
2021-11-06 07:15 | 0.39713 | 1.1164 | 0.37161 | 0.39859 | 0.031299 | 0.11778 | 0.010696 | 0.064755
2021-11-06 07:30 | 0.41653 | 1.1307 | 0.37773 | 0.43271 | 0.044033 | 0.15687 | 0.015033 | 0.090684
2021-11-06 07:45 | 0.39713 | 1.1278 | 0.35527 | 0.3471 | 0.054954 | 0.17583 | 0.024704 | 0.1043
2021-11-06 08:00 | 0.45736 | 0.91379 | 3.2464 | 1.2013 | 0.063726 | 0.18535 | 0.040493 | 0.10571
2021-11-06 08:15 | 0.51045 | 0.98781 | 3.5731 | 1.2217 | 0.072497 | 0.20538 | 0.056282 | 0.10713
2021-11-06 08:30 | 0.45736 | 1.2898 | 3.5936 | 1.251 | 0.081269 | 0.23786 | 0.07207 | 0.10854
2021-11-06 08:45 | 0.75138 | 1.0374 | 4.1734 | 1.2418 | 0.080207 | 0.25742 | 0.077253 | 0.10466
2021-11-06 09:00 | 0.67788 | 1.0657 | 3.7977 | 1.1122 | 0.067474 | 0.26612 | 0.070256 | 0.095312
2021-11-06 09:15 | 1.9601 | 0.99813 | 3.7875 | 0.96868 | 0.05474 | 0.26913 | 0.063259 | 0.085967
2021-11-06 09:30 | 1.0311 | 0.99423 | 3.8079 | 1.0792 | 0.042006 | 0.26284 | 0.056262 | 0.076621
2021-11-06 09:45 | 0.82488 | 0.98605 | 3.6038 | 1.0218 | 0.039785 | 0.27849 | 0.060969 | 0.077106
2021-11-06 10:00 | 1.0821 | 1.2995 | 3.6344 | 1.2846 | 0.050062 | 0.28824 | 0.079135 | 0.087313
2021-11-06 10:15 | 0.71871 | 1.5264 | 3.6752 | 1.5783 | 0.060339 | 0.28038 | 0.097301 | 0.097519
2021-11-06 10:30 | 0.64112 | 1.2114 | 3.7467 | 1.202 | 0.070615 | 0.27865 | 0.11547 | 0.10773
2021-11-06 10:45 | 0.8698 | 1.0284 | 3.6446 | 1.1023 | 0.072781 | 0.29184 | 0.13129 | 0.11959
2021-11-06 11:00 | 1.1944 | 1.2639 | 3.4915 | 1.9203 | 0.065291 | 0.32689 | 0.1444 | 0.13349
2021-11-06 11:15 | 3.0933 | 1.1486 | 3.5119 | 1.3673 | 0.057802 | 0.32812 | 0.15752 | 0.1474
2021-11-06 11:30 | 2.6645 | 0.98435 | 3.5119 | 0.98837 | 0.050313 | 0.32734 | 0.17064 | 0.1613
2021-11-06 11:45 | 0.63296 | 1.0686 | 3.4506 | 1.116 | 0.058496 | 0.34553 | 0.186 | 0.17317
2021-11-06 12:00 | 0.55128 | 1.0143 | 3.5323 | 1.2458 | 0.085362 | 0.3052 | 0.20397 | 0.1832
2021-11-06 12:15 | 0.48595 | 1.2391 | 3.665 | 1.2925 | 0.11223 | 0.30769 | 0.22194 | 0.19324
2021-11-06 12:30 | 0.51862 | 1.047 | 3.7161 | 1.3213 | 0.13909 | 0.279 | 0.2399 | 0.20327
2021-11-06 12:45 | 0.53495 | 0.96013 | 3.226 | 0.94229 | 0.19584 | 0.25889 | 0.25451 | 0.22701
2021-11-06 13:00 | 0.55945 | 0.98934 | 2.0724 | 1.0925 | 0.28827 | 0.2571 | 0.26524 | 0.26456
2021-11-06 13:15 | 1.4701 | 1.1422 | 1.8989 | 0.88074 | 0.3807 | 0.28052 | 0.27597 | 0.30211
2021-11-06 13:30 | 0.50636 | 1.3781 | 3.7569 | 1.5305 | 0.47313 | 0.27855 | 0.2867 | 0.33966
2021-11-06 13:45 | 0.67379 | 1.1422 | 1.1026 | 0.76655 | 0.5237 | 0.27034 | 0.2715 | 0.34237
2021-11-06 14:00 | 0.99231 | 1.3466 | 0.79222 | 0.54312 | 0.52425 | 0.26754 | 0.22631 | 0.30845
2021-11-06 14:15 | 2.0316 | 1.3936 | 0.66154 | 0.48988 | 0.5248 | 0.26592 | 0.18112 | 0.27453
2021-11-06 14:30 | 2.1847 | 1.0862 | 0.65337 | 0.88147 | 0.52535 | 0.24559 | 0.13593 | 0.24061
2021-11-06 14:45 | 2.0418 | 1.3353 | 0.65746 | 0.5243 | 0.50798 | 0.2481 | 0.099913 | 0.21899
2021-11-06 15:00 | 2.1235 | 1.4968 | 0.67379 | 0.46626 | 0.46917 | 0.23044 | 0.07452 | 0.21033
2021-11-06 15:15 | 1.4599 | 1.329 | 0.66154 | 0.47778 | 0.43035 | 0.20815 | 0.049127 | 0.20168
2021-11-06 15:30 | 0.34098 | 0.93342 | 0.61662 | 0.69567 | 0.39154 | 0.1991 | 0.023734 | 0.19302
2021-11-06 15:45 | 0.293 | 1.0154 | 0.51045 | 0.69231 | 0.32827 | 0.18472 | 0.008931 | 0.16537
2021-11-06 16:00 | 0.28789 | 0.98839 | 0.40325 | 0.67977 | 0.23568 | 0.14282 | 0.006406 | 0.11826
2021-11-06 16:15 | 0.27666 | 0.98839 | 0.4982 | 0.64273 | 0.14309 | 0.097046 | 0.003881 | 0.07115
2021-11-06 16:30 | 0.27768 | 0.93807 | 0.56762 | 0.67773 | 0.050506 | 0.047466 | 0.001357 | 0.024037
2021-11-06 16:45 | 0.27666 | 1.1897 | 0.59212 | 0.53889 | 0 | 0.000444 | 0 | 0
2021-11-06 17:00 | 0.38488 | 1.5252 | 0.70646 | 0.49513 | 0 | 0.000315 | 0 | 0
2021-11-06 17:15 | 0.38896 | 1.5217 | 0.72279 | 0.48099 | 0 | 0.000154 | 0 | 0
2021-11-06 17:30 | 0.42061 | 1.4803 | 0.75955 | 0.5122 | 0 | 0.000363 | 0 | 0
2021-11-06 17:45 | 0.66562 | 1.5088 | 0.80855 | 0.52751 | 0 | 0 | 0 | 0
2021-11-06 18:00 | 0.69013 | 1.4344 | 0.4982 | 0.5892 | 0 | 0 | 0 | 0
2021-11-06 18:15 | 0.66971 | 1.3168 | 0.46553 | 0.57083 | 0 | 0 | 0 | 0
2021-11-06 18:30 | 2.5727 | 0.99546 | 0.46961 | 0.78346 | 0 | 0 | 0 | 0
2021-11-06 18:45 | 3.8386 | 1.6018 | 0.63704 | 1.2525 | 0 | 0 | 0 | 0
2021-11-06 19:00 | 3.8896 | 1.9206 | 2.3991 | 1.7924 | 0 | 0 | 0 | 0
2021-11-06 19:15 | 4.223 | 2.0715 | 3.9509 | 2.4735 | 0 | 0 | 0 | 0
2021-11-06 19:30 | 4.0877 | 1.9631 | 3.9815 | 2.6065 | 0 | 0 | 0 | 0
2021-11-06 19:45 | 4.2071 | 1.9357 | 3.9611 | 2.734 | 0 | 0 | 0 | 0
2021-11-06 20:00 | 2.0928 | 1.3968 | 0.80855 | 1.258 | 0 | 0 | 0 | 0
2021-11-06 20:15 | 1.2353 | 1.2439 | 0.58395 | 1.0769 | 0 | 0 | 0 | 0
2021-11-06 20:30 | 1.4905 | 1.3425 | 1.5926 | 1.2376 | 0 | 0 | 0 | 0
2021-11-06 20:45 | 0.91064 | 1.0107 | 1.4395 | 0.70646 | 0 | 0 | 0 | 0
2021-11-06 21:00 | 0.4982 | 0.99627 | 2.3379 | 0.88103 | 0 | 0 | 0 | 0
2021-11-06 21:15 | 0.57578 | 0.91661 | 1.6947 | 0.86105 | 0 | 0 | 0 | 0
2021-11-06 21:30 | 0.52678 | 0.89362 | 0.57987 | 0.7543 | 0 | 0 | 0 | 0
2021-11-06 21:45 | 0.55537 | 0.95003 | 0.66971 | 0.66504 | 0 | 0 | 0 | 0
2021-11-06 22:00 | 0.54312 | 0.94848 | 2.3481 | 1.0209 | 0 | 0 | 0 | 0
2021-11-06 22:15 | 0.46553 | 0.83604 | 1.7662 | 0.90539 | 0 | 0 | 0 | 0
2021-11-06 22:30 | 0.46144 | 1.3854 | 0.76363 | 0.51176 | 0 | 0 | 0 | 0
2021-11-06 22:45 | 0.47778 | 1.2884 | 0.94739 | 0.54778 | 0 | 0 | 0 | 0
2021-11-06 23:00 | 3.3996 | 1.2409 | 3.5323 | 1.7265 | 0 | 0 | 0 | 0
2021-11-06 23:15 | 3.6038 | 1.1863 | 3.1954 | 1.7421 | 0 | 0 | 0 | 0
2021-11-06 23:30 | 3.5731 | 1.2148 | 2.8381 | 1.8332 | 0 | 0 | 0 | 0
2021-11-06 23:45 | 3.4302 | 1.2544 | 3.4302 | 2.5209 | 0 | 0 | 0 | 0
2021-11-07 | 3.4506 | 0.99846 | 0.65337 | 1.3359 | 0 | 0 | 0 | 0
2021-11-07 00:15 | 3.4506 | 0.92356 | 0.29504 | 1.2225 | 0 | 0 | 0 | 0
2021-11-07 00:30 | 3.5119 | 0.92356 | 0.29708 | 1.2035 | 0 | 0 | 0 | 0
2021-11-07 00:45 | 3.369 | 0.93328 | 0.2981 | 1.2017 | 0 | 0 | 0 | 0
2021-11-07 01:00 | 1.9193 | 0.93328 | 0.41244 | 1.2254 | 0 | 0 | 0 | 0
2021-11-07 01:15 | 1.1128 | 1.076 | 0.44511 | 1.5767 | 0 | 0 | 0 | 0
2021-11-07 01:30 | 1.1434 | 1.0758 | 0.34506 | 1.4301 | 0 | 0 | 0 | 0
2021-11-07 01:45 | 0.78813 | 1.0331 | 0.35221 | 1.2757 | 0 | 0 | 0 | 0
2021-11-07 02:00 | 0.36752 | 1.1965 | 0.39815 | 1.3283 | 0 | 0 | 0 | 0
2021-11-07 02:15 | 0.39713 | 1.0846 | 0.44511 | 1.228 | 0 | 0 | 0 | 0
2021-11-07 02:30 | 0.37671 | 1.0846 | 0.33996 | 1.2045 | 0 | 0 | 0 | 0
2021-11-07 02:45 | 0.38386 | 1.1469 | 0.35527 | 1.2308 | 0 | 0 | 0 | 0
2021-11-07 03:00 | 0.48186 | 1.2194 | 0.3859 | 1.2436 | 0 | 0 | 0 | 0
2021-11-07 03:15 | 0.36956 | 1.1915 | 0.42061 | 1.2547 | 0 | 0 | 0 | 0
2021-11-07 03:30 | 0.39611 | 1.2241 | 0.342 | 1.269 | 0 | 0 | 0 | 0
2021-11-07 03:45 | 0.46553 | 1.0491 | 0.36344 | 1.2258 | 0 | 0 | 0 | 0
2021-11-07 04:00 | 0.41244 | 1.0491 | 0.40325 | 1.2294 | 0 | 0 | 0 | 0
2021-11-07 04:15 | 0.39407 | 1.0344 | 0.45328 | 1.2236 | 0 | 0 | 0 | 0
2021-11-07 04:30 | 0.36854 | 1.1768 | 0.35731 | 1.2414 | 0 | 0 | 0 | 0
2021-11-07 04:45 | 0.45736 | 1.0294 | 0.39407 | 1.2373 | 0 | 0 | 0 | 0
2021-11-07 05:00 | 0.48186 | 1.2006 | 0.36548 | 1.3502 | 0 | 0 | 0 | 0
2021-11-07 05:15 | 0.36956 | 1.2508 | 0.46553 | 1.333 | 0 | 0 | 0 | 0
2021-11-07 05:30 | 0.40019 | 1.196 | 0.38386 | 1.2611 | 0 | 0 | 0 | 0
2021-11-07 05:45 | 0.37773 | 1.2476 | 0.37161 | 1.2852 | 0 | 0 | 0 | 0
2021-11-07 06:00 | 0.40836 | 1.0914 | 0.43694 | 1.2939 | 0 | 0 | 0 | 0
2021-11-07 06:15 | 0.49411 | 1.0999 | 0.35935 | 1.2703 | 0 | 0 | 0 | 0
2021-11-07 06:30 | 0.37058 | 1.0945 | 0.38182 | 1.2281 | 0 | 0 | 0 | 0
2021-11-07 06:45 | 0.38896 | 0.89343 | 0.38488 | 1.223 | 7.8e-05 | 0.017786 | 0.005831 | 0.013224
2021-11-07 07:00 | 0.39815 | 0.6991 | 0.49003 | 0.44847 | 0.00025 | 0.054117 | 0.018565 | 0.039994
2021-11-07 07:15 | 0.43694 | 0.70948 | 0.39713 | 0.39961 | 0.000423 | 0.090219 | 0.031299 | 0.066764
2021-11-07 07:30 | 0.44919 | 0.77192 | 0.41653 | 0.43388 | 0.000595 | 0.13847 | 0.044033 | 0.093534
2021-11-07 07:45 | 0.41244 | 0.82067 | 0.39713 | 0.36081 | 0.006006 | 0.14941 | 0.054954 | 0.10822
2021-11-07 08:00 | 1.2149 | 1.0925 | 0.45736 | 1.2125 | 0.017835 | 0.17413 | 0.063726 | 0.11085
2021-11-07 08:15 | 0.75546 | 1.0925 | 0.51045 | 1.2252 | 0.029664 | 0.21193 | 0.072497 | 0.11349
2021-11-07 08:30 | 0.61662 | 1.2206 | 0.45736 | 1.181 | 0.041493 | 0.27363 | 0.081269 | 0.11612
2021-11-07 08:45 | 0.44103 | 1.5207 | 0.75138 | 1.2897 | 0.052142 | 0.28422 | 0.080207 | 0.11195
2021-11-07 09:00 | 0.41653 | 1.3568 | 0.67788 | 1.1314 | 0.061344 | 0.27828 | 0.067474 | 0.10055
2021-11-07 09:15 | 0.46961 | 1.3343 | 1.9601 | 1.1769 | 0.070545 | 0.26356 | 0.05474 | 0.089146
2021-11-07 09:30 | 1.3067 | 1.3181 | 1.0311 | 1.1635 | 0.079747 | 0.25228 | 0.042006 | 0.077742
2021-11-07 09:45 | 2.2051 | 1.3199 | 0.82488 | 1.0667 | 0.088355 | 0.26997 | 0.039785 | 0.077859
2021-11-07 10:00 | 0.69829 | 1.3526 | 1.0821 | 1.2087 | 0.096235 | 0.28824 | 0.050062 | 0.089661
2021-11-07 10:15 | 0.7473 | 1.3974 | 0.71871 | 1.2566 | 0.10411 | 0.3055 | 0.060339 | 0.10146
2021-11-07 10:30 | 0.66154 | 1.3172 | 0.64112 | 1.0749 | 0.11199 | 0.33399 | 0.070615 | 0.11327
2021-11-07 10:45 | 1.2047 | 1.3052 | 0.8698 | 1.1414 | 0.1144 | 0.33591 | 0.072781 | 0.12534
2021-11-07 11:00 | 0.77997 | 1.7573 | 1.1944 | 1.9976 | 0.11008 | 0.3227 | 0.065291 | 0.13788
2021-11-07 11:15 | 2.5931 | 1.6107 | 3.0933 | 1.7193 | 0.10576 | 0.29853 | 0.057802 | 0.15041
2021-11-07 11:30 | 2.6747 | 1.6071 | 2.6645 | 1.2897 | 0.10144 | 0.28748 | 0.050313 | 0.16295
2021-11-07 11:45 | 2.736 | 1.2892 | 0.63296 | 1.1154 | 0.092527 | 0.29391 | 0.058496 | 0.17586
2021-11-07 12:00 | 2.5318 | 1.4384 | 0.55128 | 1.2417 | 0.077943 | 0.30919 | 0.085362 | 0.18978
2021-11-07 12:15 | 2.8789 | 1.443 | 0.48595 | 1.2633 | 0.063359 | 0.33745 | 0.11223 | 0.2037
2021-11-07 12:30 | 0.41653 | 1.4462 | 0.51862 | 1.3266 | 0.048775 | 0.35232 | 0.13909 | 0.21762
2021-11-07 12:45 | 0.46553 | 1.2214 | 0.53495 | 0.95279 | 0.038386 | 0.36705 | 0.19584 | 0.24938
2021-11-07 13:00 | 0.39202 | 1.3765 | 0.55945 | 1.096 | 0.033171 | 0.34318 | 0.28827 | 0.29992
2021-11-07 13:15 | 0.42469 | 1.3023 | 1.4701 | 0.92304 | 0.027957 | 0.31423 | 0.3807 | 0.35047
2021-11-07 13:30 | 0.44103 | 1.332 | 0.50636 | 1.1653 | 0.022742 | 0.31064 | 0.47313 | 0.40101
2021-11-07 13:45 | 0.44103 | 1.2818 | 0.67379 | 0.61633 | 0.036455 | 0.30789 | 0.5237 | 0.4111
2021-11-07 14:00 | 0.44511 | 1.2312 | 0.99231 | 0.55537 | 0.073554 | 0.3015 | 0.52425 | 0.37776
2021-11-07 14:15 | 0.5227 | 1.2799 | 2.0316 | 0.68035 | 0.11065 | 0.31419 | 0.5248 | 0.34442
2021-11-07 14:30 | 0.44919 | 1.2642 | 2.1847 | 1.0845 | 0.14775 | 0.34067 | 0.52535 | 0.31107
2021-11-07 14:45 | 0.61254 | 1.2515 | 2.0418 | 0.7384 | 0.14955 | 0.30389 | 0.50798 | 0.28438
2021-11-07 15:00 | 0.46144 | 1.1731 | 2.1235 | 0.69085 | 0.10768 | 0.26789 | 0.46917 | 0.26463
2021-11-07 15:15 | 0.5717 | 1.1396 | 1.4599 | 0.61516 | 0.065806 | 0.21038 | 0.43035 | 0.24488
2021-11-07 15:30 | 0.53495 | 1.1172 | 0.34098 | 0.67846 | 0.023932 | 0.18544 | 0.39154 | 0.22514
2021-11-07 15:45 | 0.42469 | 1.0793 | 0.293 | 0.66592 | 0.000675 | 0.16237 | 0.32827 | 0.18915
2021-11-07 16:00 | 0.34506 | 1.0724 | 0.28789 | 0.64039 | 0.000485 | 0.12647 | 0.23568 | 0.13544
2021-11-07 16:15 | 0.31444 | 1.0724 | 0.27666 | 0.61516 | 0.000295 | 0.077202 | 0.14309 | 0.081728
2021-11-07 16:30 | 0.31239 | 1.0724 | 0.27768 | 0.65206 | 0.000105 | 0.02369 | 0.050506 | 0.028018
2021-11-07 16:45 | 0.293 | 0.91942 | 0.27666 | 0.49849 | 0 | 1.2e-05 | 0 | 0
2021-11-07 17:00 | 0.28075 | 0.95304 | 0.38488 | 0.45211 | 0 | 9e-06 | 0 | 0
2021-11-07 17:15 | 0.30627 | 1.0825 | 0.38896 | 0.45371 | 0 | 5e-06 | 0 | 0
2021-11-07 17:30 | 0.41244 | 1.083 | 0.42061 | 0.49645 | 0 | 2e-06 | 0 | 0
2021-11-07 17:45 | 0.42061 | 1.0724 | 0.66562 | 0.54851 | 0 | 0 | 0 | 0
2021-11-07 18:00 | 0.80447 | 1.1479 | 0.69013 | 0.58629 | 0 | 0 | 0 | 0
2021-11-07 18:15 | 0.58804 | 1.1292 | 0.66971 | 0.56908 | 0 | 0 | 0 | 0
2021-11-07 18:30 | 0.46961 | 1.338 | 2.5727 | 1.0676 | 0 | 0 | 0 | 0
2021-11-07 18:45 | 0.50636 | 1.6159 | 3.8386 | 1.55 | 0 | 0 | 0 | 0
2021-11-07 19:00 | 0.55945 | 1.8431 | 3.8896 | 2.0039 | 0 | 0 | 0 | 0
2021-11-07 19:15 | 0.75955 | 2.1917 | 4.223 | 2.7516 | 0 | 0 | 0 | 0
2021-11-07 19:30 | 0.98414 | 2.2349 | 4.0877 | 2.8375 | 0 | 0 | 0 | 0
2021-11-07 19:45 | 1.2251 | 2.4245 | 4.2071 | 3.0258 | 0 | 0 | 0 | 0
2021-11-07 20:00 | 2.3174 | 1.3717 | 2.0928 | 1.277 | 0 | 0 | 0 | 0
2021-11-07 20:15 | 1.9703 | 1.1931 | 1.2353 | 1.1565 | 0 | 0 | 0 | 0
2021-11-07 20:30 | 1.6028 | 1.4476 | 1.4905 | 1.349 | 0 | 0 | 0 | 0
2021-11-07 20:45 | 0.70646 | 1.0066 | 0.91064 | 0.74788 | 0 | 0 | 0 | 0
2021-11-07 21:00 | 0.61254 | 1.0987 | 0.4982 | 0.83145 | 0 | 0 | 0 | 0
2021-11-07 21:15 | 0.79222 | 0.92289 | 0.57578 | 0.85172 | 0 | 0 | 0 | 0
2021-11-07 21:30 | 3.7773 | 0.80008 | 0.52678 | 0.74613 | 0 | 0 | 0 | 0
2021-11-07 21:45 | 0.81263 | 0.7948 | 0.55537 | 0.65162 | 0 | 0 | 0 | 0
2021-11-07 22:00 | 0.61662 | 0.94139 | 0.54312 | 1.0209 | 0 | 0 | 0 | 0
2021-11-07 22:15 | 0.64929 | 0.92289 | 0.46553 | 0.89139 | 0 | 0 | 0 | 0
2021-11-07 22:30 | 0.66154 | 0.71712 | 0.46144 | 0.50709 | 0 | 0 | 0 | 0
2021-11-07 22:45 | 0.71054 | 0.82361 | 0.47778 | 0.54195 | 0 | 0 | 0 | 0
2021-11-07 23:00 | 2.7258 | 1.8253 | 3.3996 | 2.1427 | 0 | 0 | 0 | 0
2021-11-07 23:15 | 2.3685 | 1.8706 | 3.6038 | 2.1764 | 0 | 0 | 0 | 0
2021-11-07 23:30 | 0.4982 | 1.9605 | 3.5731 | 2.2614 | 0 | 0 | 0 | 0
2021-11-07 23:45 | 0.57987 | 2.291 | 3.4302 | 2.9539 | 0 | 0 | 0 | 0
2021-11-08 | 0.46961 | 2.3376 | 3.4506 | 1.7886 | 0 | 0 | 0 | 0
2021-11-08 00:15 | 0.5227 | 2.0712 | 3.4506 | 1.6778 | 0 | 0 | 0 | 0
2021-11-08 00:30 | 0.56354 | 2.1698 | 3.5119 | 1.6658 | 0 | 0 | 0 | 0
2021-11-08 00:45 | 0.58804 | 2.1427 | 3.369 | 1.6277 | 0 | 0 | 0 | 0
2021-11-08 01:00 | 0.60845 | 2.205 | 1.9193 | 1.4488 | 0 | 0 | 0 | 0
2021-11-08 01:15 | 0.44919 | 2.1577 | 1.1128 | 1.6976 | 0 | 0 | 0 | 0
2021-11-08 01:30 | 0.43286 | 2.1304 | 1.1434 | 1.5554 | 0 | 0 | 0 | 0
2021-11-08 01:45 | 0.33281 | 2.0078 | 0.78813 | 1.3501 | 0 | 0 | 0 | 0
2021-11-08 02:00 | 0.33077 | 1.9498 | 0.36752 | 1.3435 | 0 | 0 | 0 | 0
2021-11-08 02:15 | 0.41653 | 2.1861 | 0.39713 | 1.2321 | 0 | 0 | 0 | 0
2021-11-08 02:30 | 0.33179 | 2.0657 | 0.37671 | 1.2093 | 0 | 0 | 0 | 0
2021-11-08 02:45 | 0.33894 | 2.1271 | 0.38386 | 1.2475 | 0 | 0 | 0 | 0
2021-11-08 03:00 | 0.41244 | 2.3079 | 0.48186 | 1.2744 | 0 | 0 | 0 | 0
2021-11-08 03:15 | 0.40427 | 2.1355 | 0.36956 | 1.2698 | 0 | 0 | 0 | 0
2021-11-08 03:30 | 0.33179 | 2.1413 | 0.39611 | 1.2745 | 0 | 0 | 0 | 0
2021-11-08 03:45 | 0.33485 | 2.2585 | 0.46553 | 1.2483 | 0 | 0 | 0 | 0
2021-11-08 04:00 | 0.39509 | 2.2585 | 0.41244 | 1.2506 | 0 | 0 | 0 | 0
2021-11-08 04:15 | 0.39815 | 2.1729 | 0.39407 | 1.2421 | 0 | 0 | 0 | 0
2021-11-08 04:30 | 0.33587 | 2.1729 | 0.36854 | 1.2427 | 0 | 0 | 0 | 0
2021-11-08 04:45 | 0.33383 | 2.0743 | 0.45736 | 1.242 | 0 | 0 | 0 | 0
2021-11-08 05:00 | 0.42469 | 2.0229 | 0.48186 | 1.328 | 0 | 0 | 0 | 0
2021-11-08 05:15 | 0.39917 | 2.0229 | 0.36956 | 1.3324 | 0 | 0 | 0 | 0
2021-11-08 05:30 | 0.33179 | 1.9972 | 0.40019 | 1.2761 | 0 | 0 | 0 | 0
2021-11-08 05:45 | 0.33281 | 2.0229 | 0.37773 | 1.2802 | 0 | 0 | 0 | 0
2021-11-08 06:00 | 0.41653 | 2.0229 | 0.40836 | 1.2922 | 0 | 0 | 0 | 0
2021-11-08 06:15 | 0.35323 | 1.9751 | 0.49411 | 1.2814 | 0 | 0 | 0 | 0
2021-11-08 06:30 | 0.32873 | 1.8404 | 0.37058 | 1.2287 | 0 | 0 | 0 | 0
2021-11-08 06:45 | 0.36446 | 1.9609 | 0.38896 | 1.2362 | 0.016975 | 0.029309 | 7.8e-05 | 0.01089
2021-11-08 07:00 | 0.44103 | 0.60621 | 0.39815 | 0.45765 | 0.055424 | 0.073599 | 0.00025 | 0.033062
2021-11-08 07:15 | 0.33894 | 0.58793 | 0.43694 | 0.40311 | 0.093873 | 0.10242 | 0.000423 | 0.055233
2021-11-08 07:30 | 0.41244 | 0.64554 | 0.44919 | 0.43563 | 0.13232 | 0.14421 | 0.000595 | 0.077404
2021-11-08 07:45 | 0.35935 | 0.7494 | 0.41244 | 0.37482 | 0.17608 | 0.16951 | 0.006006 | 0.0913
2021-11-08 08:00 | 0.46961 | 1.7223 | 1.2149 | 1.3429 | 0.22655 | 0.1659 | 0.017835 | 0.09704
2021-11-08 08:15 | 0.45328 | 1.294 | 0.75546 | 1.2856 | 0.27702 | 0.19328 | 0.029664 | 0.10278
2021-11-08 08:30 | 0.38284 | 1.2258 | 0.61662 | 1.1979 | 0.32749 | 0.21467 | 0.041493 | 0.10852
2021-11-08 08:45 | 0.35935 | 1.3008 | 0.44103 | 1.1966 | 0.35303 | 0.21965 | 0.052142 | 0.10733
2021-11-08 09:00 | 1.0617 | 1.2838 | 0.41653 | 1.0935 | 0.34695 | 0.22239 | 0.061344 | 0.098744
2021-11-08 09:15 | 0.4982 | 1.2949 | 0.46961 | 1.1746 | 0.34087 | 0.25107 | 0.070545 | 0.090159
2021-11-08 09:30 | 2.7666 | 1.2872 | 1.3067 | 1.2843 | 0.33479 | 0.25831 | 0.079747 | 0.081574
2021-11-08 09:45 | 2.0622 | 1.2958 | 2.2051 | 1.303 | 0.34704 | 0.26011 | 0.088355 | 0.081252
2021-11-08 10:00 | 0.71871 | 1.2155 | 0.69829 | 1.1761 | 0.38256 | 0.26258 | 0.096235 | 0.089416
2021-11-08 10:15 | 0.5472 | 1.1413 | 0.7473 | 1.1037 | 0.41809 | 0.24803 | 0.10411 | 0.09758
2021-11-08 10:30 | 0.40325 | 1.281 | 0.66154 | 1.0906 | 0.45361 | 0.25115 | 0.11199 | 0.10575
2021-11-08 10:45 | 0.43694 | 1.1427 | 1.2047 | 1.2324 | 0.48904 | 0.25259 | 0.1144 | 0.11078
2021-11-08 11:00 | 0.48595 | 1.539 | 0.77997 | 1.7328 | 0.52434 | 0.26128 | 0.11008 | 0.11275
2021-11-08 11:15 | 0.61254 | 1.3177 | 2.5931 | 1.7718 | 0.55964 | 0.26226 | 0.10576 | 0.11472
2021-11-08 11:30 | 0.51045 | 1.4643 | 2.6747 | 1.5128 | 0.59494 | 0.28575 | 0.10144 | 0.11669
2021-11-08 11:45 | 0.2981 | 1.3414 | 2.736 | 1.2612 | 0.61527 | 0.27935 | 0.092527 | 0.12732
2021-11-08 12:00 | 0.31648 | 1.2482 | 2.5318 | 1.195 | 0.61651 | 0.25169 | 0.077943 | 0.14688
2021-11-08 12:15 | 1.1332 | 1.2389 | 2.8789 | 1.6139 | 0.61776 | 0.26774 | 0.063359 | 0.16644
2021-11-08 12:30 | 2.1949 | 1.1268 | 0.41653 | 1.3359 | 0.619 | 0.26977 | 0.048775 | 0.186
2021-11-08 12:45 | 2.2664 | 1.199 | 0.46553 | 0.93412 | 0.61061 | 0.26062 | 0.038386 | 0.2168
2021-11-08 13:00 | 2.4297 | 1.1778 | 0.39202 | 1.0563 | 0.58991 | 0.25803 | 0.033171 | 0.26006
2021-11-08 13:15 | 0.81263 | 1.2834 | 0.42469 | 0.90204 | 0.56922 | 0.25718 | 0.027957 | 0.30333
2021-11-08 13:30 | 0.42878 | 1.3058 | 0.44103 | 1.16 | 0.54853 | 0.25177 | 0.022742 | 0.3466
2021-11-08 13:45 | 0.44103 | 1.366 | 0.44103 | 0.58424 | 0.5372 | 0.25759 | 0.036455 | 0.35848
2021-11-08 14:00 | 0.69421 | 1.5325 | 0.44511 | 0.53612 | 0.53785 | 0.26223 | 0.073554 | 0.33651
2021-11-08 14:15 | 0.69421 | 1.3464 | 0.5227 | 0.70734 | 0.53849 | 0.26522 | 0.11065 | 0.31454
2021-11-08 14:30 | 1.0168 | 1.2798 | 0.44919 | 1.1011 | 0.53913 | 0.26933 | 0.14775 | 0.29257
2021-11-08 14:45 | 0.69829 | 1.2452 | 0.61254 | 0.78274 | 0.51152 | 0.2413 | 0.14955 | 0.2724
2021-11-08 15:00 | 0.31954 | 1.2142 | 0.46144 | 0.71361 | 0.44776 | 0.23317 | 0.10768 | 0.25311
2021-11-08 15:15 | 0.44919 | 1.1938 | 0.5717 | 0.64492 | 0.38401 | 0.2103 | 0.065806 | 0.23383
2021-11-08 15:30 | 0.30116 | 1.1241 | 0.53495 | 0.68779 | 0.32025 | 0.20347 | 0.023932 | 0.21455
2021-11-08 15:45 | 0.40325 | 1.1241 | 0.42469 | 0.66125 | 0.25328 | 0.19496 | 0.000675 | 0.17979
2021-11-08 16:00 | 0.40121 | 1.055 | 0.34506 | 0.6401 | 0.18217 | 0.13045 | 0.000485 | 0.12876
2021-11-08 16:15 | 0.39611 | 1.0492 | 0.31444 | 0.61108 | 0.11106 | 0.088838 | 0.000295 | 0.077725
2021-11-08 16:30 | 0.391 | 1.0878 | 0.31239 | 0.64827 | 0.039957 | 0.029993 | 0.000105 | 0.026691
2021-11-08 16:45 | 0.28687 | 0.92763 | 0.293 | 0.49047 | 0 | 0 | 0 | 0
2021-11-08 17:00 | 0.27462 | 0.97113 | 0.28075 | 0.43038 | 0 | 0 | 0 | 0
2021-11-08 17:15 | 1.562 | 1.1393 | 0.30627 | 0.43738 | 0 | 0 | 0 | 0
2021-11-08 17:30 | 3.5323 | 1.1004 | 0.41244 | 0.49878 | 0 | 0 | 0 | 0
2021-11-08 17:45 | 3.5936 | 1.1567 | 0.42061 | 0.55493 | 0 | 0 | 0 | 0
2021-11-08 18:00 | 3.7977 | 1.1296 | 0.80447 | 0.63587 | 0 | 0 | 0 | 0
2021-11-08 18:15 | 3.8794 | 1.0217 | 0.58804 | 0.58833 | 0 | 0 | 0 | 0
2021-11-08 18:30 | 3.8692 | 1.0924 | 0.46961 | 0.87214 | 0 | 0 | 0 | 0
2021-11-08 18:45 | 3.7977 | 1.2931 | 0.50636 | 1.0652 | 0 | 0 | 0 | 0
2021-11-08 19:00 | 4.1284 | 1.3828 | 0.55945 | 1.5252 | 0 | 0 | 0 | 0
2021-11-08 19:15 | 4.053 | 1.6202 | 0.75955 | 2.3073 | 0 | 0 | 0 | 0
2021-11-08 19:30 | 4.3111 | 1.5948 | 0.98414 | 2.4414 | 0 | 0 | 0 | 0
2021-11-08 19:45 | 4.3047 | 1.6639 | 1.2251 | 2.5362 | 0 | 0 | 0 | 0
2021-11-08 20:00 | 0.72688 | 1.1961 | 2.3174 | 1.3572 | 0 | 0 | 0 | 0
2021-11-08 20:15 | 0.5962 | 1.1078 | 1.9703 | 1.2426 | 0 | 0 | 0 | 0
2021-11-08 20:30 | 0.5717 | 1.2524 | 1.6028 | 1.4339 | 0 | 0 | 0 | 0
2021-11-08 20:45 | 0.60437 | 0.87426 | 0.70646 | 0.7438 | 0 | 0 | 0 | 0
2021-11-08 21:00 | 0.56354 | 0.972 | 0.61254 | 0.82503 | 0 | 0 | 0 | 0
2021-11-08 21:15 | 0.42061 | 1.0235 | 0.79222 | 0.8908 | 0 | 0 | 0 | 0
2021-11-08 21:30 | 0.31954 | 1.213 | 3.7773 | 1.2198 | 0 | 0 | 0 | 0
2021-11-08 21:45 | 0.30729 | 0.81334 | 0.81263 | 0.69654 | 0 | 0 | 0 | 0
2021-11-08 22:00 | 0.31341 | 1.0939 | 0.61662 | 1.0366 | 0 | 0 | 0 | 0
2021-11-08 22:15 | 0.3369 | 0.88169 | 0.64929 | 0.91414 | 0 | 0 | 0 | 0
2021-11-08 22:30 | 0.3369 | 0.62309 | 0.66154 | 0.54662 | 0 | 0 | 0 | 0
2021-11-08 22:45 | 0.34302 | 0.8798 | 0.71054 | 0.5822 | 0 | 0 | 0 | 0
2021-11-08 23:00 | 2.6952 | 1.1088 | 2.7258 | 2.061 | 0 | 0 | 0 | 0
2021-11-08 23:15 | 1.1332 | 1.1903 | 2.3685 | 2.0101 | 0 | 0 | 0 | 0
2021-11-08 23:30 | 0.68196 | 1.4825 | 0.4982 | 1.8163 | 0 | 0 | 0 | 0
2021-11-08 23:45 | 0.39407 | 1.6942 | 0.57987 | 2.5 | 0 | 0 | 0 | 0
2021-11-09 | 0.1807 | 1.1566 | 0.46961 | 1.3263 | 0 | 0 | 0 | 0
2021-11-09 00:15 | 0.19499 | 1.0925 | 0.5227 | 1.2376 | 0 | 0 | 0 | 0
2021-11-09 00:30 | 0.18172 | 1.0925 | 0.56354 | 1.249 | 0 | 0 | 0 | 0
2021-11-09 00:45 | 0.1858 | 1.0308 | 0.58804 | 1.2246 | 0 | 0 | 0 | 0
2021-11-09 01:00 | 0.26237 | 1.0018 | 0.60845 | 1.0442 | 0 | 0 | 0 | 0
2021-11-09 01:15 | 0.25522 | 1.111 | 0.44919 | 1.2674 | 0 | 0 | 0 | 0
2021-11-09 01:30 | 0.3471 | 1.0062 | 0.43286 | 1.1141 | 0 | 0 | 0 | 0
2021-11-09 01:45 | 0.30014 | 0.96501 | 0.33281 | 0.8857 | 0 | 0 | 0 | 0
2021-11-09 02:00 | 0.21337 | 1.0166 | 0.33077 | 0.88614 | 0 | 0 | 0 | 0
2021-11-09 02:15 | 0.21541 | 0.93103 | 0.41653 | 0.79571 | 0 | 0 | 0 | 0
2021-11-09 02:30 | 0.21643 | 0.93103 | 0.33179 | 0.76232 | 0 | 0 | 0 | 0
2021-11-09 02:45 | 0.22664 | 0.9304 | 0.33894 | 0.79863 | 0 | 0 | 0 | 0
2021-11-09 03:00 | 0.26543 | 0.91933 | 0.41244 | 0.83597 | 0 | 0 | 0 | 0
2021-11-09 03:15 | 0.33996 | 0.93103 | 0.40427 | 0.81132 | 0 | 0 | 0 | 0
2021-11-09 03:30 | 0.50228 | 0.88615 | 0.33179 | 0.80855 | 0 | 0 | 0 | 0
2021-11-09 03:45 | 0.4737 | 0.88615 | 0.33485 | 0.7944 | 0 | 0 | 0 | 0
2021-11-09 04:00 | 0.2297 | 0.91287 | 0.39509 | 0.80242 | 0 | 0 | 0 | 0
2021-11-09 04:15 | 0.2297 | 0.913 | 0.39815 | 0.7944 | 0 | 0 | 0 | 0
2021-11-09 04:30 | 0.28687 | 0.913 | 0.33587 | 0.78901 | 0 | 0 | 0 | 0
2021-11-09 04:45 | 0.32873 | 0.913 | 0.33383 | 0.77924 | 0 | 0 | 0 | 0
2021-11-09 05:00 | 0.34404 | 0.95451 | 0.42469 | 0.83888 | 0 | 0 | 0 | 0
2021-11-09 05:15 | 0.29504 | 0.9657 | 0.39917 | 0.85711 | 0 | 0 | 0 | 0
2021-11-09 05:30 | 0.2246 | 0.88474 | 0.33179 | 0.82182 | 0 | 0 | 0 | 0
2021-11-09 05:45 | 0.21133 | 0.92034 | 0.33281 | 0.81147 | 0 | 0 | 0 | 0
2021-11-09 06:00 | 0.29912 | 0.92034 | 0.41653 | 0.83393 | 0 | 0 | 0 | 0
2021-11-09 06:15 | 0.27462 | 0.93903 | 0.35323 | 0.81263 | 0 | 0 | 0 | 0
2021-11-09 06:30 | 0.22051 | 0.91232 | 0.32873 | 0.76669 | 0 | 0 | 0 | 0
2021-11-09 06:45 | 0.22766 | 0.91232 | 0.36446 | 0.79528 | 0.003151 | 0.020802 | 0.016975 | 0.005136
2021-11-09 07:00 | 0.37977 | 0.63343 | 0.44103 | 0.43957 | 0.010423 | 0.059283 | 0.055424 | 0.016411
2021-11-09 07:15 | 0.26441 | 0.64836 | 0.33894 | 0.38269 | 0.017694 | 0.11504 | 0.093873 | 0.027686
2021-11-09 07:30 | 0.69829 | 0.68303 | 0.41244 | 0.41813 | 0.024966 | 0.15006 | 0.13232 | 0.038961
2021-11-09 07:45 | 0.39713 | 0.70192 | 0.35935 | 0.37234 | 0.04991 | 0.20777 | 0.17608 | 0.052178
2021-11-09 08:00 | 1.1536 | 1.0843 | 0.46961 | 0.94039 | 0.098001 | 0.19218 | 0.22655 | 0.067707
2021-11-09 08:15 | 0.96781 | 1.226 | 0.45328 | 0.9945 | 0.14609 | 0.18177 | 0.27702 | 0.083237
2021-11-09 08:30 | 0.69829 | 1.3157 | 0.38284 | 1.0791 | 0.19418 | 0.21901 | 0.32749 | 0.098767
2021-11-09 08:45 | 0.58804 | 1.2023 | 0.35935 | 1.073 | 0.24657 | 0.23832 | 0.35303 | 0.10842
2021-11-09 09:00 | 0.53903 | 1.2143 | 1.0617 | 1.0396 | 0.30458 | 0.23863 | 0.34695 | 0.1108
2021-11-09 09:15 | 0.44511 | 1.2448 | 0.4982 | 1.1513 | 0.3626 | 0.25651 | 0.34087 | 0.11318
2021-11-09 09:30 | 0.43286 | 1.3707 | 2.7666 | 1.6037 | 0.42061 | 0.26779 | 0.33479 | 0.11556
2021-11-09 09:45 | 0.40325 | 1.462 | 2.0622 | 1.5188 | 0.4776 | 0.28183 | 0.34704 | 0.11923
2021-11-09 10:00 | 0.3614 | 1.2968 | 0.71871 | 1.1673 | 0.53326 | 0.30584 | 0.38256 | 0.12507
2021-11-09 10:15 | 0.50228 | 1.2698 | 0.5472 | 1.0588 | 0.58891 | 0.3229 | 0.41809 | 0.1309
2021-11-09 10:30 | 0.65746 | 1.2744 | 0.40325 | 1.0385 | 0.64455 | 0.34206 | 0.45361 | 0.13673
2021-11-09 10:45 | 0.54312 | 1.2415 | 0.43694 | 1.1081 | 0.67627 | 0.35649 | 0.48904 | 0.14706
2021-11-09 11:00 | 0.56354 | 1.3476 | 0.48595 | 1.3763 | 0.6765 | 0.35784 | 0.52434 | 0.162
2021-11-09 11:15 | 0.64521 | 1.3478 | 0.61254 | 1.6668 | 0.67673 | 0.3504 | 0.55964 | 0.17695
2021-11-09 11:30 | 0.49003 | 1.3476 | 0.51045 | 1.5058 | 0.67697 | 0.35171 | 0.59494 | 0.19189
2021-11-09 11:45 | 0.38182 | 1.2423 | 0.2981 | 1.207 | 0.6782 | 0.34493 | 0.61527 | 0.20528
2021-11-09 12:00 | 0.33281 | 1.2306 | 0.31648 | 1.1621 | 0.68076 | 0.33814 | 0.61651 | 0.21671
2021-11-09 12:15 | 1.7662 | 1.3478 | 1.1332 | 1.6953 | 0.68332 | 0.32555 | 0.61776 | 0.22814
2021-11-09 12:30 | 2.5522 | 1.3018 | 2.1949 | 1.5258 | 0.68588 | 0.29987 | 0.619 | 0.23956
2021-11-09 12:45 | 2.2256 | 1.1878 | 2.2664 | 1.1751 | 0.68128 | 0.29073 | 0.61061 | 0.25812
2021-11-09 13:00 | 0.95964 | 1.2937 | 2.4297 | 1.2757 | 0.66723 | 0.28768 | 0.58991 | 0.28463
2021-11-09 13:15 | 2.7156 | 1.3662 | 0.81263 | 0.91253 | 0.65317 | 0.24441 | 0.56922 | 0.31115
2021-11-09 13:30 | 1.0821 | 1.3282 | 0.42878 | 1.1513 | 0.63912 | 0.23917 | 0.54853 | 0.33766
2021-11-09 13:45 | 0.65337 | 1.1593 | 0.44103 | 0.58774 | 0.62467 | 0.26695 | 0.5372 | 0.34643
2021-11-09 14:00 | 0.26748 | 1.2453 | 0.69421 | 0.58045 | 0.60969 | 0.33001 | 0.53785 | 0.33554
2021-11-09 14:15 | 0.27768 | 1.2646 | 0.69421 | 0.74875 | 0.59471 | 0.34377 | 0.53849 | 0.32464
2021-11-09 14:30 | 0.31035 | 1.2099 | 1.0168 | 1.1775 | 0.57973 | 0.34765 | 0.53913 | 0.31375
2021-11-09 14:45 | 0.36752 | 1.1692 | 0.69829 | 0.81774 | 0.54621 | 0.33669 | 0.51152 | 0.29184
2021-11-09 15:00 | 1.3986 | 1.1007 | 0.31954 | 0.6945 | 0.48816 | 0.32483 | 0.44776 | 0.25674
2021-11-09 15:15 | 0.20418 | 1.0511 | 0.44919 | 0.64258 | 0.43011 | 0.27254 | 0.38401 | 0.22165
2021-11-09 15:30 | 0.19601 | 0.997 | 0.30116 | 0.5033 | 0.37207 | 0.21141 | 0.32025 | 0.18656
2021-11-09 15:45 | 0.30218 | 1.083 | 0.40325 | 0.40967 | 0.30254 | 0.15477 | 0.25328 | 0.14842
2021-11-09 16:00 | 0.22868 | 1.0049 | 0.40121 | 0.41594 | 0.2178 | 0.12512 | 0.18217 | 0.10651
2021-11-09 16:15 | 0.26645 | 0.90491 | 0.39611 | 0.35848 | 0.13306 | 0.086176 | 0.11106 | 0.064592
2021-11-09 16:30 | 0.28789 | 0.95523 | 0.391 | 0.40661 | 0.048315 | 0.02582 | 0.039957 | 0.022676
2021-11-09 16:45 | 0.41653 | 0.98057 | 0.28687 | 0.39727 | 0 | 0 | 0 | 0
2021-11-09 17:00 | 0.31239 | 0.97656 | 0.27462 | 0.39027 | 0 | 0 | 0 | 0
2021-11-09 17:15 | 0.26543 | 1.0684 | 1.562 | 0.59285 | 0 | 0 | 0 | 0
2021-11-09 17:30 | 0.34506 | 1.147 | 3.5323 | 0.92872 | 0 | 0 | 0 | 0
2021-11-09 17:45 | 0.44919 | 1.1878 | 3.5936 | 0.97846 | 0 | 0 | 0 | 0
2021-11-09 18:00 | 0.42469 | 1.3239 | 3.7977 | 1.0763 | 0 | 0 | 0 | 0
2021-11-09 18:15 | 0.25625 | 1.2593 | 3.8794 | 1.0288 | 0 | 0 | 0 | 0
2021-11-09 18:30 | 0.21541 | 1.3911 | 3.8692 | 1.3135 | 0 | 0 | 0 | 0
2021-11-09 18:45 | 0.32567 | 1.1718 | 3.7977 | 1.5127 | 0 | 0 | 0 | 0
2021-11-09 19:00 | 0.28177 | 1.351 | 4.1284 | 2.0205 | 0 | 0 | 0 | 0
2021-11-09 19:15 | 0.33485 | 1.6654 | 4.053 | 2.6953 | 0 | 0 | 0 | 0
2021-11-09 19:30 | 0.52678 | 1.7032 | 4.3111 | 2.9161 | 0 | 0 | 0 | 0
2021-11-09 19:45 | 0.73913 | 1.8805 | 4.3047 | 3.0023 | 0 | 0 | 0 | 0
2021-11-09 20:00 | 0.92289 | 1.287 | 0.72688 | 1.2554 | 0 | 0 | 0 | 0
2021-11-09 20:15 | 0.96781 | 1.1784 | 0.5962 | 1.1236 | 0 | 0 | 0 | 0
2021-11-09 20:30 | 0.83713 | 1.3756 | 0.5717 | 1.3464 | 0 | 0 | 0 | 0
2021-11-09 20:45 | 0.77588 | 0.88276 | 0.60437 | 0.77501 | 0 | 0 | 0 | 0
2021-11-09 21:00 | 0.67379 | 0.94808 | 0.56354 | 0.84851 | 0 | 0 | 0 | 0
2021-11-09 21:15 | 0.71054 | 1.1567 | 0.42061 | 0.8208 | 0 | 0 | 0 | 0
2021-11-09 21:30 | 1.9193 | 1.2427 | 0.31954 | 1.1681 | 0 | 0 | 0 | 0
2021-11-09 21:45 | 1.0719 | 1.001 | 0.30729 | 0.65935 | 0 | 0 | 0 | 0
2021-11-09 22:00 | 1.3476 | 1.013 | 0.31341 | 0.86412 | 0 | 0 | 0 | 0
2021-11-09 22:15 | 0.75955 | 0.85387 | 0.3369 | 0.68663 | 0 | 0 | 0 | 0
2021-11-09 22:30 | 0.47778 | 0.64672 | 0.3369 | 0.51891 | 0 | 0 | 0 | 0
2021-11-09 22:45 | 0.41653 | 0.87857 | 0.34302 | 0.55537 | 0 | 0 | 0 | 0
2021-11-09 23:00 | 0.3665 | 1.19 | 2.6952 | 2.3696 | 0 | 0 | 0 | 0
2021-11-09 23:15 | 0.3471 | 1.1514 | 1.1332 | 2.1009 | 0 | 0 | 0 | 0
2021-11-09 23:30 | 0.3471 | 1.0708 | 0.68196 | 1.7475 | 0 | 0 | 0 | 0
2021-11-09 23:45 | 0.4053 | 1.5663 | 0.39407 | 2.1334 | 0 | 0 | 0 | 0
2021-11-10 | 0.41244 | 0.73471 | 0.1807 | 1.2946 | 0 | 0 | 0 | 0
2021-11-10 00:15 | 0.41653 | 0.61033 | 0.19499 | 1.2239 | 0 | 0 | 0 | 0
2021-11-10 00:30 | 0.5227 | 0.7618 | 0.18172 | 1.2337 | 0 | 0 | 0 | 0
2021-11-10 00:45 | 0.53087 | 0.63864 | 0.1858 | 1.2099 | 0 | 0 | 0 | 0
2021-11-10 01:00 | 0.4737 | 0.58964 | 0.26237 | 1.0362 | 0 | 0 | 0 | 0
2021-11-10 01:15 | 0.40836 | 0.93002 | 0.25522 | 1.2443 | 0 | 0 | 0 | 0
2021-11-10 01:30 | 0.33281 | 0.87353 | 0.3471 | 1.1048 | 0 | 0 | 0 | 0
2021-11-10 01:45 | 0.28177 | 0.56697 | 0.30014 | 0.88308 | 0 | 0 | 0 | 0
2021-11-10 02:00 | 0.27564 | 0.6484 | 0.21337 | 0.87155 | 0 | 0 | 0 | 0
2021-11-10 02:15 | 0.29708 | 0.57302 | 0.21541 | 0.78332 | 0 | 0 | 0 | 0
2021-11-10 02:30 | 0.40019 | 0.56768 | 0.21643 | 0.74511 | 0 | 0 | 0 | 0
2021-11-10 02:45 | 0.30627 | 0.56768 | 0.22664 | 0.77034 | 0 | 0 | 0 | 0
2021-11-10 03:00 | 0.27564 | 0.56768 | 0.26543 | 0.82459 | 0 | 0 | 0 | 0
2021-11-10 03:15 | 0.27462 | 0.57302 | 0.33996 | 0.81511 | 0 | 0 | 0 | 0
2021-11-10 03:30 | 0.52678 | 0.58399 | 0.50228 | 0.83466 | 0 | 0 | 0 | 0
2021-11-10 03:45 | 0.55128 | 0.56768 | 0.4737 | 0.81803 | 0 | 0 | 0 | 0
2021-11-10 04:00 | 0.35935 | 0.56768 | 0.2297 | 0.77399 | 0 | 0 | 0 | 0
2021-11-10 04:15 | 0.39815 | 0.59986 | 0.2297 | 0.77705 | 0 | 0 | 0 | 0
2021-11-10 04:30 | 0.40427 | 0.59453 | 0.28687 | 0.78449 | 0 | 0 | 0 | 0
2021-11-10 04:45 | 0.391 | 0.59453 | 0.32873 | 0.78317 | 0 | 0 | 0 | 0
2021-11-10 05:00 | 0.27156 | 0.64179 | 0.34404 | 0.80053 | 0 | 0 | 0 | 0
2021-11-10 05:15 | 0.27768 | 0.64784 | 0.29504 | 0.82109 | 0 | 0 | 0 | 0
2021-11-10 05:30 | 0.35935 | 0.62592 | 0.2246 | 0.79557 | 0 | 0 | 0 | 0
2021-11-10 05:45 | 0.38794 | 0.60572 | 0.21133 | 0.7804 | 0 | 0 | 0 | 0
2021-11-10 06:00 | 0.27768 | 0.61106 | 0.29912 | 0.81424 | 0 | 0 | 0 | 0
2021-11-10 06:15 | 0.28585 | 0.60822 | 0.27462 | 0.78828 | 0 | 0 | 0 | 0
2021-11-10 06:30 | 0.28483 | 0.60822 | 0.22051 | 0.74773 | 0 | 0 | 0 | 0
2021-11-10 06:45 | 0.29606 | 0.60822 | 0.22766 | 0.7839 | 0.014641 | 0.022854 | 0.003151 | 0.005515
2021-11-10 07:00 | 0.44919 | 0.53619 | 0.37977 | 0.44467 | 0.049085 | 0.079909 | 0.010423 | 0.017681
2021-11-10 07:15 | 0.33894 | 0.51551 | 0.26441 | 0.35396 | 0.08353 | 0.14286 | 0.017694 | 0.029848
2021-11-10 07:30 | 0.36344 | 0.56261 | 0.69829 | 0.45663 | 0.11797 | 0.20451 | 0.024966 | 0.042015
2021-11-10 07:45 | 0.33587 | 0.55534 | 0.39713 | 0.37977 | 0.15936 | 0.23752 | 0.04991 | 0.057953
2021-11-10 08:00 | 0.3226 | 0.89468 | 1.1536 | 1.0496 | 0.21015 | 0.25466 | 0.098001 | 0.078788
2021-11-10 08:15 | 0.40427 | 0.86998 | 0.96781 | 1.0114 | 0.26094 | 0.23433 | 0.14609 | 0.099623
2021-11-10 08:30 | 0.391 | 1.1331 | 0.69829 | 1.0213 | 0.31172 | 0.26175 | 0.19418 | 0.12046
2021-11-10 08:45 | 0.37569 | 1.0499 | 0.58804 | 1.0706 | 0.34644 | 0.29061 | 0.24657 | 0.13716
2021-11-10 09:00 | 0.48186 | 0.84464 | 0.53903 | 1.0501 | 0.35935 | 0.2832 | 0.30458 | 0.14858
2021-11-10 09:15 | 1.0413 | 0.92948 | 0.44511 | 1.1414 | 0.37226 | 0.31171 | 0.3626 | 0.15999
2021-11-10 09:30 | 0.41244 | 1.1224 | 0.43286 | 1.5774 | 0.38516 | 0.33771 | 0.42061 | 0.17141
2021-11-10 09:45 | 0.48595 | 1.0335 | 0.40325 | 1.4743 | 0.41503 | 0.35541 | 0.4776 | 0.18377
2021-11-10 10:00 | 0.62479 | 1.0296 | 0.3614 | 1.0999 | 0.46792 | 0.37396 | 0.53326 | 0.19787
2021-11-10 10:15 | 0.73504 | 0.89459 | 0.50228 | 1.025 | 0.52081 | 0.35676 | 0.58891 | 0.21198
2021-11-10 10:30 | 0.69829 | 0.87522 | 0.65746 | 1.0292 | 0.57371 | 0.37376 | 0.64455 | 0.22608
2021-11-10 10:45 | 0.53495 | 0.87547 | 0.54312 | 1.104 | 0.59686 | 0.39215 | 0.67627 | 0.24086
2021-11-10 11:00 | 0.44103 | 0.82611 | 0.56354 | 1.4084 | 0.57957 | 0.39529 | 0.6765 | 0.25534
2021-11-10 11:15 | 0.56762 | 0.86731 | 0.64521 | 1.7166 | 0.56228 | 0.41457 | 0.67673 | 0.26983
2021-11-10 11:30 | 0.40121 | 0.78235 | 0.49003 | 1.5213 | 0.54498 | 0.41213 | 0.67697 | 0.28432
2021-11-10 11:45 | 0.48186 | 0.64519 | 0.38182 | 1.2137 | 0.54288 | 0.41288 | 0.6782 | 0.29411
2021-11-10 12:00 | 1.1536 | 0.78347 | 0.33281 | 1.1667 | 0.56146 | 0.4051 | 0.68076 | 0.29868
2021-11-10 12:15 | 2.6339 | 1.296 | 1.7662 | 1.8922 | 0.58005 | 0.40358 | 0.68332 | 0.30325
2021-11-10 12:30 | 2.1949 | 1.148 | 2.5522 | 1.8429 | 0.59864 | 0.38129 | 0.68588 | 0.30783
2021-11-10 12:45 | 0.8453 | 0.88447 | 2.2256 | 1.4503 | 0.61222 | 0.38354 | 0.68128 | 0.31931
2021-11-10 13:00 | 2.542 | 0.84144 | 0.95964 | 1.3562 | 0.61899 | 0.37631 | 0.66723 | 0.33823
2021-11-10 13:15 | 1.5109 | 0.88414 | 2.7156 | 1.161 | 0.62576 | 0.36838 | 0.65317 | 0.35714
2021-11-10 13:30 | 0.91472 | 1.0768 | 1.0821 | 1.1629 | 0.63253 | 0.3633 | 0.63912 | 0.37606
2021-11-10 13:45 | 0.43286 | 0.84619 | 0.65337 | 0.60291 | 0.6165 | 0.34667 | 0.62467 | 0.3784
2021-11-10 14:00 | 0.46553 | 0.83196 | 0.26748 | 0.58716 | 0.56932 | 0.35799 | 0.60969 | 0.36228
2021-11-10 14:15 | 0.55128 | 0.8222 | 0.27768 | 0.73446 | 0.52215 | 0.36208 | 0.59471 | 0.34615
2021-11-10 14:30 | 0.44919 | 0.88716 | 0.31035 | 1.1606 | 0.47497 | 0.35994 | 0.57973 | 0.33003
2021-11-10 14:45 | 0.39713 | 0.81962 | 0.36752 | 0.80782 | 0.43776 | 0.3451 | 0.54621 | 0.30893
2021-11-10 15:00 | 2.7564 | 0.92242 | 1.3986 | 0.83422 | 0.41416 | 0.33381 | 0.48816 | 0.28025
2021-11-10 15:15 | 3.6242 | 0.95275 | 0.20418 | 0.61589 | 0.39057 | 0.30799 | 0.43011 | 0.25158
2021-11-10 15:30 | 3.5833 | 0.81326 | 0.19601 | 0.47763 | 0.36698 | 0.28617 | 0.37207 | 0.2229
2021-11-10 15:45 | 3.6038 | 0.74844 | 0.30218 | 0.384 | 0.31607 | 0.25376 | 0.30254 | 0.1835
2021-11-10 16:00 | 3.7059 | 0.77849 | 0.22868 | 0.39086 | 0.22774 | 0.17685 | 0.2178 | 0.13179
2021-11-10 16:15 | 3.6854 | 0.77871 | 0.26645 | 0.33646 | 0.13941 | 0.10333 | 0.13306 | 0.080092
2021-11-10 16:30 | 3.5221 | 0.73057 | 0.28789 | 0.36898 | 0.051087 | 0.031759 | 0.048315 | 0.02839
2021-11-10 16:45 | 3.5221 | 0.81563 | 0.41653 | 0.38152 | 0 | 0 | 0 | 0
2021-11-10 17:00 | 3.5221 | 0.8108 | 0.31239 | 0.37365 | 0 | 0 | 0 | 0
2021-11-10 17:15 | 3.5017 | 0.82557 | 0.26543 | 0.5561 | 0 | 0 | 0 | 0
2021-11-10 17:30 | 3.5527 | 0.81105 | 0.34506 | 0.8946 | 0 | 0 | 0 | 0
2021-11-10 17:45 | 3.6344 | 0.80243 | 0.44919 | 0.95512 | 0 | 0 | 0 | 0
2021-11-10 18:00 | 3.614 | 0.86916 | 0.42469 | 1.025 | 0 | 0 | 0 | 0
2021-11-10 18:15 | 3.6344 | 0.84515 | 0.25625 | 0.96037 | 0 | 0 | 0 | 0
2021-11-10 18:30 | 3.7569 | 0.97482 | 0.21541 | 1.2421 | 0 | 0 | 0 | 0
2021-11-10 18:45 | 3.8488 | 0.94796 | 0.32567 | 1.4781 | 0 | 0 | 0 | 0
2021-11-10 19:00 | 3.9202 | 1.2679 | 0.28177 | 1.9726 | 0 | 0 | 0 | 0
2021-11-10 19:15 | 3.9713 | 1.3826 | 0.33485 | 2.6264 | 0 | 0 | 0 | 0
2021-11-10 19:30 | 4.0632 | 1.4259 | 0.52678 | 2.8367 | 0 | 0 | 0 | 0
2021-11-10 19:45 | 3.8284 | 1.598 | 0.73913 | 2.9703 | 0 | 0 | 0 | 0
2021-11-10 20:00 | 0.88205 | 0.97511 | 0.92289 | 1.249 | 0 | 0 | 0 | 0
2021-11-10 20:15 | 0.91064 | 1.0268 | 0.96781 | 1.0708 | 0 | 0 | 0 | 0
2021-11-10 20:30 | 1.1128 | 1.0135 | 0.83713 | 1.186 | 0 | 0 | 0 | 0
2021-11-10 20:45 | 1.8682 | 0.95486 | 0.77588 | 0.80709 | 0 | 0 | 0 | 0
2021-11-10 21:00 | 1.0821 | 0.93997 | 0.67379 | 0.85668 | 0 | 0 | 0 | 0
2021-11-10 21:15 | 1.2455 | 0.96673 | 0.71054 | 0.78463 | 0 | 0 | 0 | 0
2021-11-10 21:30 | 0.69013 | 0.93046 | 1.9193 | 1.2001 | 0 | 0 | 0 | 0
2021-11-10 21:45 | 0.5227 | 0.80231 | 1.0719 | 0.62873 | 0 | 0 | 0 | 0
2021-11-10 22:00 | 0.73913 | 0.82203 | 1.3476 | 0.87432 | 0 | 0 | 0 | 0
2021-11-10 22:15 | 0.71871 | 0.79011 | 0.75955 | 0.71871 | 0 | 0 | 0 | 0
2021-11-10 22:30 | 0.54312 | 0.59175 | 0.47778 | 0.51074 | 0 | 0 | 0 | 0
2021-11-10 22:45 | 0.54312 | 0.66759 | 0.41653 | 0.54078 | 0 | 0 | 0 | 0
2021-11-10 23:00 | 3.3485 | 1.036 | 0.3665 | 2.3637 | 0 | 0 | 0 | 0
2021-11-10 23:15 | 3.5119 | 0.94108 | 0.3471 | 2.0969 | 0 | 0 | 0 | 0
2021-11-10 23:30 | 3.4608 | 0.84225 | 0.3471 | 1.7376 | 0 | 0 | 0 | 0
2021-11-10 23:45 | 3.0831 | 0.88477 | 0.4053 | 1.7698 | 0 | 0 | 0 | 0
2021-11-11 | 1.5722 | 1.2549 | 0.41244 | 1.2882 | 0 | 0 | 0 | 0
2021-11-11 00:15 | 0.77997 | 1.0764 | 0.41653 | 1.2198 | 0 | 0 | 0 | 0
2021-11-11 00:30 | 0.70646 | 1.1753 | 0.5227 | 1.2442 | 0 | 0 | 0 | 0
2021-11-11 00:45 | 0.23991 | 1.0764 | 0.53087 | 1.2294 | 0 | 0 | 0 | 0
2021-11-11 01:00 | 0.27156 | 1.0624 | 0.4737 | 1.061 | 0 | 0 | 0 | 0
2021-11-11 01:15 | 0.40734 | 1.0186 | 0.40836 | 0.93368 | 0 | 0 | 0 | 0
2021-11-11 01:30 | 0.32669 | 1.0186 | 0.33281 | 0.92916 | 0 | 0 | 0 | 0
2021-11-11 01:45 | 0.28075 | 0.91134 | 0.28177 | 0.88628 | 0 | 0 | 0 | 0
2021-11-11 02:00 | 0.26645 | 0.90903 | 0.27564 | 0.87345 | 0 | 0 | 0 | 0
2021-11-11 02:15 | 0.2736 | 0.99665 | 0.29708 | 0.78886 | 0 | 0 | 0 | 0
2021-11-11 02:30 | 0.38896 | 0.99665 | 0.40019 | 0.76582 | 0 | 0 | 0 | 0
2021-11-11 02:45 | 0.26339 | 0.99665 | 0.30627 | 0.7629 | 0 | 0 | 0 | 0
2021-11-11 03:00 | 0.27768 | 0.91136 | 0.27564 | 0.81336 | 0 | 0 | 0 | 0
2021-11-11 03:15 | 0.32771 | 0.91821 | 0.27462 | 0.8173 | 0 | 0 | 0 | 0
2021-11-11 03:30 | 0.3614 | 0.88503 | 0.52678 | 0.87272 | 0 | 0 | 0 | 0
2021-11-11 03:45 | 0.28177 | 0.94871 | 0.55128 | 0.85974 | 0 | 0 | 0 | 0
2021-11-11 04:00 | 0.28279 | 0.96347 | 0.35935 | 0.78813 | 0 | 0 | 0 | 0
2021-11-11 04:15 | 0.28585 | 0.95332 | 0.39815 | 0.79119 | 0 | 0 | 0 | 0
2021-11-11 04:30 | 0.40836 | 0.92083 | 0.40427 | 0.79367 | 0 | 0 | 0 | 0
2021-11-11 04:45 | 0.27973 | 0.95332 | 0.391 | 0.80067 | 0 | 0 | 0 | 0
2021-11-11 05:00 | 0.28483 | 0.93567 | 0.27156 | 0.79995 | 0 | 0 | 0 | 0
2021-11-11 05:15 | 0.2981 | 1.0147 | 0.27768 | 0.81234 | 0 | 0 | 0 | 0
2021-11-11 05:30 | 0.36446 | 0.98404 | 0.35935 | 0.78799 | 0 | 0 | 0 | 0
2021-11-11 05:45 | 0.27973 | 0.987 | 0.38794 | 0.7909 | 0 | 0 | 0 | 0
2021-11-11 06:00 | 0.27258 | 0.987 | 0.27768 | 0.81074 | 0 | 0 | 0 | 0
2021-11-11 06:15 | 0.35119 | 0.99785 | 0.28585 | 0.78769 | 0 | 0 | 0 | 0
2021-11-11 06:30 | 0.342 | 0.99785 | 0.28483 | 0.74759 | 0 | 0 | 0 | 0
2021-11-11 06:45 | 0.27462 | 0.96536 | 0.29606 | 0.77748 | 0.003008 | 0.020002 | 0.014641 | 0.007497
2021-11-11 07:00 | 0.33894 | 0.64914 | 0.44919 | 0.45197 | 0.010225 | 0.055737 | 0.049085 | 0.02436
2021-11-11 07:15 | 0.33894 | 0.63658 | 0.33894 | 0.35513 | 0.017442 | 0.094638 | 0.08353 | 0.041222
2021-11-11 07:30 | 0.44511 | 0.64575 | 0.36344 | 0.45474 | 0.024659 | 0.15079 | 0.11797 | 0.058085
2021-11-11 07:45 | 0.32158 | 0.67846 | 0.33587 | 0.37744 | 0.039822 | 0.18849 | 0.15936 | 0.079501
2021-11-11 08:00 | 0.42878 | 1.2294 | 0.3226 | 1.0286 | 0.066117 | 0.2046 | 0.21015 | 0.10693
2021-11-11 08:15 | 0.48186 | 1.2146 | 0.40427 | 0.99975 | 0.092412 | 0.22493 | 0.26094 | 0.13437
2021-11-11 08:30 | 0.7718 | 1.1268 | 0.391 | 0.93543 | 0.11871 | 0.26157 | 0.31172 | 0.1618
2021-11-11 08:45 | 0.83305 | 1.2212 | 0.37569 | 1.0094 | 0.13096 | 0.26986 | 0.34644 | 0.18066
2021-11-11 09:00 | 0.71463 | 1.1757 | 0.48186 | 1.0629 | 0.1235 | 0.26264 | 0.35935 | 0.18883
2021-11-11 09:15 | 0.48186 | 1.2382 | 1.0413 | 1.2294 | 0.11604 | 0.26198 | 0.37226 | 0.19699
2021-11-11 09:30 | 0.50636 | 1.5502 | 0.41244 | 1.5442 | 0.10859 | 0.28383 | 0.38516 | 0.20516
2021-11-11 09:45 | 0.47778 | 1.3534 | 0.48595 | 1.4294 | 0.10609 | 0.28655 | 0.41503 | 0.22064
2021-11-11 10:00 | 0.65337 | 1.1749 | 0.62479 | 1.0778 | 0.11057 | 0.30314 | 0.46792 | 0.24542
2021-11-11 10:15 | 0.56762 | 1.2065 | 0.73504 | 1.0676 | 0.11505 | 0.31153 | 0.52081 | 0.27019
2021-11-11 10:30 | 0.49411 | 1.2185 | 0.69829 | 1.0543 | 0.11952 | 0.33519 | 0.57371 | 0.29497
2021-11-11 10:45 | 0.56762 | 1.2065 | 0.53495 | 1.1099 | 0.12006 | 0.35168 | 0.59686 | 0.31174
2021-11-11 11:00 | 0.93922 | 1.4924 | 0.44103 | 1.4138 | 0.11506 | 0.3518 | 0.57957 | 0.31769
2021-11-11 11:15 | 3.5017 | 1.5509 | 0.56762 | 1.7484 | 0.11006 | 0.35192 | 0.56228 | 0.32363
2021-11-11 11:30 | 1.7457 | 1.4019 | 0.40121 | 1.5353 | 0.10506 | 0.35204 | 0.54498 | 0.32957
2021-11-11 11:45 | 0.89431 | 1.2439 | 0.48186 | 1.2446 | 0.10491 | 0.35269 | 0.54288 | 0.33988
2021-11-11 12:00 | 1.2251 | 1.3644 | 1.1536 | 1.272 | 0.11162 | 0.34035 | 0.56146 | 0.35541
2021-11-11 12:15 | 0.95147 | 1.7365 | 2.6339 | 2.1973 | 0.11832 | 0.35347 | 0.58005 | 0.37093
2021-11-11 12:30 | 1.6436 | 1.8339 | 2.1949 | 2.1039 | 0.12503 | 0.35296 | 0.59864 | 0.38645
2021-11-11 12:45 | 0.76771 | 1.4507 | 0.8453 | 1.5238 | 0.12773 | 0.35805 | 0.61222 | 0.40175
2021-11-11 13:00 | 0.53495 | 1.7665 | 2.542 | 1.6789 | 0.12478 | 0.35066 | 0.61899 | 0.41658
2021-11-11 13:15 | 0.95556 | 1.3982 | 1.5109 | 1.3347 | 0.12183 | 0.34328 | 0.62576 | 0.43142
2021-11-11 13:30 | 1.0821 | 1.2401 | 0.91472 | 1.0938 | 0.11888 | 0.34395 | 0.63253 | 0.44625
2021-11-11 13:45 | 0.94331 | 1.2727 | 0.43286 | 0.61079 | 0.11291 | 0.32829 | 0.6165 | 0.44569
2021-11-11 14:00 | 0.55128 | 1.209 | 0.46553 | 0.59825 | 0.10269 | 0.30954 | 0.56932 | 0.42702
2021-11-11 14:15 | 3.1852 | 1.2372 | 0.55128 | 0.76334 | 0.092465 | 0.31308 | 0.52215 | 0.40835
2021-11-11 14:30 | 2.0418 | 1.1406 | 0.44919 | 1.1799 | 0.08224 | 0.32554 | 0.47497 | 0.38968
2021-11-11 14:45 | 2.052 | 1.1725 | 0.39713 | 0.82211 | 0.074293 | 0.31527 | 0.43776 | 0.36521
2021-11-11 15:00 | 1.1638 | 1.3327 | 2.7564 | 1.1417 | 0.069565 | 0.29264 | 0.41416 | 0.33269
2021-11-11 15:15 | 0.5227 | 1.2302 | 3.6242 | 1.031 | 0.064838 | 0.26671 | 0.39057 | 0.30017
2021-11-11 15:30 | 0.41244 | 1.2633 | 3.5833 | 0.84661 | 0.060111 | 0.25958 | 0.36698 | 0.26765
2021-11-11 15:45 | 0.29198 | 1.273 | 3.6038 | 0.83232 | 0.051409 | 0.24596 | 0.31607 | 0.22168
2021-11-11 16:00 | 0.53087 | 1.2798 | 3.7059 | 0.80242 | 0.037076 | 0.15524 | 0.22774 | 0.15934
2021-11-11 16:15 | 0.30933 | 1.2798 | 3.6854 | 0.81161 | 0.022742 | 0.09304 | 0.13941 | 0.096997
2021-11-11 16:30 | 0.28993 | 1.3165 | 3.5221 | 0.80563 | 0.008408 | 0.026184 | 0.051087 | 0.034657
2021-11-11 16:45 | 0.31954 | 1.2449 | 3.5221 | 0.82226 | 0 | 0 | 0 | 0
2021-11-11 17:00 | 0.81263 | 1.2593 | 3.5221 | 0.81876 | 0 | 0 | 0 | 0
2021-11-11 17:15 | 2.4808 | 1.2095 | 3.5017 | 0.99916 | 0 | 0 | 0 | 0
2021-11-11 17:30 | 0.36548 | 1.2397 | 3.5527 | 1.3245 | 0 | 0 | 0 | 0
2021-11-11 17:45 | 0.99231 | 1.2229 | 3.6344 | 1.4119 | 0 | 0 | 0 | 0
2021-11-11 18:00 | 1.3986 | 1.2833 | 3.614 | 1.4561 | 0 | 0 | 0 | 0
2021-11-11 18:15 | 1.0311 | 1.2289 | 3.6344 | 1.3956 | 0 | 0 | 0 | 0
2021-11-11 18:30 | 1.2047 | 1.2478 | 3.7569 | 1.6709 | 0 | 0 | 0 | 0
2021-11-11 18:45 | 3.8794 | 1.4028 | 3.8488 | 1.9363 | 0 | 0 | 0 | 0
2021-11-11 19:00 | 2.3481 | 1.4236 | 3.9202 | 2.4323 | 0 | 0 | 0 | 0
2021-11-11 19:15 | 1.3884 | 2.1042 | 3.9713 | 3.1016 | 0 | 0 | 0 | 0
2021-11-11 19:30 | 0.82897 | 2.1416 | 4.0632 | 3.3198 | 0 | 0 | 0 | 0
2021-11-11 19:45 | 0.74321 | 2.1341 | 3.8284 | 3.3713 | 0 | 0 | 0 | 0
2021-11-11 20:00 | 1.9805 | 1.2773 | 0.88205 | 1.2589 | 0 | 0 | 0 | 0
2021-11-11 20:15 | 1.1332 | 1.109 | 0.91064 | 1.0947 | 0 | 0 | 0 | 0
2021-11-11 20:30 | 1.2659 | 1.2504 | 1.1128 | 1.244 | 0 | 0 | 0 | 0
2021-11-11 20:45 | 1.1638 | 0.93334 | 1.8682 | 0.98181 | 0 | 0 | 0 | 0
2021-11-11 21:00 | 0.72279 | 0.92732 | 1.0821 | 0.9051 | 0 | 0 | 0 | 0
2021-11-11 21:15 | 0.56762 | 0.94781 | 1.2455 | 0.85755 | 0 | 0 | 0 | 0
2021-11-11 21:30 | 0.56762 | 1.1131 | 0.69013 | 1.2025 | 0 | 0 | 0 | 0
2021-11-11 21:45 | 0.55128 | 0.82727 | 0.5227 | 0.63689 | 0 | 0 | 0 | 0
2021-11-11 22:00 | 0.48595 | 0.83631 | 0.73913 | 0.90991 | 0 | 0 | 0 | 0
2021-11-11 22:15 | 0.42469 | 0.83434 | 0.71871 | 0.75546 | 0 | 0 | 0 | 0
2021-11-11 22:30 | 0.42469 | 0.62797 | 0.54312 | 0.52532 | 0 | 0 | 0 | 0
2021-11-11 22:45 | 0.42878 | 0.66897 | 0.54312 | 0.55303 | 0 | 0 | 0 | 0
2021-11-11 23:00 | 0.46961 | 2.2334 | 3.3485 | 2.7767 | 0 | 0 | 0 | 0
2021-11-11 23:15 | 0.39815 | 2.2026 | 3.5119 | 2.5333 | 0 | 0 | 0 | 0
2021-11-11 23:30 | 0.39304 | 2.3584 | 3.4608 | 2.155 | 0 | 0 | 0 | 0
2021-11-11 23:45 | 0.31341 | 2.3067 | 3.0831 | 2.1338 | 0 | 0 | 0 | 0
2021-11-12 | 0.23991 | 1.8869 | 1.5722 | 1.4571 | 0 | 0 | 0 | 0
2021-11-12 00:15 | 0.19193 | 1.894 | 0.77997 | 1.2927 | 0 | 0 | 0 | 0
2021-11-12 00:30 | 0.1858 | 1.8736 | 0.70646 | 1.3075 | 0 | 0 | 0 | 0
2021-11-12 00:45 | 0.19397 | 1.7291 | 0.23991 | 1.2258 | 0 | 0 | 0 | 0
2021-11-12 01:00 | 0.2736 | 1.6839 | 0.27156 | 1.0628 | 0 | 0 | 0 | 0
2021-11-12 01:15 | 0.27973 | 1.6228 | 0.40734 | 0.9487 | 0 | 0 | 0 | 0
2021-11-12 01:30 | 0.33996 | 1.6228 | 0.32669 | 0.92143 | 0 | 0 | 0 | 0
2021-11-12 01:45 | 0.26339 | 1.5729 | 0.28075 | 0.85289 | 0 | 0 | 0 | 0
2021-11-12 02:00 | 0.22766 | 1.5553 | 0.26645 | 0.81584 | 0 | 0 | 0 | 0
2021-11-12 02:15 | 0.22664 | 1.5413 | 0.2736 | 0.78507 | 0 | 0 | 0 | 0
2021-11-12 02:30 | 0.21949 | 1.5413 | 0.38896 | 0.77763 | 0 | 0 | 0 | 0
2021-11-12 02:45 | 0.37977 | 1.5413 | 0.26339 | 0.7578 | 0 | 0 | 0 | 0
2021-11-12 03:00 | 0.31546 | 1.4698 | 0.27768 | 0.79571 | 0 | 0 | 0 | 0
2021-11-12 03:15 | 0.22358 | 1.5413 | 0.32771 | 0.80403 | 0 | 0 | 0 | 0
2021-11-12 03:30 | 0.23072 | 1.5081 | 0.3614 | 0.86193 | 0 | 0 | 0 | 0
2021-11-12 03:45 | 0.22358 | 1.4366 | 0.28177 | 0.84734 | 0 | 0 | 0 | 0
2021-11-12 04:00 | 0.24195 | 1.4366 | 0.28279 | 0.78755 | 0 | 0 | 0 | 0
2021-11-12 04:15 | 0.34404 | 1.535 | 0.28585 | 0.79557 | 0 | 0 | 0 | 0
2021-11-12 04:30 | 0.48595 | 1.5172 | 0.40836 | 0.80461 | 0 | 0 | 0 | 0
2021-11-12 04:45 | 0.4737 | 1.4635 | 0.27973 | 0.7963 | 0 | 0 | 0 | 0
2021-11-12 05:00 | 0.23481 | 1.3673 | 0.28483 | 0.80476 | 0 | 0 | 0 | 0
2021-11-12 05:15 | 0.23889 | 1.4388 | 0.2981 | 0.79951 | 0 | 0 | 0 | 0
2021-11-12 05:30 | 0.33996 | 1.3896 | 0.36446 | 0.78784 | 0 | 0 | 0 | 0
2021-11-12 05:45 | 0.35527 | 1.4388 | 0.27973 | 0.78915 | 0 | 0 | 0 | 0
2021-11-12 06:00 | 0.38284 | 1.4073 | 0.27258 | 0.79601 | 0 | 0 | 0 | 0
2021-11-12 06:15 | 0.25216 | 1.3195 | 0.35119 | 0.78536 | 0 | 0 | 0 | 0
2021-11-12 06:30 | 0.22256 | 1.391 | 0.342 | 0.75823 | 0 | 0 | 0 | 0
2021-11-12 06:45 | 0.26441 | 1.3733 | 0.27462 | 0.77982 | 0.001572 | 0.020629 | 0.003008 | 0.006529
2021-11-12 07:00 | 0.391 | 0.61889 | 0.33894 | 0.45299 | 0.005419 | 0.06235 | 0.010225 | 0.021476
2021-11-12 07:15 | 0.28687 | 0.61999 | 0.33894 | 0.35527 | 0.009266 | 0.10201 | 0.017442 | 0.036422
2021-11-12 07:30 | 0.34098 | 0.71683 | 0.44511 | 0.45182 | 0.013113 | 0.13219 | 0.024659 | 0.051369
2021-11-12 07:45 | 0.55537 | 0.83983 | 0.32158 | 0.3684 | 0.021132 | 0.14816 | 0.039822 | 0.072976
2021-11-12 08:00 | 0.8208 | 1.1569 | 0.42878 | 1.0419 | 0.035196 | 0.14973 | 0.066117 | 0.10327
2021-11-12 08:15 | 0.50228 | 1.3826 | 0.48186 | 1.0209 | 0.049259 | 0.14302 | 0.092412 | 0.13356
2021-11-12 08:30 | 0.45328 | 1.3826 | 0.7718 | 0.98735 | 0.063323 | 0.14024 | 0.11871 | 0.16385
2021-11-12 08:45 | 0.65746 | 1.453 | 0.83305 | 1.0746 | 0.070057 | 0.16345 | 0.13096 | 0.1838
2021-11-12 09:00 | 0.55128 | 1.3937 | 0.71463 | 1.0985 | 0.066153 | 0.14998 | 0.1235 | 0.19049
2021-11-12 09:15 | 0.41244 | 1.5072 | 0.48186 | 1.2405 | 0.062248 | 0.14058 | 0.11604 | 0.19719
2021-11-12 09:30 | 0.37875 | 1.4854 | 0.50636 | 1.4663 | 0.058343 | 0.15231 | 0.10859 | 0.20388
2021-11-12 09:45 | 0.36548 | 1.4684 | 0.47778 | 1.4376 | 0.059037 | 0.15809 | 0.10609 | 0.21927
2021-11-12 10:00 | 0.2001 | 1.3937 | 0.65337 | 1.1104 | 0.066414 | 0.15182 | 0.11057 | 0.24568
2021-11-12 10:15 | 0.20724 | 1.4153 | 0.56762 | 1.0705 | 0.07379 | 0.15105 | 0.11505 | 0.27209
2021-11-12 10:30 | 0.58804 | 1.3793 | 0.49411 | 1.0432 | 0.081167 | 0.16828 | 0.11952 | 0.2985
2021-11-12 10:45 | 0.43694 | 1.436 | 0.56762 | 1.1145 | 0.088887 | 0.17656 | 0.12006 | 0.31439
2021-11-12 11:00 | 0.48186 | 1.3904 | 0.93922 | 1.1279 | 0.097107 | 0.17962 | 0.11506 | 0.31646
2021-11-12 11:15 | 0.49411 | 1.7568 | 3.5017 | 2.075 | 0.10533 | 0.1733 | 0.11006 | 0.31854
2021-11-12 11:30 | 0.42878 | 1.7113 | 1.7457 | 1.7141 | 0.11354 | 0.17336 | 0.10506 | 0.32062
2021-11-12 11:45 | 0.34608 | 1.4615 | 0.89431 | 1.268 | 0.11885 | 0.17367 | 0.10491 | 0.32547
2021-11-12 12:00 | 0.32873 | 1.4552 | 1.2251 | 1.3776 | 0.1199 | 0.1838 | 0.11162 | 0.33395
2021-11-12 12:15 | 0.3226 | 1.5046 | 0.95147 | 1.9307 | 0.12096 | 0.18449 | 0.11832 | 0.34242
2021-11-12 12:30 | 0.29912 | 1.5367 | 1.6436 | 1.891 | 0.12201 | 0.21364 | 0.12503 | 0.3509
2021-11-12 12:45 | 0.2297 | 1.3039 | 0.76771 | 1.4759 | 0.12091 | 0.2122 | 0.12773 | 0.36008
2021-11-12 13:00 | 0.37977 | 1.2958 | 0.53495 | 1.3558 | 0.11666 | 0.20783 | 0.12478 | 0.36966
2021-11-12 13:15 | 0.37875 | 1.3183 | 0.95556 | 1.3983 | 0.11241 | 0.20624 | 0.12183 | 0.37923
2021-11-12 13:30 | 0.28993 | 1.225 | 1.0821 | 1.1732 | 0.10816 | 0.17916 | 0.11888 | 0.3888
2021-11-12 13:45 | 0.25625 | 1.1389 | 0.94331 | 0.66971 | 0.10005 | 0.16953 | 0.11291 | 0.38899
2021-11-12 14:00 | 0.25625 | 1.0758 | 0.55128 | 0.60116 | 0.086299 | 0.16176 | 0.10269 | 0.37767
2021-11-12 14:15 | 0.23583 | 1.22 | 3.1852 | 1.132 | 0.072545 | 0.14952 | 0.092465 | 0.36634
2021-11-12 14:30 | 0.18785 | 1.1833 | 2.0418 | 1.0151 | 0.058792 | 0.15605 | 0.08224 | 0.35502
2021-11-12 14:45 | 0.28075 | 1.1753 | 2.052 | 0.97525 | 0.051282 | 0.1446 | 0.074293 | 0.33246
2021-11-12 15:00 | 0.5717 | 1.2352 | 1.1638 | 1.271 | 0.052911 | 0.12829 | 0.069565 | 0.29586
2021-11-12 15:15 | 0.43694 | 1.2416 | 0.5227 | 1.0705 | 0.054541 | 0.12999 | 0.064838 | 0.25926
2021-11-12 15:30 | 0.19703 | 1.1418 | 0.41244 | 0.85507 | 0.056171 | 0.14614 | 0.060111 | 0.22266
2021-11-12 15:45 | 0.2246 | 1.1976 | 0.29198 | 0.83276 | 0.051348 | 0.14988 | 0.051409 | 0.18017
2021-11-12 16:00 | 0.25931 | 1.1548 | 0.53087 | 0.84326 | 0.037064 | 0.1193 | 0.037076 | 0.12962
2021-11-12 16:15 | 0.38284 | 1.1876 | 0.30933 | 0.82095 | 0.02278 | 0.078502 | 0.022742 | 0.079078
2021-11-12 16:30 | 0.43694 | 1.1706 | 0.28993 | 0.80695 | 0.008496 | 0.025273 | 0.008408 | 0.028534
2021-11-12 16:45 | 0.3665 | 1.1138 | 0.31954 | 0.81526 | 0 | 0 | 0 | 0
2021-11-12 17:00 | 0.36242 | 1.0735 | 0.81263 | 0.89912 | 0 | 0 | 0 | 0
2021-11-12 17:15 | 0.35017 | 1.2697 | 2.4808 | 1.3183 | 0 | 0 | 0 | 0
2021-11-12 17:30 | 0.34404 | 1.2938 | 0.36548 | 1.3412 | 0 | 0 | 0 | 0
2021-11-12 17:45 | 0.44511 | 1.3382 | 0.99231 | 1.5092 | 0 | 0 | 0 | 0
2021-11-12 18:00 | 0.48595 | 1.4259 | 1.3986 | 1.604 | 0 | 0 | 0 | 0
2021-11-12 18:15 | 0.42878 | 1.3405 | 1.0311 | 1.5035 | 0 | 0 | 0 | 0
2021-11-12 18:30 | 0.42878 | 1.4456 | 1.2047 | 1.794 | 0 | 0 | 0 | 0
2021-11-12 18:45 | 0.4982 | 1.6846 | 3.8794 | 2.4048 | 0 | 0 | 0 | 0
2021-11-12 19:00 | 0.5717 | 1.7094 | 2.3481 | 2.5038 | 0 | 0 | 0 | 0
2021-11-12 19:15 | 0.62479 | 1.924 | 1.3884 | 2.6687 | 0 | 0 | 0 | 0
2021-11-12 19:30 | 0.53903 | 1.924 | 0.82897 | 2.6833 | 0 | 0 | 0 | 0
2021-11-12 19:45 | 2.3583 | 2.0339 | 0.74321 | 2.7155 | 0 | 0 | 0 | 0
2021-11-12 20:00 | 0.72688 | 1.2328 | 1.9805 | 1.3902 | 0 | 0 | 0 | 0
2021-11-12 20:15 | 1.3884 | 0.99183 | 1.1332 | 1.0568 | 0 | 0 | 0 | 0
2021-11-12 20:30 | 1.4905 | 1.1153 | 1.2659 | 1.2105 | 0 | 0 | 0 | 0
2021-11-12 20:45 | 0.63296 | 1.0938 | 1.1638 | 1.067 | 0 | 0 | 0 | 0
2021-11-12 21:00 | 0.7963 | 1.0154 | 0.72279 | 0.92727 | 0 | 0 | 0 | 0
2021-11-12 21:15 | 0.43286 | 0.92004 | 0.56762 | 0.85814 | 0 | 0 | 0 | 0
2021-11-12 21:30 | 0.45736 | 1.1425 | 0.56762 | 1.1972 | 0 | 0 | 0 | 0
2021-11-12 21:45 | 0.46961 | 0.87721 | 0.55128 | 0.64156 | 0 | 0 | 0 | 0
2021-11-12 22:00 | 0.40427 | 0.95726 | 0.48595 | 0.91341 | 0 | 0 | 0 | 0
2021-11-12 22:15 | 0.40121 | 0.90679 | 0.42469 | 0.73155 | 0 | 0 | 0 | 0
2021-11-12 22:30 | 0.40223 | 0.62531 | 0.42469 | 0.52416 | 0 | 0 | 0 | 0
2021-11-12 22:45 | 0.5227 | 0.70996 | 0.42878 | 0.55245 | 0 | 0 | 0 | 0
2021-11-12 23:00 | 3.2669 | 2.1687 | 0.46961 | 2.3625 | 0 | 0 | 0 | 0
2021-11-12 23:15 | 3.3179 | 1.915 | 0.39815 | 2.0797 | 0 | 0 | 0 | 0
2021-11-12 23:30 | 3.3383 | 1.4991 | 0.39304 | 1.6846 | 0 | 0 | 0 | 0
2021-11-12 23:45 | 3.4302 | 2.3259 | 0.31341 | 1.6623 | 0 | 0 | 0 | 0
2021-11-13 | 3.3383 | 0.87547 | 0.23991 | 0.99698 | 0 | 0 | 0 | 0
2021-11-13 00:15 | 3.4302 | 0.59562 | 0.19193 | 0.83597 | 0 | 0 | 0 | 0
2021-11-13 00:30 | 3.3383 | 0.59562 | 0.1858 | 0.85274 | 0 | 0 | 0 | 0
2021-11-13 00:45 | 3.3996 | 0.59562 | 0.19397 | 0.77224 | 0 | 0 | 0 | 0
2021-11-13 01:00 | 3.4915 | 0.60538 | 0.2736 | 0.60306 | 0 | 0 | 0 | 0
2021-11-13 01:15 | 3.4098 | 0.6054 | 0.27973 | 0.47968 | 0 | 0 | 0 | 0
2021-11-13 01:30 | 3.369 | 0.60475 | 0.33996 | 0.46684 | 0 | 0 | 0 | 0
2021-11-13 01:45 | 3.3996 | 0.5141 | 0.26339 | 0.37131 | 0 | 0 | 0 | 0
2021-11-13 02:00 | 3.4506 | 0.56207 | 0.22766 | 0.29708 | 0 | 0 | 0 | 0
2021-11-13 02:15 | 3.4098 | 0.51475 | 0.22664 | 0.3245 | 0 | 0 | 0 | 0
2021-11-13 02:30 | 3.4302 | 0.51481 | 0.21949 | 0.32479 | 0 | 0 | 0 | 0
2021-11-13 02:45 | 3.471 | 0.51481 | 0.37977 | 0.32202 | 0 | 0 | 0 | 0
2021-11-13 03:00 | 3.3996 | 0.51481 | 0.31546 | 0.34492 | 0 | 0 | 0 | 0
2021-11-13 03:15 | 3.4302 | 0.52136 | 0.22358 | 0.33719 | 0 | 0 | 0 | 0
2021-11-13 03:30 | 3.4915 | 0.51625 | 0.23072 | 0.38444 | 0 | 0 | 0 | 0
2021-11-13 03:45 | 3.42 | 0.53324 | 0.22358 | 0.38488 | 0 | 0 | 0 | 0
2021-11-13 04:00 | 3.3996 | 0.50599 | 0.24195 | 0.33208 | 0 | 0 | 0 | 0
2021-11-13 04:15 | 3.5119 | 0.52968 | 0.34404 | 0.35761 | 0 | 0 | 0 | 0
2021-11-13 04:30 | 3.42 | 0.49637 | 0.48595 | 0.37817 | 0 | 0 | 0 | 0
2021-11-13 04:45 | 3.4098 | 0.5141 | 0.4737 | 0.37977 | 0 | 0 | 0 | 0
2021-11-13 05:00 | 3.4915 | 0.56136 | 0.23481 | 0.3439 | 0 | 0 | 0 | 0
2021-11-13 05:15 | 3.471 | 0.5826 | 0.23889 | 0.33485 | 0 | 0 | 0 | 0
2021-11-13 05:30 | 3.3996 | 0.49637 | 0.33996 | 0.34346 | 0 | 0 | 0 | 0
2021-11-13 05:45 | 3.42 | 0.5141 | 0.35527 | 0.33092 | 0 | 0 | 0 | 0
2021-11-13 06:00 | 3.42 | 0.52968 | 0.38284 | 0.35629 | 0 | 0 | 0 | 0
2021-11-13 06:15 | 3.5221 | 0.51212 | 0.25216 | 0.33865 | 0 | 0 | 0 | 0
2021-11-13 06:30 | 3.4506 | 0.51212 | 0.22256 | 0.30729 | 0 | 0 | 0 | 0
2021-11-13 06:45 | 2.5318 | 0.49439 | 0.26441 | 0.31444 | 0.001444 | 0.023893 | 0.001572 | 0.006465
2021-11-13 07:00 | 0.37773 | 0.57432 | 0.391 | 0.41259 | 0.005051 | 0.063186 | 0.005419 | 0.021342
2021-11-13 07:15 | 0.36038 | 0.53222 | 0.28687 | 0.34317 | 0.008659 | 0.1067 | 0.009266 | 0.036218
2021-11-13 07:30 | 0.4053 | 0.62095 | 0.34098 | 0.44657 | 0.012266 | 0.14667 | 0.013113 | 0.051095
2021-11-13 07:45 | 0.80855 | 0.76317 | 0.55537 | 0.39698 | 0.020304 | 0.18452 | 0.021132 | 0.072465
2021-11-13 08:00 | 1.9295 | 0.9564 | 0.8208 | 0.69538 | 0.034988 | 0.1709 | 0.035196 | 0.10251
2021-11-13 08:15 | 0.70238 | 0.95176 | 0.50228 | 0.5822 | 0.049672 | 0.16161 | 0.049259 | 0.13255
2021-11-13 08:30 | 0.66971 | 0.94619 | 0.45328 | 0.53874 | 0.064355 | 0.18078 | 0.063323 | 0.1626
2021-11-13 08:45 | 0.68604 | 1.0975 | 0.65746 | 0.57229 | 0.070756 | 0.16642 | 0.070057 | 0.18277
2021-11-13 09:00 | 0.73504 | 1.1433 | 0.55128 | 0.63471 | 0.064717 | 0.16141 | 0.066153 | 0.18991
2021-11-13 09:15 | 0.78813 | 1.1273 | 0.41244 | 0.75838 | 0.058677 | 0.16028 | 0.062248 | 0.19704
2021-11-13 09:30 | 0.60437 | 1.1771 | 0.37875 | 0.97641 | 0.052638 | 0.18025 | 0.058343 | 0.20418
2021-11-13 09:45 | 0.49003 | 1.1069 | 0.36548 | 0.97496 | 0.068131 | 0.20467 | 0.059037 | 0.21899
2021-11-13 10:00 | 0.53087 | 1.0733 | 0.2001 | 0.61983 | 0.11601 | 0.22561 | 0.066414 | 0.24386
2021-11-13 10:15 | 0.69829 | 1.0957 | 0.20724 | 0.57506 | 0.16389 | 0.24877 | 0.07379 | 0.26873
2021-11-13 10:30 | 0.78405 | 1.0323 | 0.58804 | 0.59197 | 0.21177 | 0.27804 | 0.081167 | 0.2936
2021-11-13 10:45 | 0.91472 | 1.1463 | 0.43694 | 0.65629 | 0.22956 | 0.29172 | 0.088887 | 0.30833
2021-11-13 11:00 | 0.49003 | 1.1415 | 0.48186 | 0.698 | 0.20203 | 0.29182 | 0.097107 | 0.30971
2021-11-13 11:15 | 0.56762 | 1.4475 | 0.49411 | 1.6439 | 0.1745 | 0.29192 | 0.10533 | 0.31109
2021-11-13 11:30 | 0.58804 | 1.321 | 0.42878 | 1.2736 | 0.14697 | 0.26802 | 0.11354 | 0.31246
2021-11-13 11:45 | 0.27462 | 0.95803 | 0.34608 | 0.82445 | 0.12492 | 0.2685 | 0.11885 | 0.31588
2021-11-13 12:00 | 0.64112 | 0.93817 | 0.32873 | 0.91997 | 0.11114 | 0.29366 | 0.1199 | 0.32194
2021-11-13 12:15 | 0.3369 | 1.1503 | 0.3226 | 1.4532 | 0.097359 | 0.31517 | 0.12096 | 0.328
2021-11-13 12:30 | 0.38182 | 1.1303 | 0.29912 | 1.4029 | 0.08358 | 0.31939 | 0.12201 | 0.33406
2021-11-13 12:45 | 0.40121 | 1.1147 | 0.2297 | 1.0479 | 0.069825 | 0.31082 | 0.12091 | 0.341
2021-11-13 13:00 | 0.42878 | 1.079 | 0.37977 | 1.1139 | 0.056107 | 0.28449 | 0.11666 | 0.34843
2021-11-13 13:15 | 0.3614 | 1.1319 | 0.37875 | 1.1812 | 0.042388 | 0.26164 | 0.11241 | 0.35586
2021-11-13 13:30 | 0.27462 | 0.99086 | 0.28993 | 0.67788 | 0.028669 | 0.25601 | 0.10816 | 0.3633
2021-11-13 13:45 | 0.2297 | 1.1516 | 0.25625 | 0.5488 | 0.028841 | 0.25022 | 0.10005 | 0.3645
2021-11-13 14:00 | 0.21745 | 1.1138 | 0.25625 | 0.5246 | 0.050024 | 0.22611 | 0.086299 | 0.35766
2021-11-13 14:15 | 0.3369 | 1.1087 | 0.23583 | 1.0712 | 0.071207 | 0.22847 | 0.072545 | 0.35083
2021-11-13 14:30 | 0.24399 | 1.0455 | 0.18785 | 0.94856 | 0.09239 | 0.23698 | 0.058792 | 0.34399
2021-11-13 14:45 | 0.21949 | 1.1123 | 0.28075 | 0.92143 | 0.098498 | 0.22528 | 0.051282 | 0.32551
2021-11-13 15:00 | 0.2052 | 1.1782 | 0.5717 | 1.2564 | 0.081769 | 0.18893 | 0.052911 | 0.29277
2021-11-13 15:15 | 0.32771 | 1.1133 | 0.43694 | 1.0384 | 0.065041 | 0.17233 | 0.054541 | 0.26003
2021-11-13 15:30 | 0.32465 | 0.81646 | 0.19703 | 0.79513 | 0.048312 | 0.18956 | 0.056171 | 0.22729
2021-11-13 15:45 | 0.22358 | 0.83801 | 0.2246 | 0.79192 | 0.034433 | 0.17567 | 0.051348 | 0.18623
2021-11-13 16:00 | 0.24093 | 0.85411 | 0.25931 | 0.8227 | 0.024876 | 0.12099 | 0.037064 | 0.134
2021-11-13 16:15 | 0.25522 | 0.79407 | 0.38284 | 0.80447 | 0.01532 | 0.080152 | 0.02278 | 0.081778
2021-11-13 16:30 | 0.33792 | 0.86206 | 0.43694 | 0.78828 | 0.005763 | 0.027358 | 0.008496 | 0.029553
2021-11-13 16:45 | 0.64112 | 0.89421 | 0.3665 | 0.78303 | 0 | 0 | 0 | 0
2021-11-13 17:00 | 0.25727 | 0.82792 | 0.36242 | 0.84997 | 0 | 0 | 0 | 0
2021-11-13 17:15 | 0.27054 | 1.2259 | 0.35017 | 1.265 | 0 | 0 | 0 | 0
2021-11-13 17:30 | 0.42061 | 0.99354 | 0.34404 | 1.2818 | 0 | 0 | 0 | 0
2021-11-13 17:45 | 0.30525 | 1.2648 | 0.44511 | 1.4573 | 0 | 0 | 0 | 0
2021-11-13 18:00 | 0.40223 | 1.4003 | 0.48595 | 1.6022 | 0 | 0 | 0 | 0
2021-11-13 18:15 | 0.38386 | 1.2026 | 0.42878 | 1.4982 | 0 | 0 | 0 | 0
2021-11-13 18:30 | 0.4982 | 1.3915 | 0.42878 | 1.7882 | 0 | 0 | 0 | 0
2021-11-13 18:45 | 0.48186 | 1.6413 | 0.4982 | 2.385 | 0 | 0 | 0 | 0
2021-11-13 19:00 | 0.44919 | 1.7604 | 0.5717 | 2.2427 | 0 | 0 | 0 | 0
2021-11-13 19:15 | 0.46144 | 1.5892 | 0.62479 | 2.1936 | 0 | 0 | 0 | 0
2021-11-13 19:30 | 0.51045 | 1.6544 | 0.53903 | 2.1916 | 0 | 0 | 0 | 0
2021-11-13 19:45 | 0.49003 | 1.8529 | 2.3583 | 2.4865 | 0 | 0 | 0 | 0
2021-11-13 20:00 | 0.43694 | 1.1946 | 0.72688 | 1.3785 | 0 | 0 | 0 | 0
2021-11-13 20:15 | 0.33383 | 1.1795 | 1.3884 | 1.1717 | 0 | 0 | 0 | 0
2021-11-13 20:30 | 0.3175 | 1.1135 | 1.4905 | 1.1959 | 0 | 0 | 0 | 0
2021-11-13 20:45 | 0.31444 | 1.0765 | 0.63296 | 0.95177 | 0 | 0 | 0 | 0
2021-11-13 21:00 | 0.33077 | 0.86494 | 0.7963 | 0.70704 | 0 | 0 | 0 | 0
2021-11-13 21:15 | 0.42469 | 0.85391 | 0.43286 | 0.67788 | 0 | 0 | 0 | 0
2021-11-13 21:30 | 0.44511 | 1.0276 | 0.45736 | 1.1797 | 0 | 0 | 0 | 0
2021-11-13 21:45 | 0.51045 | 0.84066 | 0.46961 | 0.61298 | 0 | 0 | 0 | 0
2021-11-13 22:00 | 0.52678 | 0.87635 | 0.40427 | 0.63573 | 0 | 0 | 0 | 0
2021-11-13 22:15 | 0.55128 | 0.65737 | 0.40121 | 0.53655 | 0 | 0 | 0 | 0
2021-11-13 22:30 | 0.60029 | 0.59175 | 0.40223 | 0.47253 | 0 | 0 | 0 | 0
2021-11-13 22:45 | 0.5962 | 0.60843 | 0.5227 | 0.49178 | 0 | 0 | 0 | 0
2021-11-13 23:00 | 0.58804 | 1.9791 | 3.2669 | 2.3246 | 0 | 0 | 0 | 0
2021-11-13 23:15 | 0.51045 | 1.9082 | 3.3179 | 2.0972 | 0 | 0 | 0 | 0
2021-11-13 23:30 | 0.40325 | 1.9245 | 3.3383 | 1.7561 | 0 | 0 | 0 | 0
2021-11-13 23:45 | 0.34608 | 2.1424 | 3.4302 | 1.6623 | 0 | 0 | 0 | 0
2021-11-14 | 0.25318 | 2.0789 | 3.3383 | 1.3805 | 0 | 0 | 0 | 0
2021-11-14 00:15 | 0.2052 | 2.0789 | 3.4302 | 1.2838 | 0 | 0 | 0 | 0
2021-11-14 00:30 | 0.24502 | 1.9708 | 3.3383 | 1.2872 | 0 | 0 | 0 | 0
2021-11-14 00:45 | 0.32975 | 1.8599 | 3.3996 | 1.2153 | 0 | 0 | 0 | 0
2021-11-14 01:00 | 0.30321 | 1.1585 | 3.4915 | 1.0429 | 0 | 0 | 0 | 0
2021-11-14 01:15 | 0.22868 | 1.1751 | 3.4098 | 0.9032 | 0 | 0 | 0 | 0
2021-11-14 01:30 | 0.23685 | 1.1751 | 3.369 | 0.89883 | 0 | 0 | 0 | 0
2021-11-14 01:45 | 0.2297 | 0.97306 | 3.3996 | 0.80665 | 0 | 0 | 0 | 0
2021-11-14 02:00 | 0.23787 | 0.86448 | 3.4506 | 0.73315 | 0 | 0 | 0 | 0
2021-11-14 02:15 | 0.34302 | 0.85471 | 3.4098 | 0.74803 | 0 | 0 | 0 | 0
2021-11-14 02:30 | 0.29096 | 0.84587 | 3.4302 | 0.76626 | 0 | 0 | 0 | 0
2021-11-14 02:45 | 0.2297 | 0.84587 | 3.471 | 0.76713 | 0 | 0 | 0 | 0
2021-11-14 03:00 | 0.2297 | 0.87133 | 3.3996 | 0.77544 | 0 | 0 | 0 | 0
2021-11-14 03:15 | 0.24297 | 0.84587 | 3.4302 | 0.76713 | 0 | 0 | 0 | 0
2021-11-14 03:30 | 0.30423 | 0.8342 | 3.4915 | 0.83436 | 0 | 0 | 0 | 0
2021-11-14 03:45 | 0.28279 | 0.83448 | 3.42 | 0.82153 | 0 | 0 | 0 | 0
2021-11-14 04:00 | 0.23991 | 0.8342 | 3.3996 | 0.76013 | 0 | 0 | 0 | 0
2021-11-14 04:15 | 0.24093 | 0.82405 | 3.5119 | 0.79455 | 0 | 0 | 0 | 0
2021-11-14 04:30 | 0.33281 | 0.79749 | 3.42 | 0.8157 | 0 | 0 | 0 | 0
2021-11-14 04:45 | 0.24706 | 0.82401 | 3.4098 | 0.81059 | 0 | 0 | 0 | 0
2021-11-14 05:00 | 0.23481 | 0.83782 | 3.4915 | 0.79046 | 0 | 0 | 0 | 0
2021-11-14 05:15 | 0.26033 | 0.8474 | 3.471 | 0.76421 | 0 | 0 | 0 | 0
2021-11-14 05:30 | 0.32771 | 0.8199 | 3.3996 | 0.77428 | 0 | 0 | 0 | 0
2021-11-14 05:45 | 0.60029 | 0.82879 | 3.42 | 0.7664 | 0 | 0 | 0 | 0
2021-11-14 06:00 | 0.34302 | 0.83763 | 3.42 | 0.78244 | 0 | 0 | 0 | 0
2021-11-14 06:15 | 0.27768 | 0.88858 | 3.5221 | 0.79046 | 0 | 0 | 0 | 0
2021-11-14 06:30 | 0.35119 | 0.84748 | 3.4506 | 0.74569 | 0 | 0 | 0 | 0
2021-11-14 06:45 | 0.36446 | 0.85923 | 2.5318 | 0.62114 | 0 | 0.042434 | 0.001444 | 0.005838
2021-11-14 07:00 | 0.35935 | 0.60238 | 0.37773 | 0.39654 | 0 | 0.13447 | 0.005051 | 0.019411
2021-11-14 07:15 | 0.24706 | 0.63582 | 0.36038 | 0.33792 | 0 | 0.2167 | 0.008659 | 0.032984
2021-11-14 07:30 | 0.30627 | 0.68908 | 0.4053 | 0.44496 | 0 | 0.32887 | 0.012266 | 0.046557
2021-11-14 07:45 | 0.30218 | 0.75237 | 0.80855 | 0.45576 | 0.000258 | 0.3686 | 0.020304 | 0.067515
2021-11-14 08:00 | 0.36242 | 1.1927 | 1.9295 | 0.90568 | 0.000915 | 0.34885 | 0.034988 | 0.098404
2021-11-14 08:15 | 0.28075 | 1.081 | 0.70238 | 0.60962 | 0.001572 | 0.30179 | 0.049672 | 0.12929
2021-11-14 08:30 | 0.30321 | 1.0617 | 0.66971 | 0.56908 | 0.00223 | 0.32655 | 0.064355 | 0.16018
2021-11-14 08:45 | 0.64929 | 1.09 | 0.68604 | 0.56295 | 0.003328 | 0.31183 | 0.070756 | 0.18142
2021-11-14 09:00 | 0.75955 | 1.2195 | 0.73504 | 0.64287 | 0.00511 | 0.30835 | 0.064717 | 0.18951
2021-11-14 09:15 | 0.89431 | 1.2515 | 0.78813 | 0.59095 | 0.006892 | 0.30241 | 0.058677 | 0.19761
2021-11-14 09:30 | 0.42878 | 1.312 | 0.60437 | 0.91545 | 0.008675 | 0.33902 | 0.052638 | 0.2057
2021-11-14 09:45 | 0.35119 | 1.2997 | 0.49003 | 0.92712 | 0.013157 | 0.38495 | 0.068131 | 0.22304
2021-11-14 10:00 | 1.5416 | 1.1076 | 0.53087 | 0.54107 | 0.021841 | 0.44947 | 0.11601 | 0.25328
2021-11-14 10:15 | 0.73504 | 1.1395 | 0.69829 | 0.57214 | 0.030525 | 0.47358 | 0.16389 | 0.28352
2021-11-14 10:30 | 3.2771 | 1.2653 | 0.78405 | 0.61239 | 0.03921 | 0.52789 | 0.21177 | 0.31376
2021-11-14 10:45 | 1.2149 | 1.2337 | 0.91472 | 0.66271 | 0.047673 | 0.55387 | 0.22956 | 0.33072
2021-11-14 11:00 | 0.47778 | 1.2277 | 0.49003 | 0.59737 | 0.055792 | 0.56037 | 0.20203 | 0.32924
2021-11-14 11:15 | 0.27462 | 1.4816 | 0.56762 | 1.2831 | 0.063912 | 0.56605 | 0.1745 | 0.32776
2021-11-14 11:30 | 0.35833 | 1.28 | 0.58804 | 0.977 | 0.072031 | 0.60717 | 0.14697 | 0.32627
2021-11-14 11:45 | 0.32465 | 1.3787 | 0.27462 | 0.77326 | 0.085339 | 0.60828 | 0.12492 | 0.32537
2021-11-14 12:00 | 0.32056 | 1.2355 | 0.64112 | 0.93281 | 0.10675 | 0.62816 | 0.11114 | 0.32562
2021-11-14 12:15 | 2.2868 | 1.3112 | 0.3369 | 1.4319 | 0.12815 | 0.63053 | 0.097359 | 0.32588
2021-11-14 12:30 | 3.7059 | 1.3093 | 0.38182 | 1.3833 | 0.14956 | 0.63289 | 0.08358 | 0.32613
2021-11-14 12:45 | 3.5527 | 1.1981 | 0.40121 | 1.0288 | 0.15234 | 0.58116 | 0.069825 | 0.32299
2021-11-14 13:00 | 3.4302 | 1.2488 | 0.42878 | 1.0953 | 0.12599 | 0.57757 | 0.056107 | 0.31526
2021-11-14 13:15 | 3.4098 | 1.2693 | 0.3614 | 1.0228 | 0.099646 | 0.56541 | 0.042388 | 0.30753
2021-11-14 13:30 | 6.2572 | 1.2273 | 0.27462 | 0.64477 | 0.073298 | 0.55324 | 0.028669 | 0.2998
2021-11-14 13:45 | 3.5629 | 1.3418 | 0.2297 | 0.48536 | 0.060777 | 0.50296 | 0.028841 | 0.2938
2021-11-14 14:00 | 4.6439 | 1.3583 | 0.21745 | 0.4139 | 0.069904 | 0.50554 | 0.050024 | 0.28992
2021-11-14 14:15 | 3.6038 | 1.2065 | 0.3369 | 0.82911 | 0.079031 | 0.50127 | 0.071207 | 0.28603
2021-11-14 14:30 | 3.6446 | 1.2152 | 0.24399 | 0.67131 | 0.088157 | 0.46401 | 0.09239 | 0.28214
2021-11-14 14:45 | 3.5527 | 1.2373 | 0.21949 | 0.6611 | 0.087252 | 0.41305 | 0.098498 | 0.26702
2021-11-14 15:00 | 5.8874 | 1.2383 | 0.2052 | 0.98239 | 0.070619 | 0.35945 | 0.081769 | 0.23743
2021-11-14 15:15 | 5.1274 | 1.1514 | 0.32771 | 0.87666 | 0.053985 | 0.34527 | 0.065041 | 0.20785
2021-11-14 15:30 | 3.5629 | 1.0928 | 0.32465 | 0.7928 | 0.037352 | 0.37198 | 0.048312 | 0.17826
2021-11-14 15:45 | 3.5527 | 1.136 | 0.22358 | 0.78201 | 0.024545 | 0.33622 | 0.034433 | 0.14425
2021-11-14 16:00 | 3.3894 | 1.1267 | 0.24093 | 0.81599 | 0.017748 | 0.28528 | 0.024876 | 0.10389
2021-11-14 16:15 | 4.1951 | 1.1461 | 0.25522 | 0.8014 | 0.010952 | 0.17567 | 0.01532 | 0.063524
2021-11-14 16:30 | 5.7449 | 1.1635 | 0.33792 | 0.79688 | 0.004155 | 0.059083 | 0.005763 | 0.023162
2021-11-14 16:45 | 4.9473 | 1.1225 | 0.64112 | 0.83509 | 0 | 0 | 0 | 0
2021-11-14 17:00 | 3.4506 | 1.0556 | 0.25727 | 0.83174 | 0 | 0 | 0 | 0
2021-11-14 17:15 | 3.4506 | 1.2146 | 0.27054 | 1.2481 | 0 | 0 | 0 | 0
2021-11-14 17:30 | 3.665 | 1.2194 | 0.42061 | 1.2818 | 0 | 0 | 0 | 0
2021-11-14 17:45 | 3.7365 | 1.2015 | 0.30525 | 1.4058 | 0 | 0 | 0 | 0
2021-11-14 18:00 | 3.8896 | 1.6596 | 0.40223 | 1.5611 | 0 | 0 | 0 | 0
2021-11-14 18:15 | 3.9815 | 1.2627 | 0.38386 | 1.4574 | 0 | 0 | 0 | 0
2021-11-14 18:30 | 3.9611 | 1.2367 | 0.4982 | 1.4918 | 0 | 0 | 0 | 0
2021-11-14 18:45 | 3.8284 | 1.3538 | 0.48186 | 1.9054 | 0 | 0 | 0 | 0
2021-11-14 19:00 | 3.8998 | 1.3276 | 0.44919 | 1.7513 | 0 | 0 | 0 | 0
2021-11-14 19:15 | 5.4934 | 1.6919 | 0.46144 | 1.6562 | 0 | 0 | 0 | 0
2021-11-14 19:30 | 4.9049 | 1.7431 | 0.51045 | 1.6805 | 0 | 0 | 0 | 0
2021-11-14 19:45 | 3.7977 | 1.7531 | 0.49003 | 1.9555 | 0 | 0 | 0 | 0
2021-11-14 20:00 | 1.6334 | 1.1857 | 0.43694 | 1.1419 | 0 | 0 | 0 | 0
2021-11-14 20:15 | 2.5931 | 1.1144 | 0.33383 | 1.0429 | 0 | 0 | 0 | 0
2021-11-14 20:30 | 2.5727 | 1.085 | 0.3175 | 1.0283 | 0 | 0 | 0 | 0
2021-11-14 20:45 | 2.6747 | 0.92145 | 0.31444 | 0.8666 | 0 | 0 | 0 | 0
2021-11-14 21:00 | 2.3072 | 0.79687 | 0.33077 | 0.68312 | 0 | 0 | 0 | 0
2021-11-14 21:15 | 2.1643 | 0.90581 | 0.42469 | 0.65629 | 0 | 0 | 0 | 0
2021-11-14 21:30 | 1.9295 | 1.2302 | 0.44511 | 1.1681 | 0 | 0 | 0 | 0
2021-11-14 21:45 | 0.5962 | 0.88124 | 0.51045 | 0.60656 | 0 | 0 | 0 | 0
2021-11-14 22:00 | 0.53087 | 0.8204 | 0.52678 | 0.63339 | 0 | 0 | 0 | 0
2021-11-14 22:15 | 0.46961 | 0.67603 | 0.55128 | 0.5488 | 0 | 0 | 0 | 0
2021-11-14 22:30 | 0.38386 | 0.63812 | 0.60029 | 0.49236 | 0 | 0 | 0 | 0
2021-11-14 22:45 | 0.40019 | 0.63812 | 0.5962 | 0.5087 | 0 | 0 | 0 | 0
2021-11-14 23:00 | 3.2464 | 1.6397 | 0.58804 | 1.9229 | 0 | 0 | 0 | 0
2021-11-14 23:15 | 3.6242 | 1.5044 | 0.51045 | 1.6553 | 0 | 0 | 0 | 0
2021-11-14 23:30 | 3.5119 | 1.1749 | 0.40325 | 1.3032 | 0 | 0 | 0 | 0
2021-11-14 23:45 | 3.471 | 1.0254 | 0.34608 | 1.2217 | 0 | 0 | 0 | 0
2021-11-15 | 3.369 | 1.2442 | 0.25318 | 0.92376 | 0 | 0 | 0 | 0
2021-11-15 00:15 | 2.2868 | 0.86188 | 0.2052 | 0.82022 | 0 | 0 | 0 | 0
2021-11-15 00:30 | 1.2659 | 1.2442 | 0.24502 | 0.82051 | 0 | 0 | 0 | 0
2021-11-15 00:45 | 0.55128 | 1.2695 | 0.32975 | 0.78113 | 0 | 0 | 0 | 0
2021-11-15 01:00 | 0.86572 | 0.83391 | 0.30321 | 0.81205 | 0 | 0 | 0 | 0
2021-11-15 01:15 | 0.34915 | 0.81637 | 0.22868 | 0.7769 | 0 | 0 | 0 | 0
2021-11-15 01:30 | 0.37365 | 0.80132 | 0.23685 | 0.76932 | 0 | 0 | 0 | 0
2021-11-15 01:45 | 0.2685 | 0.81615 | 0.2297 | 0.72688 | 0 | 0 | 0 | 0
2021-11-15 02:00 | 0.24195 | 0.89599 | 0.23787 | 0.71463 | 0 | 0 | 0 | 0
2021-11-15 02:15 | 0.24502 | 0.8535 | 0.34302 | 0.7403 | 0 | 0 | 0 | 0
2021-11-15 02:30 | 0.25931 | 0.78751 | 0.29096 | 0.75401 | 0 | 0 | 0 | 0
2021-11-15 02:45 | 0.30014 | 0.76737 | 0.2297 | 0.74511 | 0 | 0 | 0 | 0
2021-11-15 03:00 | 0.34915 | 0.79181 | 0.2297 | 0.73942 | 0 | 0 | 0 | 0
2021-11-15 03:15 | 0.26237 | 0.69012 | 0.24297 | 0.74905 | 0 | 0 | 0 | 0
2021-11-15 03:30 | 0.23276 | 0.63585 | 0.30423 | 0.82124 | 0 | 0 | 0 | 0
2021-11-15 03:45 | 0.23174 | 0.63585 | 0.28279 | 0.79542 | 0 | 0 | 0 | 0
2021-11-15 04:00 | 0.23174 | 0.66029 | 0.23991 | 0.73548 | 0 | 0 | 0 | 0
2021-11-15 04:15 | 0.30423 | 0.58863 | 0.24093 | 0.77267 | 0 | 0 | 0 | 0
2021-11-15 04:30 | 0.33587 | 0.56419 | 0.33281 | 0.81059 | 0 | 0 | 0 | 0
2021-11-15 04:45 | 0.23685 | 0.56419 | 0.24706 | 0.78055 | 0 | 0 | 0 | 0
2021-11-15 05:00 | 0.2246 | 0.73367 | 0.23481 | 0.75517 | 0 | 0 | 0 | 0
2021-11-15 05:15 | 0.24706 | 0.73579 | 0.26033 | 0.74861 | 0 | 0 | 0 | 0
2021-11-15 05:30 | 0.31239 | 0.56808 | 0.32771 | 0.76392 | 0 | 0 | 0 | 0
2021-11-15 05:45 | 0.33996 | 0.59671 | 0.60029 | 0.79819 | 0 | 0 | 0 | 0
2021-11-15 06:00 | 0.28687 | 0.62614 | 0.34302 | 0.77311 | 0 | 0 | 0 | 0
2021-11-15 06:15 | 0.21745 | 0.53249 | 0.27768 | 0.75955 | 0 | 0 | 0 | 0
2021-11-15 06:30 | 0.26033 | 0.56113 | 0.35119 | 0.74292 | 0 | 0 | 0 | 0
2021-11-15 06:45 | 0.32669 | 0.57137 | 0.36446 | 0.61764 | 3.3e-05 | 0.024863 | 0 | 0.005827
2021-11-15 07:00 | 0.34302 | 0.52594 | 0.35935 | 0.391 | 0.000118 | 0.069539 | 0 | 0.019375
2021-11-15 07:15 | 0.25114 | 0.49053 | 0.24706 | 0.31079 | 0.000203 | 0.1012 | 0 | 0.032923
2021-11-15 07:30 | 0.31137 | 0.52553 | 0.30627 | 0.42455 | 0.000288 | 0.14249 | 0 | 0.046472
2021-11-15 07:45 | 0.26237 | 0.57444 | 0.30218 | 0.44001 | 0.002186 | 0.16271 | 0.000258 | 0.066694
2021-11-15 08:00 | 1.2455 | 0.78774 | 0.36242 | 0.7839 | 0.006998 | 0.13545 | 0.000915 | 0.095987
2021-11-15 08:15 | 0.69829 | 0.93106 | 0.28075 | 0.5418 | 0.01181 | 0.11044 | 0.001572 | 0.12528
2021-11-15 08:30 | 0.35833 | 0.93129 | 0.30321 | 0.5243 | 0.016622 | 0.11807 | 0.00223 | 0.15457
2021-11-15 08:45 | 0.89431 | 0.78965 | 0.64929 | 0.5927 | 0.019311 | 0.10919 | 0.003328 | 0.17445
2021-11-15 09:00 | 0.69421 | 1.1121 | 0.75955 | 0.69188 | 0.018584 | 0.12111 | 0.00511 | 0.18148
2021-11-15 09:15 | 0.4737 | 0.95273 | 0.89431 | 0.65162 | 0.017856 | 0.12671 | 0.006892 | 0.18851
2021-11-15 09:30 | 0.55128 | 1.1966 | 0.42878 | 0.79003 | 0.017129 | 0.133 | 0.008675 | 0.19554
2021-11-15 09:45 | 0.56354 | 1.1755 | 0.35119 | 0.66227 | 0.019071 | 0.16471 | 0.013157 | 0.2123
2021-11-15 10:00 | 0.56762 | 1.0012 | 1.5416 | 0.66154 | 0.025316 | 0.19129 | 0.021841 | 0.24265
2021-11-15 10:15 | 0.57987 | 0.82167 | 0.73504 | 0.57039 | 0.03156 | 0.22306 | 0.030525 | 0.27301
2021-11-15 10:30 | 0.49411 | 1.0469 | 3.2771 | 0.98604 | 0.037805 | 0.2682 | 0.03921 | 0.30336
2021-11-15 10:45 | 0.37263 | 0.82432 | 1.2149 | 0.66417 | 0.042152 | 0.2814 | 0.047673 | 0.32119
2021-11-15 11:00 | 1.7968 | 0.95697 | 0.47778 | 0.5542 | 0.043436 | 0.28882 | 0.055792 | 0.32149
2021-11-15 11:15 | 0.46144 | 0.96142 | 0.27462 | 0.95191 | 0.044721 | 0.28892 | 0.063912 | 0.32178
2021-11-15 11:30 | 0.37977 | 0.86117 | 0.35833 | 0.64608 | 0.046006 | 0.2901 | 0.072031 | 0.32207
2021-11-15 11:45 | 0.32771 | 0.99203 | 0.32465 | 0.42878 | 0.046062 | 0.29063 | 0.085339 | 0.32434
2021-11-15 12:00 | 0.34608 | 0.75402 | 0.32056 | 0.61691 | 0.044133 | 0.29173 | 0.10675 | 0.32974
2021-11-15 12:15 | 0.23787 | 1.1369 | 2.2868 | 1.3473 | 0.042203 | 0.27808 | 0.12815 | 0.33513
2021-11-15 12:30 | 0.19601 | 1.2334 | 3.7059 | 1.8532 | 0.040273 | 0.27869 | 0.14956 | 0.34053
2021-11-15 12:45 | 0.19703 | 1.1883 | 3.5527 | 1.4698 | 0.037242 | 0.27681 | 0.15234 | 0.33927
2021-11-15 13:00 | 0.20214 | 1.3061 | 3.4302 | 1.5293 | 0.03243 | 0.26871 | 0.12599 | 0.32853
2021-11-15 13:15 | 0.23787 | 1.1089 | 3.4098 | 1.4492 | 0.027618 | 0.28462 | 0.099646 | 0.31777
2021-11-15 13:30 | 0.30218 | 0.94175 | 6.2572 | 1.4757 | 0.022806 | 0.27847 | 0.073298 | 0.30703
2021-11-15 13:45 | 2.1235 | 0.83088 | 3.5629 | 0.93135 | 0.020244 | 0.27118 | 0.060777 | 0.29728
2021-11-15 14:00 | 3.3281 | 1.1884 | 4.6439 | 1.0137 | 0.021329 | 0.25046 | 0.069904 | 0.2894
2021-11-15 14:15 | 3.226 | 0.94662 | 3.6038 | 1.2693 | 0.022414 | 0.2257 | 0.079031 | 0.28151
2021-11-15 14:30 | 1.6334 | 1.0226 | 3.6446 | 1.1278 | 0.023499 | 0.20954 | 0.088157 | 0.27363
2021-11-15 14:45 | 0.71463 | 0.91113 | 3.5527 | 1.0811 | 0.022153 | 0.20645 | 0.087252 | 0.25811
2021-11-15 15:00 | 0.50228 | 0.73925 | 5.8874 | 1.7575 | 0.016861 | 0.17613 | 0.070619 | 0.23214
2021-11-15 15:15 | 1.5313 | 1.0016 | 5.1274 | 1.5275 | 0.011569 | 0.16598 | 0.053985 | 0.20616
2021-11-15 15:30 | 2.2766 | 0.83126 | 3.5629 | 1.2254 | 0.006276 | 0.17213 | 0.037352 | 0.18018
2021-11-15 15:45 | 0.68196 | 0.84523 | 3.5527 | 1.2289 | 0.002714 | 0.15755 | 0.024545 | 0.14766
2021-11-15 16:00 | 1.2659 | 0.87703 | 3.3894 | 1.2509 | 0.001964 | 0.13251 | 0.017748 | 0.10635
2021-11-15 16:15 | 0.95147 | 0.94734 | 4.1951 | 1.3558 | 0.001215 | 0.085334 | 0.010952 | 0.065047
2021-11-15 16:30 | 1.8989 | 0.86608 | 5.7449 | 1.573 | 0.000465 | 0.026929 | 0.004155 | 0.02374
2021-11-15 16:45 | 2.1235 | 0.89498 | 4.9473 | 1.5 | 0 | 0 | 0 | 0
2021-11-15 17:00 | 4.2799 | 0.81854 | 3.4506 | 1.2846 | 0 | 0 | 0 | 0
2021-11-15 17:15 | 1.2863 | 1.0874 | 3.4506 | 1.6973 | 0 | 0 | 0 | 0
2021-11-15 17:30 | 0.75955 | 1.2018 | 3.665 | 1.7465 | 0 | 0 | 0 | 0
2021-11-15 17:45 | 0.80447 | 1.3336 | 3.7365 | 1.8795 | 0 | 0 | 0 | 0
2021-11-15 18:00 | 0.91472 | 1.308 | 3.8896 | 2.0018 | 0 | 0 | 0 | 0
2021-11-15 18:15 | 0.7963 | 1.3718 | 3.9815 | 1.9422 | 0 | 0 | 0 | 0
2021-11-15 18:30 | 0.75546 | 1.3718 | 3.9611 | 1.9906 | 0 | 0 | 0 | 0
2021-11-15 18:45 | 0.84938 | 1.3114 | 3.8284 | 2.38 | 0 | 0 | 0 | 0
2021-11-15 19:00 | 0.85347 | 1.4553 | 3.8998 | 2.2285 | 0 | 0 | 0 | 0
2021-11-15 19:15 | 0.8453 | 1.2681 | 5.4934 | 2.3325 | 0 | 0 | 0 | 0
2021-11-15 19:30 | 0.71054 | 1.2681 | 4.9049 | 2.2406 | 0 | 0 | 0 | 0
2021-11-15 19:45 | 0.95147 | 1.3838 | 3.7977 | 2.3231 | 0 | 0 | 0 | 0
2021-11-15 20:00 | 1.2557 | 1.0247 | 1.6334 | 1.0442 | 0 | 0 | 0 | 0
2021-11-15 20:15 | 1.9601 | 0.79297 | 2.5931 | 1.1319 | 0 | 0 | 0 | 0
2021-11-15 20:30 | 0.66154 | 0.82394 | 2.5727 | 1.1669 | 0 | 0 | 0 | 0
2021-11-15 20:45 | 1.858 | 0.82394 | 2.6747 | 1.1478 | 0 | 0 | 0 | 0
2021-11-15 21:00 | 0.58395 | 0.8243 | 2.3072 | 0.92522 | 0 | 0 | 0 | 0
2021-11-15 21:15 | 0.42878 | 0.76303 | 2.1643 | 0.8523 | 0 | 0 | 0 | 0
2021-11-15 21:30 | 0.49003 | 0.84701 | 1.9295 | 0.90408 | 0 | 0 | 0 | 0
2021-11-15 21:45 | 0.47778 | 0.75423 | 0.5962 | 0.57564 | 0 | 0 | 0 | 0
2021-11-15 22:00 | 0.58804 | 0.77879 | 0.53087 | 0.62114 | 0 | 0 | 0 | 0
2021-11-15 22:15 | 0.38284 | 0.65995 | 0.46961 | 0.52314 | 0 | 0 | 0 | 0
2021-11-15 22:30 | 0.27462 | 0.62346 | 0.38386 | 0.45269 | 0 | 0 | 0 | 0
2021-11-15 22:45 | 0.25829 | 0.62346 | 0.40019 | 0.46436 | 0 | 0 | 0 | 0
2021-11-15 23:00 | 0.26237 | 1.7176 | 3.2464 | 1.9973 | 0 | 0 | 0 | 0
2021-11-15 23:15 | 0.33792 | 1.6081 | 3.6242 | 1.8347 | 0 | 0 | 0 | 0
2021-11-15 23:30 | 0.32771 | 1.144 | 3.5119 | 1.7338 | 0 | 0 | 0 | 0
2021-11-15 23:45 | 0.20418 | 0.80955 | 3.471 | 1.6347 | 0 | 0 | 0 | 0
2021-11-16 | 0.19601 | 1.1973 | 3.369 | 1.338 | 0 | 0 | 0 | 0
2021-11-16 00:15 | 0.18989 | 0.98434 | 2.2868 | 1.0722 | 0 | 0 | 0 | 0
2021-11-16 00:30 | 0.24093 | 1.0965 | 1.2659 | 0.92085 | 0 | 0 | 0 | 0
2021-11-16 00:45 | 0.2246 | 0.97803 | 0.55128 | 0.77588 | 0 | 0 | 0 | 0
2021-11-16 01:00 | 0.25216 | 0.98509 | 0.86572 | 0.8488 | 0 | 0 | 0 | 0
2021-11-16 01:15 | 0.24195 | 0.97803 | 0.34915 | 0.76261 | 0 | 0 | 0 | 0
2021-11-16 01:30 | 0.29504 | 0.97803 | 0.37365 | 0.76086 | 0 | 0 | 0 | 0
2021-11-16 01:45 | 0.26441 | 1.0224 | 0.2685 | 0.71769 | 0 | 0 | 0 | 0
2021-11-16 02:00 | 0.23174 | 1.0406 | 0.24195 | 0.70194 | 0 | 0 | 0 | 0
2021-11-16 02:15 | 0.23685 | 1.0064 | 0.24502 | 0.71579 | 0 | 0 | 0 | 0
2021-11-16 02:30 | 0.32567 | 0.96197 | 0.25931 | 0.74365 | 0 | 0 | 0 | 0
2021-11-16 02:45 | 0.24502 | 1.0064 | 0.30014 | 0.73957 | 0 | 0 | 0 | 0
2021-11-16 03:00 | 0.22868 | 1.0064 | 0.34915 | 0.73038 | 0 | 0 | 0 | 0
2021-11-16 03:15 | 0.23787 | 1.0064 | 0.26237 | 0.72877 | 0 | 0 | 0 | 0
2021-11-16 03:30 | 0.2736 | 1.0112 | 0.23276 | 0.80709 | 0 | 0 | 0 | 0
2021-11-16 03:45 | 0.24297 | 1.0112 | 0.23174 | 0.78069 | 0 | 0 | 0 | 0
2021-11-16 04:00 | 0.23787 | 0.9288 | 0.23174 | 0.71215 | 0 | 0 | 0 | 0
2021-11-16 04:15 | 0.35527 | 0.93792 | 0.30423 | 0.75926 | 0 | 0 | 0 | 0
2021-11-16 04:30 | 0.25931 | 0.93792 | 0.33587 | 0.81059 | 0 | 0 | 0 | 0
2021-11-16 04:45 | 0.22664 | 0.8821 | 0.23685 | 0.76669 | 0 | 0 | 0 | 0
2021-11-16 05:00 | 0.23378 | 0.90735 | 0.2246 | 0.72659 | 0 | 0 | 0 | 0
2021-11-16 05:15 | 0.29198 | 0.91855 | 0.24706 | 0.72688 | 0 | 0 | 0 | 0
2021-11-16 05:30 | 0.26441 | 0.86273 | 0.31239 | 0.76115 | 0 | 0 | 0 | 0
2021-11-16 05:45 | 0.23991 | 0.93627 | 0.33996 | 0.79922 | 0 | 0 | 0 | 0
2021-11-16 06:00 | 0.23787 | 0.91855 | 0.28687 | 0.75459 | 0 | 0 | 0 | 0
2021-11-16 06:15 | 0.35119 | 0.93724 | 0.21745 | 0.74015 | 0 | 0 | 0 | 0
2021-11-16 06:30 | 0.31035 | 0.88142 | 0.26033 | 0.73315 | 0 | 0 | 0 | 0
2021-11-16 06:45 | 0.22562 | 0.93724 | 0.32669 | 0.61225 | 0 | 0.004854 | 3.3e-05 | 0.003407
2021-11-16 07:00 | 0.28483 | 0.6043 | 0.34302 | 0.377 | 0 | 0.012934 | 0.000118 | 0.011474
2021-11-16 07:15 | 0.2736 | 0.61567 | 0.25114 | 0.29825 | 0 | 0.025763 | 0.000203 | 0.019542
2021-11-16 07:30 | 0.33281 | 0.63776 | 0.31137 | 0.41011 | 0 | 0.035672 | 0.000288 | 0.027609
2021-11-16 07:45 | 0.77997 | 0.71178 | 0.26237 | 0.42615 | 0.001731 | 0.06058 | 0.002186 | 0.041853
2021-11-16 08:00 | 1.2659 | 1.0954 | 1.2455 | 0.89474 | 0.006343 | 0.10403 | 0.006998 | 0.064623
2021-11-16 08:15 | 0.47778 | 1.1123 | 0.69829 | 0.57681 | 0.010956 | 0.1272 | 0.01181 | 0.087393
2021-11-16 08:30 | 0.45328 | 0.94038 | 0.35833 | 0.5208 | 0.015568 | 0.15432 | 0.016622 | 0.11016
2021-11-16 08:45 | 0.46553 | 1.2124 | 0.89431 | 0.66912 | 0.018414 | 0.15944 | 0.019311 | 0.12677
2021-11-16 09:00 | 0.65337 | 1.2061 | 0.69421 | 0.63937 | 0.018319 | 0.14287 | 0.018584 | 0.13457
2021-11-16 09:15 | 0.96781 | 1.2224 | 0.4737 | 0.64812 | 0.018224 | 0.15474 | 0.017856 | 0.14237
2021-11-16 09:30 | 0.63296 | 0.95018 | 0.55128 | 0.47355 | 0.018129 | 0.19025 | 0.017129 | 0.15016
2021-11-16 09:45 | 0.43694 | 0.8532 | 0.56354 | 0.44817 | 0.019088 | 0.24165 | 0.019071 | 0.16545
2021-11-16 10:00 | 0.45736 | 1.1782 | 0.56762 | 0.63996 | 0.021805 | 0.27105 | 0.025316 | 0.19162
2021-11-16 10:15 | 0.48186 | 1.1658 | 0.57987 | 0.57506 | 0.024523 | 0.32115 | 0.03156 | 0.21779
2021-11-16 10:30 | 0.66154 | 1.2362 | 0.49411 | 0.99902 | 0.02724 | 0.35835 | 0.037805 | 0.24396
2021-11-16 10:45 | 0.59212 | 1.1896 | 0.37263 | 0.65498 | 0.029379 | 0.36571 | 0.042152 | 0.25735
2021-11-16 11:00 | 0.73096 | 1.2126 | 1.7968 | 0.74146 | 0.030551 | 0.35672 | 0.043436 | 0.25278
2021-11-16 11:15 | 0.62479 | 1.1912 | 0.46144 | 0.93033 | 0.031724 | 0.34555 | 0.044721 | 0.24822
2021-11-16 11:30 | 0.37671 | 1.1892 | 0.37977 | 0.62741 | 0.032896 | 0.31499 | 0.046006 | 0.24365
2021-11-16 11:45 | 0.33485 | 0.90505 | 0.32771 | 0.43301 | 0.03358 | 0.31556 | 0.046062 | 0.24302
2021-11-16 12:00 | 0.32669 | 1.0855 | 0.34608 | 0.62114 | 0.033445 | 0.3546 | 0.044133 | 0.24797
2021-11-16 12:15 | 0.33894 | 1.3397 | 0.23787 | 1.2194 | 0.03331 | 0.35594 | 0.042203 | 0.25291
2021-11-16 12:30 | 0.40325 | 1.6039 | 0.19601 | 1.5677 | 0.033175 | 0.35286 | 0.040273 | 0.25785
2021-11-16 12:45 | 0.53087 | 1.3881 | 0.19703 | 1.1742 | 0.032576 | 0.34451 | 0.037242 | 0.25736
2021-11-16 13:00 | 0.30525 | 1.3567 | 0.20214 | 1.2111 | 0.031201 | 0.32351 | 0.03243 | 0.24888
2021-11-16 13:15 | 0.5962 | 1.628 | 0.23787 | 1.3671 | 0.029826 | 0.28339 | 0.027618 | 0.2404
2021-11-16 13:30 | 0.68604 | 1.6612 | 0.30218 | 1.4576 | 0.028452 | 0.28289 | 0.022806 | 0.23192
2021-11-16 13:45 | 0.23481 | 1.292 | 2.1235 | 1.1717 | 0.026231 | 0.28604 | 0.020244 | 0.22343
2021-11-16 14:00 | 0.36752 | 1.5519 | 3.3281 | 1.39 | 0.022592 | 0.26986 | 0.021329 | 0.21561
2021-11-16 14:15 | 0.4053 | 1.4718 | 3.226 | 1.631 | 0.018952 | 0.26767 | 0.022414 | 0.20779
2021-11-16 14:30 | 0.37977 | 1.2891 | 1.6334 | 1.2159 | 0.015312 | 0.26974 | 0.023499 | 0.19997
2021-11-16 14:45 | 0.293 | 1.2577 | 0.71463 | 1.0835 | 0.012478 | 0.25415 | 0.022153 | 0.18821
2021-11-16 15:00 | 0.30116 | 1.6775 | 0.50228 | 1.7836 | 0.010998 | 0.224 | 0.016861 | 0.17058
2021-11-16 15:15 | 0.29504 | 1.3581 | 1.5313 | 1.6821 | 0.009518 | 0.19313 | 0.011569 | 0.15295
2021-11-16 15:30 | 0.33281 | 1.2735 | 2.2766 | 1.5076 | 0.008038 | 0.16267 | 0.006276 | 0.13532
2021-11-16 15:45 | 0.4737 | 1.2975 | 0.68196 | 1.2687 | 0.006448 | 0.13727 | 0.002714 | 0.11187
2021-11-16 16:00 | 0.46553 | 1.261 | 1.2659 | 1.3744 | 0.00467 | 0.10439 | 0.001964 | 0.080609
2021-11-16 16:15 | 0.71463 | 1.3799 | 0.95147 | 1.4351 | 0.002893 | 0.063226 | 0.001215 | 0.049354
2021-11-16 16:30 | 0.55128 | 1.4977 | 1.8989 | 1.7884 | 0.001116 | 0.020114 | 0.000465 | 0.018098
2021-11-16 16:45 | 0.35935 | 1.3918 | 2.1235 | 1.7624 | 0 | 0 | 0 | 0
2021-11-16 17:00 | 0.47778 | 1.4241 | 4.2799 | 1.8568 | 0 | 0 | 0 | 0
2021-11-16 17:15 | 0.44103 | 1.551 | 1.2863 | 1.6579 | 0 | 0 | 0 | 0
2021-11-16 17:30 | 0.49003 | 1.4626 | 0.75955 | 1.3504 | 0 | 0 | 0 | 0
2021-11-16 17:45 | 0.52678 | 1.4874 | 0.80447 | 1.481 | 0 | 0 | 0 | 0
2021-11-16 18:00 | 0.52678 | 1.5535 | 0.91472 | 1.59 | 0 | 0 | 0 | 0
2021-11-16 18:15 | 0.53087 | 1.4188 | 0.7963 | 1.5017 | 0 | 0 | 0 | 0
2021-11-16 18:30 | 0.50636 | 1.4188 | 0.75546 | 1.5458 | 0 | 0 | 0 | 0
2021-11-16 18:45 | 0.62479 | 1.5714 | 0.84938 | 1.9588 | 0 | 0 | 0 | 0
2021-11-16 19:00 | 0.52678 | 1.1493 | 0.85347 | 1.7606 | 0 | 0 | 0 | 0
2021-11-16 19:15 | 0.5962 | 1.1929 | 0.8453 | 1.8742 | 0 | 0 | 0 | 0
2021-11-16 19:30 | 0.57578 | 1.4307 | 0.71054 | 1.7263 | 0 | 0 | 0 | 0
2021-11-16 19:45 | 0.53495 | 1.543 | 0.95147 | 1.844 | 0 | 0 | 0 | 0
2021-11-16 20:00 | 1.5007 | 1.1752 | 1.2557 | 1.1198 | 0 | 0 | 0 | 0
2021-11-16 20:15 | 1.6743 | 1.2806 | 1.9601 | 1.3267 | 0 | 0 | 0 | 0
2021-11-16 20:30 | 1.1128 | 1.2233 | 0.66154 | 1.1797 | 0 | 0 | 0 | 0
2021-11-16 20:45 | 0.37161 | 1.244 | 1.858 | 1.3269 | 0 | 0 | 0 | 0
2021-11-16 21:00 | 0.3859 | 1.0782 | 0.58395 | 0.92814 | 0 | 0 | 0 | 0
2021-11-16 21:15 | 0.5962 | 1.0263 | 0.42878 | 0.85347 | 0 | 0 | 0 | 0
2021-11-16 21:30 | 0.66562 | 1.2142 | 0.49003 | 0.92843 | 0 | 0 | 0 | 0
2021-11-16 21:45 | 0.66971 | 0.9926 | 0.47778 | 0.59999 | 0 | 0 | 0 | 0
2021-11-16 22:00 | 0.49003 | 1.0833 | 0.58804 | 0.66037 | 0 | 0 | 0 | 0
2021-11-16 22:15 | 0.44511 | 0.77709 | 0.38284 | 0.5297 | 0 | 0 | 0 | 0
2021-11-16 22:30 | 0.49003 | 0.62835 | 0.27462 | 0.4438 | 0 | 0 | 0 | 0
2021-11-16 22:45 | 0.36242 | 0.63363 | 0.25829 | 0.45226 | 0 | 0 | 0 | 0
2021-11-16 23:00 | 0.37058 | 1.0832 | 0.26237 | 1.6498 | 0 | 0 | 0 | 0
2021-11-16 23:15 | 0.33179 | 1.0832 | 0.33792 | 1.7211 | 0 | 0 | 0 | 0
2021-11-16 23:30 | 0.42878 | 1.0832 | 0.32771 | 1.6832 | 0 | 0 | 0 | 0
2021-11-16 23:45 | 0.50228 | 1.0921 | 0.20418 | 1.6076 | 0 | 0 | 0 | 0
2021-11-17 | 0.41653 | 0.65668 | 0.19601 | 1.3401 | 0 | 0 | 0 | 0
2021-11-17 00:15 | 0.37773 | 0.62104 | 0.18989 | 1.0715 | 0 | 0 | 0 | 0
2021-11-17 00:30 | 0.33077 | 0.63223 | 0.24093 | 0.92931 | 0 | 0 | 0 | 0
2021-11-17 00:45 | 0.19193 | 0.63424 | 0.2246 | 0.78142 | 0 | 0 | 0 | 0
2021-11-17 01:00 | 0.35935 | 0.63424 | 0.25216 | 0.84734 | 0 | 0 | 0 | 0
2021-11-17 01:15 | 0.29912 | 0.59098 | 0.24195 | 0.76071 | 0 | 0 | 0 | 0
2021-11-17 01:30 | 0.21337 | 0.55305 | 0.29504 | 0.75342 | 0 | 0 | 0 | 0
2021-11-17 01:45 | 0.22562 | 0.55305 | 0.26441 | 0.71259 | 0 | 0 | 0 | 0
2021-11-17 02:00 | 0.23991 | 0.55878 | 0.23174 | 0.70456 | 0 | 0 | 0 | 0
2021-11-17 02:15 | 0.34915 | 0.53584 | 0.23685 | 0.71886 | 0 | 0 | 0 | 0
2021-11-17 02:30 | 0.24706 | 0.57377 | 0.32567 | 0.75926 | 0 | 0 | 0 | 0
2021-11-17 02:45 | 0.24297 | 0.53584 | 0.24502 | 0.74219 | 0 | 0 | 0 | 0
2021-11-17 03:00 | 0.24195 | 0.53584 | 0.22868 | 0.72513 | 0 | 0 | 0 | 0
2021-11-17 03:15 | 0.31648 | 0.53584 | 0.23787 | 0.71419 | 0 | 0 | 0 | 0
2021-11-17 03:30 | 0.28279 | 0.64987 | 0.2736 | 0.77442 | 0 | 0 | 0 | 0
2021-11-17 03:45 | 0.24604 | 0.64987 | 0.24297 | 0.74773 | 0 | 0 | 0 | 0
2021-11-17 04:00 | 0.23276 | 0.53584 | 0.23787 | 0.71332 | 0 | 0 | 0 | 0
2021-11-17 04:15 | 0.31852 | 0.58289 | 0.35527 | 0.77719 | 0 | 0 | 0 | 0
2021-11-17 04:30 | 0.24808 | 0.58289 | 0.25931 | 0.80665 | 0 | 0 | 0 | 0
2021-11-17 04:45 | 0.23072 | 0.50553 | 0.22664 | 0.75211 | 0 | 0 | 0 | 0
2021-11-17 05:00 | 0.2736 | 0.54496 | 0.23378 | 0.71083 | 0 | 0 | 0 | 0
2021-11-17 05:15 | 0.33587 | 0.55615 | 0.29198 | 0.72644 | 0 | 0 | 0 | 0
2021-11-17 05:30 | 0.23174 | 0.51673 | 0.26441 | 0.76684 | 0 | 0 | 0 | 0
2021-11-17 05:45 | 0.22051 | 0.57388 | 0.23991 | 0.8033 | 0 | 0 | 0 | 0
2021-11-17 06:00 | 0.26339 | 0.55615 | 0.23787 | 0.74584 | 0 | 0 | 0 | 0
2021-11-17 06:15 | 0.32465 | 0.55865 | 0.35119 | 0.75109 | 0 | 0 | 0 | 0
2021-11-17 06:30 | 0.2246 | 0.51923 | 0.31035 | 0.74598 | 0 | 0 | 0 | 0
2021-11-17 06:45 | 0.22358 | 0.57657 | 0.22562 | 0.61195 | 6.1e-05 | 0.004904 | 0 | 0.002957
2021-11-17 07:00 | 0.33792 | 0.50351 | 0.28483 | 0.36344 | 0.000226 | 0.015743 | 0 | 0.009985
2021-11-17 07:15 | 0.3175 | 0.51551 | 0.2736 | 0.29956 | 0.000391 | 0.025705 | 0 | 0.017014
2021-11-17 07:30 | 0.3369 | 0.50851 | 0.33281 | 0.3579 | 0.000556 | 0.035751 | 0 | 0.024043
2021-11-17 07:45 | 0.37161 | 0.69163 | 0.77997 | 0.48084 | 0.00677 | 0.076114 | 0.001731 | 0.03497
2021-11-17 08:00 | 1.0821 | 0.83645 | 1.2659 | 0.91078 | 0.023411 | 0.10464 | 0.006343 | 0.051529
2021-11-17 08:15 | 0.80447 | 0.69925 | 0.47778 | 0.5068 | 0.040052 | 0.12459 | 0.010956 | 0.068088
2021-11-17 08:30 | 0.41653 | 0.68795 | 0.45328 | 0.4858 | 0.056693 | 0.14879 | 0.015568 | 0.084647
2021-11-17 08:45 | 0.45736 | 0.85667 | 0.46553 | 0.65162 | 0.065262 | 0.16045 | 0.018414 | 0.09418
2021-11-17 09:00 | 0.51453 | 0.88907 | 0.65337 | 0.65571 | 0.059898 | 0.16332 | 0.018319 | 0.093676
2021-11-17 09:15 | 0.53903 | 1.2514 | 0.96781 | 0.72279 | 0.054533 | 0.17592 | 0.018224 | 0.093171
2021-11-17 09:30 | 0.43694 | 0.74258 | 0.63296 | 0.50213 | 0.049169 | 0.19571 | 0.018129 | 0.092666
2021-11-17 09:45 | 0.71871 | 0.72564 | 0.43694 | 0.45299 | 0.048159 | 0.21881 | 0.019088 | 0.099943
2021-11-17 10:00 | 0.53087 | 0.93826 | 0.45736 | 0.65367 | 0.054679 | 0.23269 | 0.021805 | 0.11855
2021-11-17 10:15 | 0.42061 | 1.093 | 0.48186 | 0.57214 | 0.061198 | 0.24527 | 0.024523 | 0.13716
2021-11-17 10:30 | 0.40632 | 1.0883 | 0.66154 | 0.9996 | 0.067718 | 0.2753 | 0.02724 | 0.15577
2021-11-17 10:45 | 0.40632 | 0.89077 | 0.59212 | 0.66198 | 0.076209 | 0.28885 | 0.029379 | 0.16494
2021-11-17 11:00 | 0.44511 | 0.93547 | 0.73096 | 0.76538 | 0.088116 | 0.28489 | 0.030551 | 0.16051
2021-11-17 11:15 | 2.6441 | 0.86541 | 0.62479 | 0.92741 | 0.10002 | 0.28499 | 0.031724 | 0.15607
2021-11-17 11:30 | 2.1949 | 0.81721 | 0.37671 | 0.61123 | 0.11193 | 0.28509 | 0.032896 | 0.15164
2021-11-17 11:45 | 1.317 | 0.76747 | 0.33485 | 0.4263 | 0.11415 | 0.29156 | 0.03358 | 0.15093
2021-11-17 12:00 | 1.2761 | 1.11 | 0.32669 | 0.62027 | 0.099585 | 0.29703 | 0.033445 | 0.15549
2021-11-17 12:15 | 2.7973 | 1.4267 | 0.33894 | 1.0155 | 0.085019 | 0.30988 | 0.03331 | 0.16005
2021-11-17 12:30 | 0.39713 | 0.92046 | 0.40325 | 1.2607 | 0.070453 | 0.31104 | 0.033175 | 0.16461
2021-11-17 12:45 | 0.60845 | 1.1147 | 0.53087 | 0.93208 | 0.076667 | 0.30895 | 0.032576 | 0.16469
2021-11-17 13:00 | 0.24706 | 0.99143 | 0.30525 | 1.1176 | 0.11896 | 0.29548 | 0.031201 | 0.15802
2021-11-17 13:15 | 0.25012 | 1.0349 | 0.5962 | 1.0644 | 0.16126 | 0.27804 | 0.029826 | 0.15135
2021-11-17 13:30 | 0.30729 | 1.0694 | 0.68604 | 1.401 | 0.20356 | 0.25787 | 0.028452 | 0.14469
2021-11-17 13:45 | 0.37058 | 0.9515 | 0.23481 | 1.1119 | 0.21492 | 0.25204 | 0.026231 | 0.13794
2021-11-17 14:00 | 0.27768 | 0.86379 | 0.36752 | 1.4043 | 0.17249 | 0.24599 | 0.022592 | 0.13174
2021-11-17 14:15 | 0.31341 | 0.99038 | 0.4053 | 1.6492 | 0.13007 | 0.26115 | 0.018952 | 0.12554
2021-11-17 14:30 | 0.31852 | 0.91573 | 0.37977 | 1.2258 | 0.087641 | 0.25457 | 0.015312 | 0.11934
2021-11-17 14:45 | 0.37161 | 0.92711 | 0.293 | 1.0728 | 0.056549 | 0.25176 | 0.012478 | 0.11196
2021-11-17 15:00 | 0.46553 | 1.9808 | 0.30116 | 1.6269 | 0.045198 | 0.22072 | 0.010998 | 0.10241
2021-11-17 15:15 | 0.33179 | 1.9241 | 0.29504 | 1.695 | 0.033846 | 0.19766 | 0.009518 | 0.092866
2021-11-17 15:30 | 0.32975 | 1.7688 | 0.33281 | 1.5271 | 0.022495 | 0.18132 | 0.008038 | 0.08332
2021-11-17 15:45 | 0.33587 | 1.7068 | 0.4737 | 1.2932 | 0.013888 | 0.15387 | 0.006448 | 0.069567
2021-11-17 16:00 | 0.46553 | 1.5247 | 0.46553 | 1.4083 | 0.010068 | 0.11106 | 0.00467 | 0.050163
2021-11-17 16:15 | 0.55945 | 1.861 | 0.71463 | 1.4991 | 0.006249 | 0.061532 | 0.002893 | 0.030759
2021-11-17 16:30 | 0.42878 | 2.1487 | 0.55128 | 1.826 | 0.002429 | 0.015979 | 0.001116 | 0.011356
2021-11-17 16:45 | 0.35935 | 1.7939 | 0.35935 | 1.7542 | 0 | 0 | 0 | 0
2021-11-17 17:00 | 0.30831 | 2.1295 | 0.47778 | 1.8804 | 0 | 0 | 0 | 0
2021-11-17 17:15 | 0.39713 | 1.9082 | 0.44103 | 1.683 | 0 | 0 | 0 | 0
2021-11-17 17:30 | 0.55537 | 1.5857 | 0.49003 | 1.3711 | 0 | 0 | 0 | 0
2021-11-17 17:45 | 0.38284 | 1.395 | 0.52678 | 1.4921 | 0 | 0 | 0 | 0
2021-11-17 18:00 | 0.86164 | 1.7491 | 0.52678 | 1.6046 | 0 | 0 | 0 | 0
2021-11-17 18:15 | 1.0005 | 1.4107 | 0.53087 | 1.541 | 0 | 0 | 0 | 0
2021-11-17 18:30 | 0.56762 | 1.5496 | 0.50636 | 1.5873 | 0 | 0 | 0 | 0
2021-11-17 18:45 | 0.7963 | 2.0759 | 0.62479 | 2.0015 | 0 | 0 | 0 | 0
2021-11-17 19:00 | 0.3471 | 1.9822 | 0.52678 | 1.7956 | 0 | 0 | 0 | 0
2021-11-17 19:15 | 1.123 | 2.0759 | 0.5962 | 1.9115 | 0 | 0 | 0 | 0
2021-11-17 19:30 | 3.5323 | 1.8501 | 0.57578 | 1.7333 | 0 | 0 | 0 | 0
2021-11-17 19:45 | 3.8692 | 2.0365 | 0.53495 | 1.8149 | 0 | 0 | 0 | 0
2021-11-17 20:00 | 0.98823 | 1.1063 | 1.5007 | 1.2023 | 0 | 0 | 0 | 0
2021-11-17 20:15 | 0.37875 | 1.0918 | 1.6743 | 1.4277 | 0 | 0 | 0 | 0
2021-11-17 20:30 | 0.73913 | 1.1071 | 1.1128 | 1.2191 | 0 | 0 | 0 | 0
2021-11-17 20:45 | 1.0617 | 1.0381 | 0.37161 | 1.2691 | 0 | 0 | 0 | 0
2021-11-17 21:00 | 1.0924 | 1.0134 | 0.3859 | 0.88701 | 0 | 0 | 0 | 0
2021-11-17 21:15 | 1.0515 | 1.0676 | 0.5962 | 0.83713 | 0 | 0 | 0 | 0
2021-11-17 21:30 | 0.91881 | 1.0237 | 0.66562 | 0.74934 | 0 | 0 | 0 | 0
2021-11-17 21:45 | 0.49003 | 0.68853 | 0.66971 | 0.54253 | 0 | 0 | 0 | 0
2021-11-17 22:00 | 0.52678 | 0.78029 | 0.49003 | 0.53787 | 0 | 0 | 0 | 0
2021-11-17 22:15 | 0.51453 | 0.76509 | 0.44511 | 0.48478 | 0 | 0 | 0 | 0
2021-11-17 22:30 | 0.39304 | 0.61249 | 0.49003 | 0.44555 | 0 | 0 | 0 | 0
2021-11-17 22:45 | 0.27666 | 0.61249 | 0.36242 | 0.44453 | 0 | 0 | 0 | 0
2021-11-17 23:00 | 3.1648 | 1.7263 | 0.37058 | 1.6504 | 0 | 0 | 0 | 0
2021-11-17 23:15 | 3.369 | 2.1111 | 0.33179 | 1.7189 | 0 | 0 | 0 | 0
2021-11-17 23:30 | 3.3485 | 1.9283 | 0.42878 | 1.6948 | 0 | 0 | 0 | 0
2021-11-17 23:45 | 3.4915 | 1.7055 | 0.50228 | 1.6215 | 0 | 0 | 0 | 0
2021-11-18 | 3.4915 | 1.3301 | 0.41653 | 1.3407 | 0 | 0 | 0 | 0
2021-11-18 00:15 | 3.3894 | 1.3678 | 0.37773 | 1.066 | 0 | 0 | 0 | 0
2021-11-18 00:30 | 3.3894 | 1.6677 | 0.33077 | 0.90189 | 0 | 0 | 0 | 0
2021-11-18 00:45 | 3.369 | 1.0981 | 0.19193 | 0.733 | 0 | 0 | 0 | 0
2021-11-18 01:00 | 3.4506 | 0.96056 | 0.35935 | 0.83101 | 0 | 0 | 0 | 0
2021-11-18 01:15 | 3.5731 | 1.0021 | 0.29912 | 0.74511 | 0 | 0 | 0 | 0
2021-11-18 01:30 | 3.471 | 0.94886 | 0.21337 | 0.73636 | 0 | 0 | 0 | 0
2021-11-18 01:45 | 3.4302 | 0.99325 | 0.22562 | 0.70456 | 0 | 0 | 0 | 0
2021-11-18 02:00 | 3.42 | 1.0114 | 0.23991 | 0.69946 | 0 | 0 | 0 | 0
2021-11-18 02:15 | 3.4302 | 0.97719 | 0.34915 | 0.7263 | 0 | 0 | 0 | 0
2021-11-18 02:30 | 3.5425 | 1.0058 | 0.24706 | 0.73738 | 0 | 0 | 0 | 0
2021-11-18 02:45 | 3.614 | 0.93281 | 0.24297 | 0.73315 | 0 | 0 | 0 | 0
2021-11-18 03:00 | 3.7977 | 0.93281 | 0.24195 | 0.72032 | 0 | 0 | 0 | 0
2021-11-18 03:15 | 3.4302 | 0.97719 | 0.31648 | 0.72017 | 0 | 0 | 0 | 0
2021-11-18 03:30 | 3.42 | 0.89963 | 0.28279 | 0.73957 | 0 | 0 | 0 | 0
2021-11-18 03:45 | 3.5017 | 0.89963 | 0.24604 | 0.70413 | 0 | 0 | 0 | 0
2021-11-18 04:00 | 3.4506 | 0.89963 | 0.23276 | 0.69523 | 0 | 0 | 0 | 0
2021-11-18 04:15 | 1.9397 | 0.90875 | 0.31852 | 0.76582 | 0 | 0 | 0 | 0
2021-11-18 04:30 | 1.0086 | 0.91759 | 0.24808 | 0.78434 | 0 | 0 | 0 | 0
2021-11-18 04:45 | 0.67788 | 0.85293 | 0.23072 | 0.72921 | 0 | 0 | 0 | 0
2021-11-18 05:00 | 0.51045 | 0.87819 | 0.2736 | 0.71113 | 0 | 0 | 0 | 0
2021-11-18 05:15 | 0.4053 | 0.88938 | 0.33587 | 0.73475 | 0 | 0 | 0 | 0
2021-11-18 05:30 | 0.27768 | 0.83356 | 0.23174 | 0.74861 | 0 | 0 | 0 | 0
2021-11-18 05:45 | 0.27666 | 0.9071 | 0.22051 | 0.77938 | 0 | 0 | 0 | 0
2021-11-18 06:00 | 0.37977 | 0.88938 | 0.26339 | 0.7438 | 0 | 0 | 0 | 0
2021-11-18 06:15 | 0.29402 | 0.98755 | 0.32465 | 0.75663 | 0 | 0 | 0 | 0
2021-11-18 06:30 | 0.29402 | 0.93173 | 0.2246 | 0.73738 | 0 | 0 | 0 | 0
2021-11-18 06:45 | 0.35119 | 0.95919 | 0.22358 | 0.6016 | 0 | 0.006334 | 6.1e-05 | 0.000874
2021-11-18 07:00 | 0.39611 | 0.6669 | 0.33792 | 0.34754 | 0 | 0.016265 | 0.000226 | 0.003006
2021-11-18 07:15 | 0.32873 | 0.65255 | 0.3175 | 0.2965 | 0 | 0.027785 | 0.000391 | 0.005137
2021-11-18 07:30 | 0.38896 | 0.70427 | 0.3369 | 0.35411 | 0 | 0.04027 | 0.000556 | 0.007269
2021-11-18 07:45 | 0.64521 | 0.76052 | 0.37161 | 0.48595 | 0.009784 | 0.11054 | 0.00677 | 0.013172
2021-11-18 08:00 | 1.1026 | 1.1767 | 1.0821 | 1.0193 | 0.037042 | 0.14887 | 0.023411 | 0.024853
2021-11-18 08:15 | 1.0821 | 1.18 | 0.80447 | 0.56397 | 0.064299 | 0.18204 | 0.040052 | 0.036533
2021-11-18 08:30 | 0.54312 | 0.85907 | 0.41653 | 0.48945 | 0.091557 | 0.21813 | 0.056693 | 0.048214
2021-11-18 08:45 | 0.50636 | 1.0883 | 0.45736 | 0.66329 | 0.11105 | 0.23521 | 0.065262 | 0.054012
2021-11-18 09:00 | 0.49411 | 1.0846 | 0.51453 | 0.66037 | 0.11666 | 0.23941 | 0.059898 | 0.050897
2021-11-18 09:15 | 0.50228 | 1.2486 | 0.53903 | 0.65104 | 0.12227 | 0.23214 | 0.054533 | 0.047782
2021-11-18 09:30 | 0.39611 | 1.0542 | 0.43694 | 0.50563 | 0.12788 | 0.26398 | 0.049169 | 0.044667
2021-11-18 09:45 | 0.79222 | 1.0492 | 0.71871 | 0.48624 | 0.1427 | 0.29975 | 0.048159 | 0.047533
2021-11-18 10:00 | 0.60029 | 1.0987 | 0.53087 | 0.64025 | 0.17401 | 0.33467 | 0.054679 | 0.059519
2021-11-18 10:15 | 0.91472 | 1.2372 | 0.42061 | 0.52722 | 0.20532 | 0.3696 | 0.061198 | 0.071504
2021-11-18 10:30 | 0.77588 | 1.2197 | 0.40632 | 0.95789 | 0.23664 | 0.40453 | 0.067718 | 0.08349
2021-11-18 10:45 | 0.76363 | 1.2365 | 0.40632 | 0.6436 | 0.26849 | 0.43828 | 0.076209 | 0.09056
2021-11-18 11:00 | 0.92697 | 1.164 | 0.44511 | 0.76596 | 0.30132 | 0.43843 | 0.088116 | 0.090298
2021-11-18 11:15 | 2.1847 | 1.4328 | 2.6441 | 1.2241 | 0.33414 | 0.43858 | 0.10002 | 0.090037
2021-11-18 11:30 | 2.2153 | 1.1524 | 2.1949 | 0.86747 | 0.36697 | 0.43876 | 0.11193 | 0.089775
2021-11-18 11:45 | 2.1949 | 1.0278 | 1.317 | 0.5456 | 0.39004 | 0.43956 | 0.11415 | 0.089687
2021-11-18 12:00 | 2.001 | 1.095 | 1.2761 | 0.63777 | 0.39557 | 0.44122 | 0.099585 | 0.08951
2021-11-18 12:15 | 1.807 | 1.0995 | 2.7973 | 1.0388 | 0.40111 | 0.44288 | 0.085019 | 0.089332
2021-11-18 12:30 | 0.5962 | 1.0556 | 0.39713 | 1.0038 | 0.40664 | 0.44454 | 0.070453 | 0.089155
2021-11-18 12:45 | 1.2965 | 1.0128 | 0.60845 | 0.89824 | 0.41471 | 0.44152 | 0.076667 | 0.088184
2021-11-18 13:00 | 1.9091 | 1.1391 | 0.24706 | 0.78974 | 0.42735 | 0.43241 | 0.11896 | 0.086591
2021-11-18 13:15 | 0.40427 | 1.1108 | 0.25012 | 0.88424 | 0.43998 | 0.41218 | 0.16126 | 0.084997
2021-11-18 13:30 | 0.31239 | 1.408 | 0.30729 | 1.3142 | 0.45261 | 0.40331 | 0.20356 | 0.083403
2021-11-18 13:45 | 0.31648 | 1.1657 | 0.37058 | 1.103 | 0.4244 | 0.38981 | 0.21492 | 0.080568
2021-11-18 14:00 | 0.28789 | 1.3207 | 0.27768 | 1.3775 | 0.32256 | 0.38046 | 0.17249 | 0.075047
2021-11-18 14:15 | 0.94331 | 1.4273 | 0.31341 | 1.6152 | 0.22072 | 0.37112 | 0.13007 | 0.069526
2021-11-18 14:30 | 3.1546 | 1.1669 | 0.31852 | 1.2071 | 0.11889 | 0.37165 | 0.087641 | 0.064004
2021-11-18 14:45 | 0.23685 | 1.1661 | 0.37161 | 1.0692 | 0.053955 | 0.34521 | 0.056549 | 0.057501
2021-11-18 15:00 | 0.23378 | 1.4196 | 0.46553 | 1.2996 | 0.055625 | 0.30852 | 0.045198 | 0.049703
2021-11-18 15:15 | 0.25931 | 1.2654 | 0.33179 | 1.2247 | 0.057295 | 0.27199 | 0.033846 | 0.041906
2021-11-18 15:30 | 0.33996 | 1.2141 | 0.32975 | 1.0623 | 0.058965 | 0.24746 | 0.022495 | 0.034108
2021-11-18 15:45 | 0.23072 | 1.1138 | 0.33587 | 0.82634 | 0.054694 | 0.2066 | 0.013888 | 0.026398
2021-11-18 16:00 | 0.2246 | 1.1945 | 0.46553 | 0.94535 | 0.039685 | 0.1607 | 0.010068 | 0.019067
2021-11-18 16:15 | 0.22766 | 1.2137 | 0.55945 | 1.0526 | 0.024676 | 0.095246 | 0.006249 | 0.011736
2021-11-18 16:30 | 0.34404 | 1.2351 | 0.42878 | 1.3841 | 0.009668 | 0.030322 | 0.002429 | 0.004404
2021-11-18 16:45 | 0.24502 | 1.2039 | 0.35935 | 1.3024 | 0 | 0 | 0 | 0
2021-11-18 17:00 | 0.23174 | 1.2285 | 0.30831 | 1.4213 | 0 | 0 | 0 | 0
2021-11-18 17:15 | 0.22664 | 1.2468 | 0.39713 | 1.2395 | 0 | 0 | 0 | 0
2021-11-18 17:30 | 0.33077 | 1.1018 | 0.55537 | 0.94287 | 0 | 0 | 0 | 0
2021-11-18 17:45 | 0.2491 | 1.1847 | 0.38284 | 1.0276 | 0 | 0 | 0 | 0
2021-11-18 18:00 | 0.32873 | 1.2214 | 0.86164 | 1.2114 | 0 | 0 | 0 | 0
2021-11-18 18:15 | 0.28279 | 1.2384 | 1.0005 | 1.1647 | 0 | 0 | 0 | 0
2021-11-18 18:30 | 0.36956 | 1.2384 | 0.56762 | 1.1317 | 0 | 0 | 0 | 0
2021-11-18 18:45 | 0.26237 | 1.3701 | 0.7963 | 1.5655 | 0 | 0 | 0 | 0
2021-11-18 19:00 | 0.26952 | 1.2509 | 0.3471 | 1.2852 | 0 | 0 | 0 | 0
2021-11-18 19:15 | 0.34098 | 1.3906 | 1.123 | 1.5046 | 0 | 0 | 0 | 0
2021-11-18 19:30 | 0.39611 | 1.4423 | 3.5323 | 1.6574 | 0 | 0 | 0 | 0
2021-11-18 19:45 | 0.27054 | 1.4972 | 3.8692 | 1.8207 | 0 | 0 | 0 | 0
2021-11-18 20:00 | 0.26339 | 1.1017 | 0.98823 | 1.2175 | 0 | 0 | 0 | 0
2021-11-18 20:15 | 0.26748 | 1.2305 | 0.37875 | 1.3517 | 0 | 0 | 0 | 0
2021-11-18 20:30 | 0.36242 | 1.175 | 0.73913 | 1.1657 | 0 | 0 | 0 | 0
2021-11-18 20:45 | 0.33587 | 1.1525 | 1.0617 | 1.1539 | 0 | 0 | 0 | 0
2021-11-18 21:00 | 0.23889 | 0.94265 | 1.0924 | 0.88847 | 0 | 0 | 0 | 0
2021-11-18 21:15 | 0.22868 | 0.85479 | 1.0515 | 0.80942 | 0 | 0 | 0 | 0
2021-11-18 21:30 | 0.30627 | 0.97839 | 0.91881 | 0.78201 | 0 | 0 | 0 | 0
2021-11-18 21:45 | 0.51453 | 0.64868 | 0.49003 | 0.53787 | 0 | 0 | 0 | 0
2021-11-18 22:00 | 0.33996 | 0.65466 | 0.52678 | 0.50753 | 0 | 0 | 0 | 0
2021-11-18 22:15 | 0.31239 | 0.60732 | 0.51453 | 0.45561 | 0 | 0 | 0 | 0
2021-11-18 22:30 | 0.35833 | 0.60732 | 0.39304 | 0.42411 | 0 | 0 | 0 | 0
2021-11-18 22:45 | 0.3859 | 0.60732 | 0.27666 | 0.40646 | 0 | 0 | 0 | 0
2021-11-18 23:00 | 3.175 | 1.1658 | 3.1648 | 1.6241 | 0 | 0 | 0 | 0
2021-11-18 23:15 | 3.3996 | 1.108 | 3.369 | 1.6985 | 0 | 0 | 0 | 0
2021-11-18 23:30 | 3.471 | 1.117 | 3.3485 | 1.6788 | 0 | 0 | 0 | 0
2021-11-18 23:45 | 3.3894 | 1.117 | 3.4915 | 1.6798 | 0 | 0 | 0 | 0
2021-11-19 | 3.3485 | 1.2409 | 3.4915 | 1.6149 | 0 | 0 | 0 | 0
2021-11-19 00:15 | 3.369 | 1.2408 | 3.3894 | 1.4387 | 0 | 0 | 0 | 0
2021-11-19 00:30 | 3.4506 | 1.2738 | 3.3894 | 1.2852 | 0 | 0 | 0 | 0
2021-11-19 00:45 | 3.4098 | 1.0165 | 3.369 | 1.18 | 0 | 0 | 0 | 0
2021-11-19 01:00 | 3.4404 | 1.2408 | 3.4506 | 1.2852 | 0 | 0 | 0 | 0
2021-11-19 01:15 | 3.4302 | 1.0165 | 3.5731 | 1.1974 | 0 | 0 | 0 | 0
2021-11-19 01:30 | 3.5017 | 1.0165 | 3.471 | 1.1856 | 0 | 0 | 0 | 0
2021-11-19 01:45 | 3.42 | 1.0165 | 3.4302 | 1.1545 | 0 | 0 | 0 | 0
2021-11-19 02:00 | 3.4302 | 1.0969 | 3.42 | 1.15 | 0 | 0 | 0 | 0
2021-11-19 02:15 | 3.5221 | 1.0273 | 3.4302 | 1.1772 | 0 | 0 | 0 | 0
2021-11-19 02:30 | 3.3996 | 0.9946 | 3.5425 | 1.1879 | 0 | 0 | 0 | 0
2021-11-19 02:45 | 3.5425 | 1.0413 | 3.614 | 1.2118 | 0 | 0 | 0 | 0
2021-11-19 03:00 | 3.7671 | 1.0969 | 3.7977 | 1.2232 | 0 | 0 | 0 | 0
2021-11-19 03:15 | 3.471 | 0.9946 | 3.4302 | 1.1634 | 0 | 0 | 0 | 0
2021-11-19 03:30 | 3.5119 | 1.0337 | 3.42 | 1.1765 | 0 | 0 | 0 | 0
2021-11-19 03:45 | 3.5323 | 0.98698 | 3.5017 | 1.1641 | 0 | 0 | 0 | 0
2021-11-19 04:00 | 3.5119 | 0.98698 | 3.4506 | 1.1478 | 0 | 0 | 0 | 0
2021-11-19 04:15 | 3.3792 | 1.0766 | 1.9397 | 1.0021 | 0 | 0 | 0 | 0
2021-11-19 04:30 | 3.4098 | 1.0484 | 1.0086 | 0.87009 | 0 | 0 | 0 | 0
2021-11-19 04:45 | 3.5119 | 0.88782 | 0.67788 | 0.78609 | 0 | 0 | 0 | 0
2021-11-19 05:00 | 3.4813 | 1.0164 | 0.51045 | 0.74336 | 0 | 0 | 0 | 0
2021-11-19 05:15 | 3.4404 | 1.0276 | 0.4053 | 0.75007 | 0 | 0 | 0 | 0
2021-11-19 05:30 | 3.4506 | 0.82734 | 0.27768 | 0.73621 | 0 | 0 | 0 | 0
2021-11-19 05:45 | 3.5119 | 0.99859 | 0.27666 | 0.77894 | 0 | 0 | 0 | 0
2021-11-19 06:00 | 3.3894 | 0.98087 | 0.37977 | 0.75911 | 0 | 0 | 0 | 0
2021-11-19 06:15 | 3.3996 | 1.0463 | 0.29402 | 0.74846 | 0 | 0 | 0 | 0
2021-11-19 06:30 | 3.5425 | 0.84604 | 0.29402 | 0.73052 | 0 | 0 | 0 | 0
2021-11-19 06:45 | 2.1235 | 0.99956 | 0.35119 | 0.61254 | 0 | 0.0028 | 0 | 0.000444
2021-11-19 07:00 | 0.41653 | 0.61734 | 0.39611 | 0.35571 | 0 | 0.010046 | 0 | 0.001545
2021-11-19 07:15 | 0.47778 | 0.63521 | 0.32873 | 0.29504 | 0 | 0.012823 | 0 | 0.002645
2021-11-19 07:30 | 0.44511 | 0.65962 | 0.38896 | 0.34608 | 0 | 0.026172 | 0 | 0.003746
2021-11-19 07:45 | 0.52678 | 0.73491 | 0.64521 | 0.53218 | 0.003948 | 0.061645 | 0.009784 | 0.008881
2021-11-19 08:00 | 1.807 | 1.2356 | 1.1026 | 1.1155 | 0.015204 | 0.093218 | 0.037042 | 0.020699
2021-11-19 08:15 | 0.85347 | 1.1306 | 1.0821 | 0.64973 | 0.026461 | 0.11594 | 0.064299 | 0.032517
2021-11-19 08:30 | 0.58395 | 0.92952 | 0.54312 | 0.45678 | 0.037718 | 0.15269 | 0.091557 | 0.044336
2021-11-19 08:45 | 0.45736 | 1.1298 | 0.50636 | 0.61662 | 0.046717 | 0.16645 | 0.11105 | 0.051169
2021-11-19 09:00 | 0.60029 | 1.162 | 0.49411 | 0.62887 | 0.051532 | 0.16943 | 0.11666 | 0.04992
2021-11-19 09:15 | 0.46553 | 1.2216 | 0.50228 | 0.65396 | 0.056346 | 0.163 | 0.12227 | 0.048672
2021-11-19 09:30 | 0.48595 | 1.0286 | 0.39611 | 0.48988 | 0.061161 | 0.18661 | 0.12788 | 0.047423
2021-11-19 09:45 | 0.47778 | 1.0303 | 0.79222 | 0.53116 | 0.064336 | 0.20408 | 0.1427 | 0.052763
2021-11-19 10:00 | 0.39407 | 1.126 | 0.60029 | 0.63266 | 0.064469 | 0.22786 | 0.17401 | 0.068582
2021-11-19 10:15 | 0.37365 | 1.1298 | 0.91472 | 0.57681 | 0.064601 | 0.26622 | 0.20532 | 0.084401
2021-11-19 10:30 | 0.36956 | 1.2221 | 0.77588 | 0.99814 | 0.064734 | 0.33106 | 0.23664 | 0.10022
2021-11-19 10:45 | 0.41244 | 1.1653 | 0.76363 | 0.6716 | 0.067847 | 0.34735 | 0.26849 | 0.11176
2021-11-19 11:00 | 0.35221 | 1.1944 | 0.92697 | 0.76421 | 0.076504 | 0.34747 | 0.30132 | 0.11691
2021-11-19 11:15 | 0.30014 | 1.2101 | 2.1847 | 1.0359 | 0.085161 | 0.36292 | 0.33414 | 0.12205
2021-11-19 11:30 | 0.34098 | 1.1589 | 2.2153 | 0.93456 | 0.093818 | 0.38877 | 0.36697 | 0.12719
2021-11-19 11:45 | 0.31648 | 1.1936 | 2.1949 | 0.7314 | 0.096615 | 0.36932 | 0.39004 | 0.13042
2021-11-19 12:00 | 0.22153 | 1.1492 | 2.001 | 0.74861 | 0.088501 | 0.34485 | 0.39557 | 0.13007
2021-11-19 12:15 | 0.22358 | 1.2177 | 1.807 | 1.161 | 0.080387 | 0.33067 | 0.40111 | 0.12973
2021-11-19 12:30 | 0.22256 | 1.1591 | 0.5962 | 0.8542 | 0.072272 | 0.33191 | 0.40664 | 0.12939
2021-11-19 12:45 | 0.29504 | 1.1594 | 1.2965 | 0.97379 | 0.065948 | 0.32199 | 0.41471 | 0.12918
2021-11-19 13:00 | 0.28381 | 0.99761 | 1.9091 | 0.98604 | 0.062964 | 0.35836 | 0.42735 | 0.12982
2021-11-19 13:15 | 0.33792 | 1.0332 | 0.40427 | 0.80549 | 0.059979 | 0.35081 | 0.43998 | 0.13045
2021-11-19 13:30 | 0.24195 | 1.1283 | 0.31239 | 1.2042 | 0.056994 | 0.37265 | 0.45261 | 0.13108
2021-11-19 13:45 | 0.22358 | 1.1882 | 0.31648 | 1.0135 | 0.051953 | 0.35865 | 0.4244 | 0.12507
2021-11-19 14:00 | 0.2246 | 1.3497 | 0.28789 | 1.3398 | 0.043071 | 0.34701 | 0.32256 | 0.10646
2021-11-19 14:15 | 0.22256 | 1.2886 | 0.94331 | 1.2949 | 0.03419 | 0.32988 | 0.22072 | 0.087848
2021-11-19 14:30 | 0.29708 | 1.2886 | 3.1546 | 1.3661 | 0.025308 | 0.26862 | 0.11889 | 0.06924
2021-11-19 14:45 | 0.30627 | 1.1538 | 0.23685 | 0.80986 | 0.018307 | 0.21563 | 0.053955 | 0.054595
2021-11-19 15:00 | 0.25318 | 1.3377 | 0.23378 | 1.1667 | 0.014825 | 0.18038 | 0.055625 | 0.047712
2021-11-19 15:15 | 0.25625 | 1.2546 | 0.25931 | 1.1871 | 0.011343 | 0.15902 | 0.057295 | 0.040828
2021-11-19 15:30 | 0.25727 | 1.1845 | 0.33996 | 1.052 | 0.00786 | 0.14192 | 0.058965 | 0.033944
2021-11-19 15:45 | 0.3369 | 1.1019 | 0.23072 | 0.81759 | 0.005104 | 0.12413 | 0.054694 | 0.026867
2021-11-19 16:00 | 0.32158 | 1.1382 | 0.2246 | 0.9016 | 0.003706 | 0.091943 | 0.039685 | 0.01944
2021-11-19 16:15 | 0.24706 | 1.214 | 0.22766 | 1.0409 | 0.002309 | 0.051855 | 0.024676 | 0.012012
2021-11-19 16:30 | 0.26135 | 1.3942 | 0.34404 | 1.3918 | 0.000912 | 0.018513 | 0.009668 | 0.004584
2021-11-19 16:45 | 0.44511 | 1.2806 | 0.24502 | 1.2917 | 0 | 0 | 0 | 0
2021-11-19 17:00 | 0.40836 | 1.2218 | 0.23174 | 1.3383 | 0 | 0 | 0 | 0
2021-11-19 17:15 | 0.2981 | 1.0822 | 0.22664 | 0.91749 | 0 | 0 | 0 | 0
2021-11-19 17:30 | 0.43286 | 1.0361 | 0.33077 | 0.93791 | 0 | 0 | 0 | 0
2021-11-19 17:45 | 0.4982 | 1.0852 | 0.2491 | 0.92143 | 0 | 0 | 0 | 0
2021-11-19 18:00 | 0.40121 | 1.2157 | 0.32873 | 1.0585 | 0 | 0 | 0 | 0
2021-11-19 18:15 | 0.51453 | 1.1931 | 0.28279 | 1.0578 | 0 | 0 | 0 | 0
2021-11-19 18:30 | 0.39202 | 1.1161 | 0.36956 | 1.0124 | 0 | 0 | 0 | 0
2021-11-19 18:45 | 0.42469 | 1.1727 | 0.26237 | 1.0488 | 0 | 0 | 0 | 0
2021-11-19 19:00 | 0.78405 | 1.1333 | 0.26952 | 0.98823 | 0 | 0 | 0 | 0
2021-11-19 19:15 | 0.89022 | 1.4067 | 0.34098 | 1.355 | 0 | 0 | 0 | 0
2021-11-19 19:30 | 3.0525 | 1.4084 | 0.39611 | 1.5956 | 0 | 0 | 0 | 0
2021-11-19 19:45 | 4.134 | 1.5125 | 0.27054 | 1.7532 | 0 | 0 | 0 | 0
2021-11-19 20:00 | 0.93922 | 1.0153 | 0.26339 | 0.97218 | 0 | 0 | 0 | 0
2021-11-19 20:15 | 0.5717 | 1.1369 | 0.26748 | 1.228 | 0 | 0 | 0 | 0
2021-11-19 20:30 | 0.53087 | 1.0972 | 0.36242 | 1.0366 | 0 | 0 | 0 | 0
2021-11-19 20:45 | 0.62479 | 1.0507 | 0.33587 | 1.0356 | 0 | 0 | 0 | 0
2021-11-19 21:00 | 0.75546 | 0.87046 | 0.23889 | 0.81934 | 0 | 0 | 0 | 0
2021-11-19 21:15 | 0.80855 | 0.82999 | 0.22868 | 0.76101 | 0 | 0 | 0 | 0
2021-11-19 21:30 | 0.38182 | 0.94818 | 0.30627 | 0.74467 | 0 | 0 | 0 | 0
2021-11-19 21:45 | 0.27973 | 0.64352 | 0.51453 | 0.53262 | 0 | 0 | 0 | 0
2021-11-19 22:00 | 0.28381 | 0.64418 | 0.33996 | 0.48668 | 0 | 0 | 0 | 0
2021-11-19 22:15 | 0.35527 | 0.627 | 0.31239 | 0.43957 | 0 | 0 | 0 | 0
2021-11-19 22:30 | 0.4737 | 0.627 | 0.35833 | 0.41463 | 0 | 0 | 0 | 0
2021-11-19 22:45 | 0.45328 | 0.59173 | 0.3859 | 0.40034 | 0 | 0 | 0 | 0
2021-11-19 23:00 | 3.2771 | 2.4063 | 3.175 | 2.0106 | 0 | 0 | 0 | 0
2021-11-19 23:15 | 3.4608 | 2.5648 | 3.3996 | 2.1273 | 0 | 0 | 0 | 0
2021-11-19 23:30 | 3.42 | 2.5264 | 3.471 | 2.1185 | 0 | 0 | 0 | 0
2021-11-19 23:45 | 3.3996 | 2.7284 | 3.3894 | 2.1192 | 0 | 0 | 0 | 0
2021-11-20 | 3.3281 | 1.7619 | 3.3485 | 2.059 | 0 | 0 | 0 | 0
2021-11-20 00:15 | 3.369 | 1.7026 | 3.369 | 1.8926 | 0 | 0 | 0 | 0
2021-11-20 00:30 | 3.369 | 1.6964 | 3.4506 | 1.7516 | 0 | 0 | 0 | 0
2021-11-20 00:45 | 3.4608 | 1.5978 | 3.4098 | 1.6394 | 0 | 0 | 0 | 0
2021-11-20 01:00 | 3.5017 | 1.6758 | 3.4404 | 1.7376 | 0 | 0 | 0 | 0
2021-11-20 01:15 | 3.3587 | 1.7604 | 3.4302 | 1.6474 | 0 | 0 | 0 | 0
2021-11-20 01:30 | 3.3587 | 1.7078 | 3.5017 | 1.6372 | 0 | 0 | 0 | 0
2021-11-20 01:45 | 3.369 | 1.5951 | 3.42 | 1.6054 | 0 | 0 | 0 | 0
2021-11-20 02:00 | 3.3587 | 1.628 | 3.4302 | 1.6075 | 0 | 0 | 0 | 0
2021-11-20 02:15 | 3.369 | 1.6136 | 3.5221 | 1.648 | 0 | 0 | 0 | 0
2021-11-20 02:30 | 3.5017 | 1.4446 | 3.3996 | 1.6422 | 0 | 0 | 0 | 0
2021-11-20 02:45 | 3.5731 | 1.4972 | 3.5425 | 1.6636 | 0 | 0 | 0 | 0
2021-11-20 03:00 | 3.7773 | 1.6115 | 3.7671 | 1.7163 | 0 | 0 | 0 | 0
2021-11-20 03:15 | 3.4506 | 1.4616 | 3.471 | 1.6273 | 0 | 0 | 0 | 0
2021-11-20 03:30 | 3.42 | 1.5199 | 3.5119 | 1.6452 | 0 | 0 | 0 | 0
2021-11-20 03:45 | 3.4915 | 1.5352 | 3.5323 | 1.6368 | 0 | 0 | 0 | 0
2021-11-20 04:00 | 3.2771 | 1.5352 | 3.5119 | 1.6149 | 0 | 0 | 0 | 0
2021-11-20 04:15 | 1.7457 | 1.4334 | 3.3792 | 1.4357 | 0 | 0 | 0 | 0
2021-11-20 04:30 | 0.91881 | 1.4343 | 3.4098 | 1.2878 | 0 | 0 | 0 | 0
2021-11-20 04:45 | 0.53087 | 1.4679 | 3.5119 | 1.2201 | 0 | 0 | 0 | 0
2021-11-20 05:00 | 0.44511 | 1.3717 | 3.4813 | 1.2071 | 0 | 0 | 0 | 0
2021-11-20 05:15 | 0.37569 | 1.3717 | 3.4404 | 1.2074 | 0 | 0 | 0 | 0
2021-11-20 05:30 | 0.30423 | 1.3705 | 3.4506 | 1.1806 | 0 | 0 | 0 | 0
2021-11-20 05:45 | 0.21745 | 1.3696 | 3.5119 | 1.2299 | 0 | 0 | 0 | 0
2021-11-20 06:00 | 0.2736 | 1.4005 | 3.3894 | 1.1886 | 0 | 0 | 0 | 0
2021-11-20 06:15 | 0.29912 | 1.3218 | 3.3996 | 1.1981 | 0 | 0 | 0 | 0
2021-11-20 06:30 | 0.23685 | 1.3218 | 3.5425 | 1.2048 | 0 | 0 | 0 | 0
2021-11-20 06:45 | 0.24399 | 0.92016 | 2.1235 | 0.87812 | 5e-06 | 0.001393 | 0 | 0.00022
2021-11-20 07:00 | 0.38692 | 0.57429 | 0.41653 | 0.35935 | 2e-05 | 0.011499 | 0 | 0.000771
2021-11-20 07:15 | 0.30525 | 0.59681 | 0.47778 | 0.32231 | 3.5e-05 | 0.018591 | 0 | 0.001322
2021-11-20 07:30 | 0.30218 | 0.60817 | 0.44511 | 0.36096 | 5e-05 | 0.027072 | 0 | 0.001873
2021-11-20 07:45 | 0.2981 | 0.74229 | 0.52678 | 0.52809 | 0.008953 | 0.047535 | 0.003948 | 0.006426
2021-11-20 08:00 | 0.71463 | 1.2365 | 1.807 | 1.2564 | 0.034919 | 0.066596 | 0.015204 | 0.017843
2021-11-20 08:15 | 1.1434 | 1.0229 | 0.85347 | 0.6999 | 0.060884 | 0.083816 | 0.026461 | 0.02926
2021-11-20 08:30 | 0.76363 | 1.0433 | 0.58395 | 0.47545 | 0.086849 | 0.10964 | 0.037718 | 0.040678
2021-11-20 08:45 | 0.59212 | 1.0093 | 0.45736 | 0.58804 | 0.098673 | 0.10958 | 0.046717 | 0.047834
2021-11-20 09:00 | 0.4737 | 1.078 | 0.60029 | 0.63587 | 0.083309 | 0.11154 | 0.051532 | 0.047831
2021-11-20 09:15 | 0.57987 | 1.0825 | 0.46553 | 0.66154 | 0.067946 | 0.11779 | 0.056346 | 0.047829
2021-11-20 09:30 | 1.2863 | 1.0109 | 0.48595 | 0.5052 | 0.052582 | 0.13563 | 0.061161 | 0.047826
2021-11-20 09:45 | 2.5931 | 1.0855 | 0.47778 | 0.5472 | 0.042201 | 0.154 | 0.064336 | 0.05352
2021-11-20 10:00 | 1.858 | 1.0519 | 0.39407 | 0.66037 | 0.041413 | 0.18364 | 0.064469 | 0.068304
2021-11-20 10:15 | 1.8376 | 1.1165 | 0.37365 | 0.60058 | 0.040626 | 0.1653 | 0.064601 | 0.083088
2021-11-20 10:30 | 1.8274 | 1.1791 | 0.36956 | 0.96693 | 0.039839 | 0.18093 | 0.064734 | 0.097872
2021-11-20 10:45 | 1.7151 | 1.2018 | 0.41244 | 0.6681 | 0.039741 | 0.18983 | 0.067847 | 0.10876
2021-11-20 11:00 | 0.58395 | 1.0519 | 0.35221 | 0.74569 | 0.040973 | 0.21393 | 0.076504 | 0.11396
2021-11-20 11:15 | 0.64521 | 1.1155 | 0.30014 | 1.0082 | 0.042206 | 0.2341 | 0.085161 | 0.11917
2021-11-20 11:30 | 0.63296 | 1.0482 | 0.34098 | 0.92202 | 0.043438 | 0.23799 | 0.093818 | 0.12437
2021-11-20 11:45 | 0.49003 | 1.1059 | 0.31648 | 0.72717 | 0.043467 | 0.23842 | 0.096615 | 0.12724
2021-11-20 12:00 | 0.39304 | 1.0821 | 0.22153 | 0.7333 | 0.041172 | 0.23447 | 0.088501 | 0.12559
2021-11-20 12:15 | 0.34506 | 1.1318 | 0.22358 | 1.1469 | 0.038878 | 0.23244 | 0.080387 | 0.12393
2021-11-20 12:30 | 0.31546 | 1.1683 | 0.22256 | 0.84326 | 0.036583 | 0.22729 | 0.072272 | 0.12228
2021-11-20 12:45 | 3.4813 | 1.1929 | 0.29504 | 0.98312 | 0.03477 | 0.2103 | 0.065948 | 0.12133
2021-11-20 13:00 | 3.471 | 1.0986 | 0.28381 | 0.97233 | 0.03389 | 0.21611 | 0.062964 | 0.12214
2021-11-20 13:15 | 3.3894 | 1.0913 | 0.33792 | 0.79965 | 0.03301 | 0.19495 | 0.059979 | 0.12296
2021-11-20 13:30 | 4.8366 | 1.132 | 0.24195 | 1.1974 | 0.03213 | 0.1681 | 0.056994 | 0.12377
2021-11-20 13:45 | 4.4319 | 1.0583 | 0.22358 | 1.0088 | 0.030213 | 0.1643 | 0.051953 | 0.11819
2021-11-20 14:00 | 2.7973 | 1.1153 | 0.2246 | 1.3353 | 0.026286 | 0.16724 | 0.043071 | 0.10028
2021-11-20 14:15 | 1.4497 | 1.1136 | 0.22256 | 1.293 | 0.022359 | 0.16313 | 0.03419 | 0.082369
2021-11-20 14:30 | 0.73504 | 1.1136 | 0.29708 | 1.3817 | 0.018432 | 0.16832 | 0.025308 | 0.064456
2021-11-20 14:45 | 0.61662 | 1.0566 | 0.30627 | 0.81351 | 0.015698 | 0.15615 | 0.018307 | 0.049885
2021-11-20 15:00 | 0.29708 | 1.1195 | 0.25318 | 1.1212 | 0.015281 | 0.13591 | 0.014825 | 0.042271
2021-11-20 15:15 | 0.31546 | 1.0836 | 0.25625 | 1.1613 | 0.014863 | 0.12209 | 0.011343 | 0.034657
2021-11-20 15:30 | 0.30116 | 1.0946 | 0.25727 | 1.0606 | 0.014446 | 0.11558 | 0.00786 | 0.027043
2021-11-20 15:45 | 0.31444 | 1.0758 | 0.3369 | 0.83363 | 0.012966 | 0.09527 | 0.005104 | 0.020261
2021-11-20 16:00 | 0.37671 | 1.085 | 0.32158 | 0.91049 | 0.009424 | 0.069259 | 0.003706 | 0.014674
2021-11-20 16:15 | 0.35629 | 1.0987 | 0.24706 | 1.0215 | 0.005882 | 0.037646 | 0.002309 | 0.009088
2021-11-20 16:30 | 0.26135 | 1.0697 | 0.26135 | 1.3667 | 0.00234 | 0.01455 | 0.000912 | 0.003501
2021-11-20 16:45 | 0.21847 | 0.93227 | 0.44511 | 1.303 | 0 | 0 | 0 | 0
2021-11-20 17:00 | 0.21949 | 0.91156 | 0.40836 | 1.3449 | 0 | 0 | 0 | 0
2021-11-20 17:15 | 0.21337 | 1.0102 | 0.2981 | 0.91006 | 0 | 0 | 0 | 0
2021-11-20 17:30 | 0.19397 | 1.0162 | 0.43286 | 0.9506 | 0 | 0 | 0 | 0
2021-11-20 17:45 | 0.25727 | 1.0012 | 0.4982 | 0.92902 | 0 | 0 | 0 | 0
2021-11-20 18:00 | 0.48595 | 1.0728 | 0.40121 | 1.0464 | 0 | 0 | 0 | 0
2021-11-20 18:15 | 0.40121 | 1.0516 | 0.51453 | 1.07 | 0 | 0 | 0 | 0
2021-11-20 18:30 | 0.36344 | 1.1418 | 0.39202 | 1.0072 | 0 | 0 | 0 | 0
2021-11-20 18:45 | 0.3665 | 1.1297 | 0.42469 | 1.0383 | 0 | 0 | 0 | 0
2021-11-20 19:00 | 0.51045 | 1.0157 | 0.78405 | 1.0186 | 0 | 0 | 0 | 0
2021-11-20 19:15 | 0.52678 | 1.0111 | 0.89022 | 1.3929 | 0 | 0 | 0 | 0
2021-11-20 19:30 | 0.53087 | 1.2715 | 3.0525 | 1.9547 | 0 | 0 | 0 | 0
2021-11-20 19:45 | 0.62479 | 1.2149 | 4.134 | 2.0068 | 0 | 0 | 0 | 0
2021-11-20 20:00 | 0.65337 | 0.92094 | 0.93922 | 1.0025 | 0 | 0 | 0 | 0
2021-11-20 20:15 | 0.72279 | 0.95079 | 0.5717 | 1.1113 | 0 | 0 | 0 | 0
2021-11-20 20:30 | 0.88205 | 0.93604 | 0.53087 | 0.89955 | 0 | 0 | 0 | 0
2021-11-20 20:45 | 0.86164 | 0.95923 | 0.62479 | 1.0345 | 0 | 0 | 0 | 0
2021-11-20 21:00 | 0.40836 | 0.86978 | 0.75546 | 0.81351 | 0 | 0 | 0 | 0
2021-11-20 21:15 | 0.41653 | 0.83962 | 0.80855 | 0.81468 | 0 | 0 | 0 | 0
2021-11-20 21:30 | 0.43286 | 0.95074 | 0.38182 | 0.73388 | 0 | 0 | 0 | 0
2021-11-20 21:45 | 0.49411 | 0.60681 | 0.27973 | 0.50549 | 0 | 0 | 0 | 0
2021-11-20 22:00 | 0.41653 | 0.60681 | 0.28381 | 0.46947 | 0 | 0 | 0 | 0
2021-11-20 22:15 | 0.40427 | 0.60681 | 0.35527 | 0.43301 | 0 | 0 | 0 | 0
2021-11-20 22:30 | 0.29096 | 0.60681 | 0.4737 | 0.42484 | 0 | 0 | 0 | 0
2021-11-20 22:45 | 0.29402 | 0.6086 | 0.45328 | 0.39042 | 0 | 0 | 0 | 0
2021-11-20 23:00 | 0.28483 | 1.1002 | 3.2771 | 2.012 | 0 | 0 | 0 | 0
2021-11-20 23:15 | 0.28279 | 0.99558 | 3.4608 | 2.1477 | 0 | 0 | 0 | 0
2021-11-20 23:30 | 0.35017 | 1.0077 | 3.42 | 2.1302 | 0 | 0 | 0 | 0
2021-11-20 23:45 | 0.37058 | 0.97555 | 3.3996 | 2.1149 | 0 | 0 | 0 | 0
2021-11-21 | 0.46144 | 0.87452 | 3.3281 | 2.0575 | 0 | 0 | 0 | 0
2021-11-21 00:15 | 0.44103 | 0.84148 | 3.369 | 1.8838 | 0 | 0 | 0 | 0
2021-11-21 00:30 | 0.2736 | 0.81403 | 3.369 | 1.7559 | 0 | 0 | 0 | 0
2021-11-21 00:45 | 0.19499 | 0.88364 | 3.4608 | 1.6482 | 0 | 0 | 0 | 0
2021-11-21 01:00 | 0.31444 | 0.88364 | 3.5017 | 1.739 | 0 | 0 | 0 | 0
2021-11-21 01:15 | 0.23889 | 0.91186 | 3.3587 | 1.6401 | 0 | 0 | 0 | 0
2021-11-21 01:30 | 0.26237 | 0.88364 | 3.3587 | 1.6358 | 0 | 0 | 0 | 0
2021-11-21 01:45 | 0.35731 | 0.88364 | 3.369 | 1.6011 | 0 | 0 | 0 | 0
2021-11-21 02:00 | 0.37671 | 0.86759 | 3.3587 | 1.5943 | 0 | 0 | 0 | 0
2021-11-21 02:15 | 0.28789 | 0.86263 | 3.369 | 1.6422 | 0 | 0 | 0 | 0
2021-11-21 02:30 | 0.25829 | 0.89581 | 3.5017 | 1.6524 | 0 | 0 | 0 | 0
2021-11-21 02:45 | 0.36446 | 0.89581 | 3.5731 | 1.6782 | 0 | 0 | 0 | 0
2021-11-21 03:00 | 0.65746 | 0.91442 | 3.7773 | 1.7702 | 0 | 0 | 0 | 0
2021-11-21 03:15 | 0.37263 | 0.86759 | 3.4506 | 1.6302 | 0 | 0 | 0 | 0
2021-11-21 03:30 | 0.36854 | 0.86263 | 3.42 | 1.635 | 0 | 0 | 0 | 0
2021-11-21 03:45 | 0.39407 | 0.89412 | 3.4915 | 1.647 | 0 | 0 | 0 | 0
2021-11-21 04:00 | 0.38182 | 0.8921 | 3.2771 | 1.5974 | 0 | 0 | 0 | 0
2021-11-21 04:15 | 0.3614 | 1.0479 | 1.7457 | 1.1834 | 0 | 0 | 0 | 0
2021-11-21 04:30 | 0.26748 | 0.7938 | 0.91881 | 0.93047 | 0 | 0 | 0 | 0
2021-11-21 04:45 | 0.26441 | 0.92177 | 0.53087 | 0.80884 | 0 | 0 | 0 | 0
2021-11-21 05:00 | 0.33587 | 0.89121 | 0.44511 | 0.77194 | 0 | 0 | 0 | 0
2021-11-21 05:15 | 0.38284 | 0.93534 | 0.37569 | 0.76523 | 0 | 0 | 0 | 0
2021-11-21 05:30 | 0.26339 | 0.78182 | 0.30423 | 0.7384 | 0 | 0 | 0 | 0
2021-11-21 05:45 | 0.23889 | 0.97274 | 0.21745 | 0.77238 | 0 | 0 | 0 | 0
2021-11-21 06:00 | 0.26339 | 0.78182 | 0.2736 | 0.73913 | 0 | 0 | 0 | 0
2021-11-21 06:15 | 0.27564 | 0.98056 | 0.29912 | 0.73767 | 0 | 0 | 0 | 0
2021-11-21 06:30 | 0.39611 | 0.95086 | 0.23685 | 0.74569 | 0 | 0 | 0 | 0
2021-11-21 06:45 | 0.26135 | 0.71019 | 0.24399 | 0.55128 | 0 | 0.001326 | 5e-06 | 1.4e-05
2021-11-21 07:00 | 0.23174 | 0.62805 | 0.38692 | 0.36067 | 0 | 0.004042 | 2e-05 | 5.2e-05
2021-11-21 07:15 | 0.28993 | 0.64591 | 0.30525 | 0.31444 | 0 | 0.004898 | 3.5e-05 | 9e-05
2021-11-21 07:30 | 0.38386 | 0.68529 | 0.30218 | 0.34623 | 0 | 0.008789 | 5e-05 | 0.000128
2021-11-21 07:45 | 0.27156 | 0.76498 | 0.2981 | 0.45517 | 0.001003 | 0.047943 | 0.008953 | 0.004804
2021-11-21 08:00 | 0.28279 | 1.0203 | 0.71463 | 1.0829 | 0.004003 | 0.062596 | 0.034919 | 0.017833
2021-11-21 08:15 | 0.40019 | 0.93762 | 1.1434 | 0.7629 | 0.007002 | 0.078611 | 0.060884 | 0.030862
2021-11-21 08:30 | 0.81263 | 1.0202 | 0.76363 | 0.48886 | 0.010002 | 0.10692 | 0.086849 | 0.043891
2021-11-21 08:45 | 0.84122 | 1.152 | 0.59212 | 0.57462 | 0.013028 | 0.11841 | 0.098673 | 0.051822
2021-11-21 09:00 | 0.89431 | 1.2241 | 0.4737 | 0.59854 | 0.016108 | 0.11577 | 0.083309 | 0.050488
2021-11-21 09:15 | 0.57987 | 1.1568 | 0.57987 | 0.63179 | 0.019188 | 0.11972 | 0.067946 | 0.049153
2021-11-21 09:30 | 0.65337 | 1.2509 | 1.2863 | 0.60262 | 0.022268 | 0.13434 | 0.052582 | 0.047818
2021-11-21 09:45 | 0.47778 | 1.2196 | 2.5931 | 0.84764 | 0.025551 | 0.15254 | 0.042201 | 0.049816
2021-11-21 10:00 | 0.51453 | 1.2191 | 1.858 | 0.84997 | 0.029241 | 0.17032 | 0.041413 | 0.057648
2021-11-21 10:15 | 0.5227 | 1.3299 | 1.8376 | 0.76334 | 0.03293 | 0.16939 | 0.040626 | 0.065479
2021-11-21 10:30 | 2.8585 | 1.6312 | 1.8274 | 1.116 | 0.03662 | 0.1854 | 0.039839 | 0.073311
2021-11-21 10:45 | 0.79222 | 1.2332 | 1.7151 | 0.78244 | 0.039241 | 0.1742 | 0.039741 | 0.081641
2021-11-21 11:00 | 0.58395 | 1.3285 | 0.58395 | 0.75911 | 0.039723 | 0.1643 | 0.040973 | 0.090956
2021-11-21 11:15 | 0.65337 | 1.1661 | 0.64521 | 1.0193 | 0.040206 | 0.16436 | 0.042206 | 0.10027
2021-11-21 11:30 | 0.51862 | 1.3331 | 0.63296 | 0.92843 | 0.040688 | 0.15744 | 0.043438 | 0.10958
2021-11-21 11:45 | 0.42469 | 1.3354 | 0.49003 | 0.75794 | 0.043825 | 0.15773 | 0.043467 | 0.11561
2021-11-21 12:00 | 0.42878 | 1.3354 | 0.39304 | 0.69786 | 0.052282 | 0.16534 | 0.041172 | 0.11559
2021-11-21 12:15 | 0.50636 | 1.1294 | 0.34506 | 1.1481 | 0.060739 | 0.16596 | 0.038878 | 0.11558
2021-11-21 12:30 | 3.2056 | 1.6926 | 0.31546 | 0.83378 | 0.069196 | 0.16257 | 0.036583 | 0.11557
2021-11-21 12:45 | 4.1219 | 1.727 | 3.4813 | 1.4231 | 0.08211 | 0.16406 | 0.03477 | 0.11632
2021-11-21 13:00 | 4.0964 | 1.7837 | 3.471 | 1.4069 | 0.10397 | 0.16067 | 0.03389 | 0.11897
2021-11-21 13:15 | 2.9912 | 1.6042 | 3.3894 | 1.2322 | 0.12583 | 0.15729 | 0.03301 | 0.12162
2021-11-21 13:30 | 3.3383 | 1.7674 | 4.8366 | 1.8491 | 0.14769 | 0.15225 | 0.03213 | 0.12427
2021-11-21 13:45 | 1.5313 | 1.7692 | 4.4319 | 1.6091 | 0.14995 | 0.15109 | 0.030213 | 0.11839
2021-11-21 14:00 | 0.45328 | 1.8341 | 2.7973 | 1.7038 | 0.11282 | 0.17772 | 0.026286 | 0.096891
2021-11-21 14:15 | 0.44103 | 1.6691 | 1.4497 | 1.452 | 0.075684 | 0.18154 | 0.022359 | 0.075391
2021-11-21 14:30 | 0.40325 | 1.6586 | 0.73504 | 1.4519 | 0.03855 | 0.16674 | 0.018432 | 0.053891
2021-11-21 14:45 | 0.41653 | 1.5342 | 0.61662 | 0.87024 | 0.015866 | 0.13942 | 0.015698 | 0.038056
2021-11-21 15:00 | 0.50636 | 1.5375 | 0.29708 | 1.1343 | 0.022273 | 0.1246 | 0.015281 | 0.032772
2021-11-21 15:15 | 0.59212 | 1.5375 | 0.31546 | 1.1595 | 0.02868 | 0.10978 | 0.014863 | 0.027488
2021-11-21 15:30 | 0.30525 | 1.6118 | 0.30116 | 1.0572 | 0.035087 | 0.097759 | 0.014446 | 0.022205
2021-11-21 15:45 | 0.32158 | 1.5724 | 0.31444 | 0.84661 | 0.036107 | 0.083554 | 0.012966 | 0.017194
2021-11-21 16:00 | 0.30831 | 1.5345 | 0.37671 | 0.92989 | 0.026265 | 0.061234 | 0.009424 | 0.012467
2021-11-21 16:15 | 0.30423 | 1.5043 | 0.35629 | 1.036 | 0.016424 | 0.037742 | 0.005882 | 0.007739
2021-11-21 16:30 | 0.32669 | 1.6849 | 0.26135 | 1.3558 | 0.006582 | 0.013465 | 0.00234 | 0.003012
2021-11-21 16:45 | 0.36752 | 1.7042 | 0.21847 | 1.2426 | 0 | 0 | 0 | 0
2021-11-21 17:00 | 0.35935 | 1.8678 | 0.21949 | 1.3395 | 0 | 0 | 0 | 0
2021-11-21 17:15 | 0.29708 | 1.5873 | 0.21337 | 0.90189 | 0 | 0 | 0 | 0
2021-11-21 17:30 | 0.22562 | 1.4507 | 0.19397 | 0.91822 | 0 | 0 | 0 | 0
2021-11-21 17:45 | 0.31341 | 1.4817 | 0.25727 | 0.92216 | 0 | 0 | 0 | 0
2021-11-21 18:00 | 0.61254 | 1.6189 | 0.48595 | 1.0584 | 0 | 0 | 0 | 0
2021-11-21 18:15 | 0.67379 | 1.6189 | 0.40121 | 1.0725 | 0 | 0 | 0 | 0
2021-11-21 18:30 | 0.65337 | 1.542 | 0.36344 | 0.98794 | 0 | 0 | 0 | 0
2021-11-21 18:45 | 0.52678 | 1.5848 | 0.3665 | 1.0218 | 0 | 0 | 0 | 0
2021-11-21 19:00 | 0.46144 | 1.5988 | 0.51045 | 1.0273 | 0 | 0 | 0 | 0
2021-11-21 19:15 | 0.87797 | 1.8862 | 0.52678 | 1.4023 | 0 | 0 | 0 | 0
2021-11-21 19:30 | 0.73096 | 1.9252 | 0.53087 | 1.9576 | 0 | 0 | 0 | 0
2021-11-21 19:45 | 0.71054 | 1.9632 | 0.62479 | 2.0261 | 0 | 0 | 0 | 0
2021-11-21 20:00 | 0.8208 | 1.213 | 0.65337 | 1.0334 | 0 | 0 | 0 | 0
2021-11-21 20:15 | 0.57578 | 1.3194 | 0.72279 | 1.1669 | 0 | 0 | 0 | 0
2021-11-21 20:30 | 1.7559 | 1.2638 | 0.88205 | 0.98021 | 0 | 0 | 0 | 0
2021-11-21 20:45 | 1.7355 | 1.4891 | 0.86164 | 1.1126 | 0 | 0 | 0 | 0
2021-11-21 21:00 | 1.1536 | 1.0577 | 0.40836 | 0.82459 | 0 | 0 | 0 | 0
2021-11-21 21:15 | 0.53495 | 1.0161 | 0.41653 | 0.81351 | 0 | 0 | 0 | 0
2021-11-21 21:30 | 0.47778 | 1.1641 | 0.43286 | 0.73213 | 0 | 0 | 0 | 0
2021-11-21 21:45 | 0.44919 | 0.6919 | 0.49411 | 0.50316 | 0 | 0 | 0 | 0
2021-11-21 22:00 | 0.44103 | 0.6919 | 0.41653 | 0.45371 | 0 | 0 | 0 | 0
2021-11-21 22:15 | 0.45736 | 0.6919 | 0.40427 | 0.412 | 0 | 0 | 0 | 0
2021-11-21 22:30 | 0.38998 | 0.70626 | 0.29096 | 0.38065 | 0 | 0 | 0 | 0
2021-11-21 22:45 | 0.36242 | 0.70626 | 0.29402 | 0.34725 | 0 | 0 | 0 | 0
2021-11-21 23:00 | 0.35629 | 1.896 | 0.28483 | 1.9687 | 0 | 0 | 0 | 0
2021-11-21 23:15 | 0.35425 | 2.0307 | 0.28279 | 2.1152 | 0 | 0 | 0 | 0
2021-11-21 23:30 | 0.37569 | 1.9566 | 0.35017 | 2.1226 | 0 | 0 | 0 | 0
2021-11-21 23:45 | 0.45736 | 1.9126 | 0.37058 | 2.1184 | 0 | 0 | 0 | 0
2021-11-22 | 0.48595 | 2.24 | 0.46144 | 2.0873 | 0 | 0 | 0 | 0
2021-11-22 00:15 | 0.53087 | 1.2443 | 0.44103 | 1.9175 | 0 | 0 | 0 | 0
2021-11-22 00:30 | 0.49003 | 1.1783 | 0.2736 | 1.76 | 0 | 0 | 0 | 0
2021-11-22 00:45 | 0.41653 | 1.0116 | 0.19499 | 1.6289 | 0 | 0 | 0 | 0
2021-11-22 01:00 | 0.5227 | 1.1517 | 0.31444 | 1.7406 | 0 | 0 | 0 | 0
2021-11-22 01:15 | 0.31444 | 0.99346 | 0.23889 | 1.6416 | 0 | 0 | 0 | 0
2021-11-22 01:30 | 0.22051 | 1.027 | 0.26237 | 1.6394 | 0 | 0 | 0 | 0
2021-11-22 01:45 | 0.3226 | 1.027 | 0.35731 | 1.6193 | 0 | 0 | 0 | 0
2021-11-22 02:00 | 0.34098 | 0.96026 | 0.37671 | 1.6142 | 0 | 0 | 0 | 0
2021-11-22 02:15 | 0.27258 | 0.92507 | 0.28789 | 1.6343 | 0 | 0 | 0 | 0
2021-11-22 02:30 | 0.2685 | 0.92675 | 0.25829 | 1.6477 | 0 | 0 | 0 | 0
2021-11-22 02:45 | 0.22868 | 0.92675 | 0.36446 | 1.6975 | 0 | 0 | 0 | 0
2021-11-22 03:00 | 0.24502 | 1.0454 | 0.65746 | 1.8313 | 0 | 0 | 0 | 0
2021-11-22 03:15 | 0.28993 | 0.96026 | 0.37263 | 1.6487 | 0 | 0 | 0 | 0
2021-11-22 03:30 | 0.3226 | 0.92507 | 0.36854 | 1.6442 | 0 | 0 | 0 | 0
2021-11-22 03:45 | 0.44511 | 0.92507 | 0.39407 | 1.6629 | 0 | 0 | 0 | 0
2021-11-22 04:00 | 0.63296 | 0.92507 | 0.38182 | 1.6177 | 0 | 0 | 0 | 0
2021-11-22 04:15 | 0.34302 | 0.86014 | 0.3614 | 1.2006 | 0 | 0 | 0 | 0
2021-11-22 04:30 | 0.22256 | 0.85675 | 0.26748 | 0.92114 | 0 | 0 | 0 | 0
2021-11-22 04:45 | 0.34813 | 0.79972 | 0.26441 | 0.81132 | 0 | 0 | 0 | 0
2021-11-22 05:00 | 0.38182 | 0.76916 | 0.33587 | 0.78638 | 0 | 0 | 0 | 0
2021-11-22 05:15 | 0.40427 | 0.80379 | 0.38284 | 0.78274 | 0 | 0 | 0 | 0
2021-11-22 05:30 | 0.35221 | 0.81887 | 0.26339 | 0.72921 | 0 | 0 | 0 | 0
2021-11-22 05:45 | 0.24297 | 0.80379 | 0.23889 | 0.72075 | 0 | 0 | 0 | 0
2021-11-22 06:00 | 0.22256 | 0.81887 | 0.26339 | 0.72775 | 0 | 0 | 0 | 0
2021-11-22 06:15 | 0.32158 | 0.78003 | 0.27564 | 0.73738 | 0 | 0 | 0 | 0
2021-11-22 06:30 | 0.27564 | 0.78003 | 0.39611 | 0.75211 | 0 | 0 | 0 | 0
2021-11-22 06:45 | 0.28789 | 0.63923 | 0.26135 | 0.53655 | 0 | 0.000492 | 0 | 1.4e-05
2021-11-22 07:00 | 0.28381 | 0.53551 | 0.23174 | 0.34244 | 0 | 0 | 0 | 5.2e-05
2021-11-22 07:15 | 0.35527 | 0.63087 | 0.28993 | 0.32056 | 0 | 0 | 0 | 9e-05
2021-11-22 07:30 | 0.37161 | 0.65185 | 0.38386 | 0.35731 | 0 | 0.002816 | 0 | 0.000128
2021-11-22 07:45 | 0.26748 | 0.76926 | 0.27156 | 0.4508 | 0.007546 | 0.068757 | 0.001003 | 0.004911
2021-11-22 08:00 | 0.23991 | 1.0274 | 0.28279 | 1.0715 | 0.030689 | 0.081471 | 0.004003 | 0.018274
2021-11-22 08:15 | 0.25114 | 0.93185 | 0.40019 | 0.77997 | 0.053832 | 0.11457 | 0.007002 | 0.031638
2021-11-22 08:30 | 0.30218 | 0.96178 | 0.81263 | 0.56164 | 0.076975 | 0.13245 | 0.010002 | 0.045001
2021-11-22 08:45 | 0.35119 | 1.0371 | 0.84122 | 0.60204 | 0.086737 | 0.13322 | 0.013028 | 0.053208
2021-11-22 09:00 | 0.85755 | 1.0961 | 0.89431 | 0.61779 | 0.068799 | 0.14539 | 0.016108 | 0.052059
2021-11-22 09:15 | 0.91881 | 1.0253 | 0.57987 | 0.58687 | 0.05086 | 0.15565 | 0.019188 | 0.050909
2021-11-22 09:30 | 0.53903 | 1.1092 | 0.65337 | 0.63471 | 0.032922 | 0.17121 | 0.022268 | 0.04976
2021-11-22 09:45 | 0.49411 | 1.0646 | 0.47778 | 0.86572 | 0.024683 | 0.19659 | 0.025551 | 0.051586
2021-11-22 10:00 | 0.6207 | 1.1239 | 0.51453 | 0.70325 | 0.036554 | 0.2195 | 0.029241 | 0.058705
2021-11-22 10:15 | 0.67379 | 1.1239 | 0.5227 | 0.733 | 0.048426 | 0.2424 | 0.03293 | 0.065823
2021-11-22 10:30 | 0.62887 | 1.1731 | 2.8585 | 1.0562 | 0.060297 | 0.26531 | 0.03662 | 0.072941
2021-11-22 10:45 | 0.46553 | 1.2516 | 0.79222 | 0.72206 | 0.073832 | 0.27836 | 0.039241 | 0.080437
2021-11-22 11:00 | 0.5227 | 1.1541 | 0.58395 | 0.77428 | 0.09082 | 0.28144 | 0.039723 | 0.08866
2021-11-22 11:15 | 1.8989 | 1.1956 | 0.65337 | 1.0734 | 0.10781 | 0.28747 | 0.040206 | 0.096883
2021-11-22 11:30 | 0.89839 | 1.2253 | 0.51862 | 0.95133 | 0.1248 | 0.29192 | 0.040688 | 0.10511
2021-11-22 11:45 | 0.38896 | 1.2343 | 0.42469 | 0.77224 | 0.15611 | 0.29245 | 0.043825 | 0.10968
2021-11-22 12:00 | 0.98006 | 1.2536 | 0.42878 | 0.71332 | 0.21719 | 0.28918 | 0.052282 | 0.10781
2021-11-22 12:15 | 0.30933 | 1.1832 | 0.50636 | 0.89372 | 0.27829 | 0.29027 | 0.060739 | 0.10595
2021-11-22 12:30 | 0.27258 | 1.164 | 3.2056 | 0.76232 | 0.33937 | 0.2776 | 0.069196 | 0.10408
2021-11-22 12:45 | 0.23685 | 1.3924 | 4.1219 | 1.5044 | 0.37872 | 0.27682 | 0.08211 | 0.10629
2021-11-22 13:00 | 1.2965 | 1.3924 | 4.0964 | 1.5021 | 0.37279 | 0.25849 | 0.10397 | 0.11582
2021-11-22 13:15 | 2.8993 | 1.2093 | 2.9912 | 1.1724 | 0.36685 | 0.23779 | 0.12583 | 0.12536
2021-11-22 13:30 | 1.2047 | 1.6739 | 3.3383 | 1.4321 | 0.36091 | 0.23264 | 0.14769 | 0.13489
2021-11-22 13:45 | 0.36956 | 1.4899 | 1.5313 | 1.3189 | 0.35845 | 0.22738 | 0.14995 | 0.13113
2021-11-22 14:00 | 1.3476 | 1.4375 | 0.45328 | 1.1052 | 0.36323 | 0.25031 | 0.11282 | 0.10302
2021-11-22 14:15 | 1.4497 | 1.2132 | 0.44103 | 1.0002 | 0.36801 | 0.24416 | 0.075684 | 0.074913
2021-11-22 14:30 | 0.69013 | 1.2102 | 0.40325 | 0.98881 | 0.37279 | 0.23276 | 0.03855 | 0.046804
2021-11-22 14:45 | 0.5717 | 0.99108 | 0.41653 | 0.42221 | 0.34682 | 0.2193 | 0.015866 | 0.027858
2021-11-22 15:00 | 0.49411 | 1.017 | 0.50636 | 0.36563 | 0.25659 | 0.196 | 0.022273 | 0.025866
2021-11-22 15:15 | 0.5227 | 1.0135 | 0.59212 | 0.51162 | 0.16636 | 0.17269 | 0.02868 | 0.023873
2021-11-22 15:30 | 0.28483 | 1.0866 | 0.30525 | 0.59183 | 0.076135 | 0.14976 | 0.035087 | 0.021881
2021-11-22 15:45 | 0.21235 | 1.0039 | 0.32158 | 0.38502 | 0.013861 | 0.12773 | 0.036107 | 0.018846
2021-11-22 16:00 | 0.2491 | 1.0533 | 0.30831 | 0.48974 | 0.010091 | 0.094765 | 0.026265 | 0.013683
2021-11-22 16:15 | 0.86572 | 0.83946 | 0.30423 | 0.48011 | 0.006322 | 0.061149 | 0.016424 | 0.008521
2021-11-22 16:30 | 2.0622 | 0.9831 | 0.32669 | 0.58176 | 0.002552 | 0.022407 | 0.006582 | 0.003359
2021-11-22 16:45 | 2.0622 | 0.9831 | 0.36752 | 0.58833 | 0 | 0 | 0 | 0
2021-11-22 17:00 | 4.8208 | 1.2805 | 0.35935 | 0.89785 | 0 | 0 | 0 | 0
2021-11-22 17:15 | 5.2338 | 0.86771 | 0.29708 | 0.45138 | 0 | 0 | 0 | 0
2021-11-22 17:30 | 5.0578 | 0.91873 | 0.22562 | 0.42688 | 0 | 0 | 0 | 0
2021-11-22 17:45 | 3.7977 | 0.9102 | 0.31341 | 0.43315 | 0 | 0 | 0 | 0
2021-11-22 18:00 | 3.8998 | 1.0765 | 0.61254 | 0.59022 | 0 | 0 | 0 | 0
2021-11-22 18:15 | 3.8386 | 1.1216 | 0.67379 | 0.59999 | 0 | 0 | 0 | 0
2021-11-22 18:30 | 5.5198 | 1.013 | 0.65337 | 0.51541 | 0 | 0 | 0 | 0
2021-11-22 18:45 | 4.8895 | 0.96778 | 0.52678 | 0.55012 | 0 | 0 | 0 | 0
2021-11-22 19:00 | 4.6999 | 0.96778 | 0.46144 | 0.53612 | 0 | 0 | 0 | 0
2021-11-22 19:15 | 4.6125 | 1.108 | 0.87797 | 0.74292 | 0 | 0 | 0 | 0
2021-11-22 19:30 | 4.6379 | 1.3438 | 0.73096 | 1.3613 | 0 | 0 | 0 | 0
2021-11-22 19:45 | 4.5674 | 1.4048 | 0.71054 | 1.5851 | 0 | 0 | 0 | 0
2021-11-22 20:00 | 4.0958 | 0.99561 | 0.8208 | 0.91735 | 0 | 0 | 0 | 0
2021-11-22 20:15 | 2.3276 | 1.0845 | 0.57578 | 0.8787 | 0 | 0 | 0 | 0
2021-11-22 20:30 | 2.2562 | 1.0461 | 1.7559 | 0.86353 | 0 | 0 | 0 | 0
2021-11-22 20:45 | 2.1133 | 1.1391 | 1.7355 | 0.97846 | 0 | 0 | 0 | 0
2021-11-22 21:00 | 2.8789 | 0.88812 | 1.1536 | 0.65979 | 0 | 0 | 0 | 0
2021-11-22 21:15 | 0.60029 | 0.82232 | 0.53495 | 0.58074 | 0 | 0 | 0 | 0
2021-11-22 21:30 | 0.72279 | 0.6276 | 0.47778 | 0.52474 | 0 | 0 | 0 | 0
2021-11-22 21:45 | 0.37977 | 0.58741 | 0.44919 | 0.48216 | 0 | 0 | 0 | 0
2021-11-22 22:00 | 0.45328 | 0.58741 | 0.44103 | 0.44088 | 0 | 0 | 0 | 0
2021-11-22 22:15 | 0.47778 | 0.64153 | 0.45736 | 0.41025 | 0 | 0 | 0 | 0
2021-11-22 22:30 | 0.44103 | 0.61942 | 0.38998 | 0.38152 | 0 | 0 | 0 | 0
2021-11-22 22:45 | 0.3175 | 0.61942 | 0.36242 | 0.34185 | 0 | 0 | 0 | 0
2021-11-22 23:00 | 3.1546 | 1.0265 | 0.35629 | 1.5558 | 0 | 0 | 0 | 0
2021-11-22 23:15 | 3.3894 | 0.91168 | 0.35425 | 1.648 | 0 | 0 | 0 | 0
2021-11-22 23:30 | 3.4098 | 0.97394 | 0.37569 | 1.6746 | 0 | 0 | 0 | 0
2021-11-22 23:45 | 3.3485 | 1.027 | 0.45736 | 1.6878 | 0 | 0 | 0 | 0
2021-11-23 | 1.858 | 1.2021 | 0.48595 | 1.6754 | 0 | 0 | 0 | 0
2021-11-23 00:15 | 0.94739 | 1.1479 | 0.53087 | 1.6667 | 0 | 0 | 0 | 0
2021-11-23 00:30 | 0.64929 | 1.0184 | 0.49003 | 1.6492 | 0 | 0 | 0 | 0
2021-11-23 00:45 | 0.4737 | 1.047 | 0.41653 | 1.6097 | 0 | 0 | 0 | 0
2021-11-23 01:00 | 0.293 | 1.0184 | 0.5227 | 1.6916 | 0 | 0 | 0 | 0
2021-11-23 01:15 | 0.23583 | 1.0151 | 0.31444 | 1.6366 | 0 | 0 | 0 | 0
2021-11-23 01:30 | 0.23889 | 0.91721 | 0.22051 | 1.6175 | 0 | 0 | 0 | 0
2021-11-23 01:45 | 0.34098 | 1.1479 | 0.3226 | 1.627 | 0 | 0 | 0 | 0
2021-11-23 02:00 | 0.34608 | 1.1139 | 0.34098 | 1.6283 | 0 | 0 | 0 | 0
2021-11-23 02:15 | 0.32771 | 0.97944 | 0.27258 | 1.6382 | 0 | 0 | 0 | 0
2021-11-23 02:30 | 0.23991 | 0.98113 | 0.2685 | 1.649 | 0 | 0 | 0 | 0
2021-11-23 02:45 | 0.21745 | 1.0182 | 0.22868 | 1.6872 | 0 | 0 | 0 | 0
2021-11-23 03:00 | 0.21949 | 1.1966 | 0.24502 | 1.8165 | 0 | 0 | 0 | 0
2021-11-23 03:15 | 0.25012 | 1.1139 | 0.28993 | 1.6527 | 0 | 0 | 0 | 0
2021-11-23 03:30 | 0.22766 | 1.109 | 0.3226 | 1.6571 | 0 | 0 | 0 | 0
2021-11-23 03:45 | 0.293 | 1.109 | 0.44511 | 1.6934 | 0 | 0 | 0 | 0
2021-11-23 04:00 | 0.40427 | 1.2139 | 0.63296 | 1.675 | 0 | 0 | 0 | 0
2021-11-23 04:15 | 0.31341 | 0.99685 | 0.34302 | 1.2061 | 0 | 0 | 0 | 0
2021-11-23 04:30 | 0.23685 | 0.92663 | 0.22256 | 0.90495 | 0 | 0 | 0 | 0
2021-11-23 04:45 | 0.24093 | 0.92906 | 0.34813 | 0.82722 | 0 | 0 | 0 | 0
2021-11-23 05:00 | 0.22358 | 0.8985 | 0.38182 | 0.80884 | 0 | 0 | 0 | 0
2021-11-23 05:15 | 0.22766 | 0.90969 | 0.40427 | 0.80519 | 0 | 0 | 0 | 0
2021-11-23 05:30 | 0.29606 | 0.90725 | 0.35221 | 0.7349 | 0 | 0 | 0 | 0
2021-11-23 05:45 | 0.34098 | 0.93832 | 0.24297 | 0.7069 | 0 | 0 | 0 | 0
2021-11-23 06:00 | 0.24706 | 0.90725 | 0.22256 | 0.71857 | 0 | 0 | 0 | 0
2021-11-23 06:15 | 0.23889 | 0.92626 | 0.32158 | 0.75225 | 0 | 0 | 0 | 0
2021-11-23 06:30 | 0.26543 | 0.94399 | 0.27564 | 0.7543 | 0 | 0 | 0 | 0
2021-11-23 06:45 | 0.24093 | 0.7534 | 0.28789 | 0.53101 | 0 | 0.000464 | 0 | 9e-06
2021-11-23 07:00 | 0.41244 | 0.66345 | 0.28381 | 0.33398 | 0 | 0.000844 | 0 | 3.5e-05
2021-11-23 07:15 | 0.27258 | 0.67482 | 0.35527 | 0.33544 | 0 | 0 | 0 | 6.1e-05
2021-11-23 07:30 | 0.33281 | 0.66735 | 0.37161 | 0.36592 | 0 | 0.000578 | 0 | 8.7e-05
2021-11-23 07:45 | 0.77588 | 0.73653 | 0.26748 | 0.45153 | 0.039908 | 0.063309 | 0.007546 | 0.005676
2021-11-23 08:00 | 2.1745 | 1.0777 | 0.23991 | 0.92785 | 0.16546 | 0.094563 | 0.030689 | 0.021659
2021-11-23 08:15 | 0.98823 | 1.0257 | 0.25114 | 0.71609 | 0.29102 | 0.11806 | 0.053832 | 0.037641
2021-11-23 08:30 | 0.77997 | 0.85911 | 0.30218 | 0.55362 | 0.41658 | 0.15729 | 0.076975 | 0.053623
2021-11-23 08:45 | 0.51453 | 0.86758 | 0.35119 | 0.52445 | 0.5117 | 0.17332 | 0.086737 | 0.062841
2021-11-23 09:00 | 0.49411 | 1.0947 | 0.85755 | 0.64112 | 0.5414 | 0.17531 | 0.068799 | 0.059232
2021-11-23 09:15 | 0.53495 | 1.1493 | 0.91881 | 0.65046 | 0.5711 | 0.17322 | 0.05086 | 0.055624
2021-11-23 09:30 | 0.35323 | 1.1297 | 0.53903 | 0.63296 | 0.6008 | 0.19501 | 0.032922 | 0.052016
2021-11-23 09:45 | 0.43286 | 1.203 | 0.49411 | 0.8558 | 0.62375 | 0.22144 | 0.024683 | 0.052388
2021-11-23 10:00 | 0.62887 | 1.2867 | 0.6207 | 0.71083 | 0.63215 | 0.25098 | 0.036554 | 0.06031
2021-11-23 10:15 | 0.66971 | 1.333 | 0.67379 | 0.74642 | 0.64056 | 0.27719 | 0.048426 | 0.068232
2021-11-23 10:30 | 0.4737 | 1.2738 | 0.62887 | 1.0754 | 0.64897 | 0.30339 | 0.060297 | 0.076155
2021-11-23 10:45 | 0.42878 | 1.3588 | 0.46553 | 0.73534 | 0.65477 | 0.32742 | 0.073832 | 0.084963
2021-11-23 11:00 | 0.29198 | 1.1897 | 0.5227 | 0.59227 | 0.65497 | 0.32753 | 0.09082 | 0.095429
2021-11-23 11:15 | 0.25522 | 1.4804 | 1.8989 | 1.2787 | 0.65517 | 0.32765 | 0.10781 | 0.1059
2021-11-23 11:30 | 0.2981 | 1.2091 | 0.89839 | 1.0254 | 0.65536 | 0.30237 | 0.1248 | 0.11636
2021-11-23 11:45 | 0.40325 | 1.2096 | 0.38896 | 0.78099 | 0.65557 | 0.2859 | 0.15611 | 0.1254
2021-11-23 12:00 | 0.44511 | 1.2096 | 0.98006 | 0.80388 | 0.65577 | 0.30418 | 0.21719 | 0.13254
2021-11-23 12:15 | 0.33792 | 1.1708 | 0.30933 | 0.90393 | 0.65598 | 0.35136 | 0.27829 | 0.13967
2021-11-23 12:30 | 1.4395 | 1.3012 | 0.27258 | 0.77326 | 0.65619 | 0.31273 | 0.33937 | 0.14681
2021-11-23 12:45 | 1.7151 | 1.5808 | 0.23685 | 1.5101 | 0.65168 | 0.31063 | 0.37872 | 0.15507
2021-11-23 13:00 | 1.9499 | 1.4004 | 1.2965 | 1.6585 | 0.63697 | 0.31664 | 0.37279 | 0.16445
2021-11-23 13:15 | 0.53903 | 1.2943 | 2.8993 | 1.5526 | 0.62225 | 0.31951 | 0.36685 | 0.17382
2021-11-23 13:30 | 0.43694 | 1.3842 | 1.2047 | 1.561 | 0.60754 | 0.32814 | 0.36091 | 0.18319
2021-11-23 13:45 | 0.42061 | 1.3121 | 0.36956 | 1.0683 | 0.58981 | 0.32072 | 0.35845 | 0.17944
2021-11-23 14:00 | 0.3226 | 1.1944 | 1.3476 | 0.82226 | 0.56557 | 0.31593 | 0.36323 | 0.15186
2021-11-23 14:15 | 0.2736 | 1.1901 | 1.4497 | 0.74642 | 0.54132 | 0.29512 | 0.36801 | 0.12428
2021-11-23 14:30 | 0.27258 | 1.1813 | 0.69013 | 0.85405 | 0.51708 | 0.29148 | 0.37279 | 0.096702
2021-11-23 14:45 | 0.30014 | 1.0041 | 0.5717 | 0.4018 | 0.47533 | 0.27078 | 0.34682 | 0.074239
2021-11-23 15:00 | 0.46961 | 0.81405 | 0.49411 | 0.36446 | 0.39561 | 0.22383 | 0.25659 | 0.060113
2021-11-23 15:15 | 0.46553 | 0.8063 | 0.5227 | 0.36752 | 0.31589 | 0.20023 | 0.16636 | 0.045987
2021-11-23 15:30 | 0.36956 | 0.77704 | 0.28483 | 0.30729 | 0.23616 | 0.17798 | 0.076135 | 0.031861
2021-11-23 15:45 | 0.35323 | 0.78212 | 0.21235 | 0.31794 | 0.16726 | 0.12658 | 0.013861 | 0.020438
2021-11-23 16:00 | 0.35629 | 0.83502 | 0.2491 | 0.34448 | 0.12187 | 0.097616 | 0.010091 | 0.014844
2021-11-23 16:15 | 0.30525 | 0.83984 | 0.86572 | 0.46786 | 0.076486 | 0.057475 | 0.006322 | 0.009251
2021-11-23 16:30 | 0.32873 | 1.0852 | 2.0622 | 0.6051 | 0.0311 | 0.021676 | 0.002552 | 0.003657
2021-11-23 16:45 | 0.40836 | 1.0743 | 2.0622 | 0.57958 | 0 | 0 | 0 | 0
2021-11-23 17:00 | 0.25114 | 1.1745 | 4.8208 | 0.97513 | 0 | 0 | 0 | 0
2021-11-23 17:15 | 0.31648 | 1.2279 | 5.2338 | 1.0153 | 0 | 0 | 0 | 0
2021-11-23 17:30 | 0.31648 | 1.2743 | 5.0578 | 1.0409 | 0 | 0 | 0 | 0
2021-11-23 17:45 | 0.39713 | 1.2209 | 3.7977 | 0.86076 | 0 | 0 | 0 | 0
2021-11-23 18:00 | 0.43694 | 1.2389 | 3.8998 | 1.0167 | 0 | 0 | 0 | 0
2021-11-23 18:15 | 0.44511 | 1.2223 | 3.8386 | 1.0346 | 0 | 0 | 0 | 0
2021-11-23 18:30 | 0.46961 | 1.2241 | 5.5198 | 1.196 | 0 | 0 | 0 | 0
2021-11-23 18:45 | 0.62479 | 1.3005 | 4.8895 | 1.1273 | 0 | 0 | 0 | 0
2021-11-23 19:00 | 1.0515 | 1.2406 | 4.6999 | 1.0856 | 0 | 0 | 0 | 0
2021-11-23 19:15 | 3.7773 | 1.3449 | 4.6125 | 1.2811 | 0 | 0 | 0 | 0
2021-11-23 19:30 | 3.6548 | 1.3922 | 4.6379 | 1.9223 | 0 | 0 | 0 | 0
2021-11-23 19:45 | 3.6854 | 1.3716 | 4.5674 | 2.1016 | 0 | 0 | 0 | 0
2021-11-23 20:00 | 0.95556 | 1.4618 | 4.0958 | 1.3231 | 0 | 0 | 0 | 0
2021-11-23 20:15 | 0.91064 | 1.172 | 2.3276 | 0.9312 | 0 | 0 | 0 | 0
2021-11-23 20:30 | 1.4497 | 1.3094 | 2.2562 | 1.0913 | 0 | 0 | 0 | 0
2021-11-23 20:45 | 1.419 | 1.0226 | 2.1133 | 1.0149 | 0 | 0 | 0 | 0
2021-11-23 21:00 | 0.5472 | 1.0226 | 2.8789 | 0.98764 | 0 | 0 | 0 | 0
2021-11-23 21:15 | 0.45328 | 0.92301 | 0.60029 | 0.60525 | 0 | 0 | 0 | 0
2021-11-23 21:30 | 0.5962 | 0.9731 | 0.72279 | 0.55799 | 0 | 0 | 0 | 0
2021-11-23 21:45 | 0.78405 | 0.70362 | 0.37977 | 0.46815 | 0 | 0 | 0 | 0
2021-11-23 22:00 | 0.6207 | 0.66411 | 0.45328 | 0.42163 | 0 | 0 | 0 | 0
2021-11-23 22:15 | 0.39611 | 0.66061 | 0.47778 | 0.42382 | 0 | 0 | 0 | 0
2021-11-23 22:30 | 0.44511 | 0.6659 | 0.44103 | 0.4053 | 0 | 0 | 0 | 0
2021-11-23 22:45 | 0.60029 | 0.67847 | 0.3175 | 0.35031 | 0 | 0 | 0 | 0
2021-11-23 23:00 | 3.2567 | 1.1462 | 3.1546 | 1.969 | 0 | 0 | 0 | 0
2021-11-23 23:15 | 3.4506 | 1.1047 | 3.3894 | 2.0839 | 0 | 0 | 0 | 0
2021-11-23 23:30 | 3.4404 | 1.3386 | 3.4098 | 2.1149 | 0 | 0 | 0 | 0
2021-11-23 23:45 | 3.4506 | 1.3868 | 3.3485 | 2.137 | 0 | 0 | 0 | 0
2021-11-24 | 3.3587 | 1.1051 | 1.858 | 1.9129 | 0 | 0 | 0 | 0
2021-11-24 00:15 | 3.3894 | 1.117 | 0.94739 | 1.7749 | 0 | 0 | 0 | 0
2021-11-24 00:30 | 3.4404 | 1.117 | 0.64929 | 1.7075 | 0 | 0 | 0 | 0
2021-11-24 00:45 | 3.5119 | 1.117 | 0.4737 | 1.6452 | 0 | 0 | 0 | 0
2021-11-24 01:00 | 3.4915 | 1.117 | 0.293 | 1.6975 | 0 | 0 | 0 | 0
2021-11-24 01:15 | 3.4506 | 1.0665 | 0.23583 | 1.6358 | 0 | 0 | 0 | 0
2021-11-24 01:30 | 3.4302 | 1.0665 | 0.23889 | 1.6095 | 0 | 0 | 0 | 0
2021-11-24 01:45 | 3.4404 | 1.0798 | 0.34098 | 1.638 | 0 | 0 | 0 | 0
2021-11-24 02:00 | 3.4506 | 1.0773 | 0.34608 | 1.6447 | 0 | 0 | 0 | 0
2021-11-24 02:15 | 3.5119 | 1.0267 | 0.32771 | 1.6512 | 0 | 0 | 0 | 0
2021-11-24 02:30 | 3.5017 | 1.09 | 0.23991 | 1.6368 | 0 | 0 | 0 | 0
2021-11-24 02:45 | 3.4404 | 1.0096 | 0.21745 | 1.6833 | 0 | 0 | 0 | 0
2021-11-24 03:00 | 3.4506 | 1.0249 | 0.21949 | 1.8152 | 0 | 0 | 0 | 0
2021-11-24 03:15 | 3.4813 | 1.0267 | 0.25012 | 1.6544 | 0 | 0 | 0 | 0
2021-11-24 03:30 | 3.5119 | 1.0399 | 0.22766 | 1.6505 | 0 | 0 | 0 | 0
2021-11-24 03:45 | 3.4608 | 1.0803 | 0.293 | 1.7005 | 0 | 0 | 0 | 0
2021-11-24 04:00 | 3.4915 | 1.0951 | 0.40427 | 1.6988 | 0 | 0 | 0 | 0
2021-11-24 04:15 | 3.5936 | 0.98008 | 0.31341 | 1.2001 | 0 | 0 | 0 | 0
2021-11-24 04:30 | 3.5527 | 0.86933 | 0.23685 | 0.90174 | 0 | 0 | 0 | 0
2021-11-24 04:45 | 3.4915 | 0.90875 | 0.24093 | 0.82926 | 0 | 0 | 0 | 0
2021-11-24 05:00 | 3.4404 | 0.87819 | 0.22358 | 0.80738 | 0 | 0 | 0 | 0
2021-11-24 05:15 | 3.4915 | 0.88938 | 0.22766 | 0.79601 | 0 | 0 | 0 | 0
2021-11-24 05:30 | 3.5221 | 0.83356 | 0.29606 | 0.73942 | 0 | 0 | 0 | 0
2021-11-24 05:45 | 3.5731 | 0.88938 | 0.34098 | 0.72134 | 0 | 0 | 0 | 0
2021-11-24 06:00 | 3.471 | 0.83356 | 0.24706 | 0.71988 | 0 | 0 | 0 | 0
2021-11-24 06:15 | 3.4506 | 0.90808 | 0.23889 | 0.73621 | 0 | 0 | 0 | 0
2021-11-24 06:30 | 3.4813 | 0.9258 | 0.26543 | 0.74788 | 0 | 0 | 0 | 0
2021-11-24 06:45 | 3.5221 | 0.69808 | 0.24093 | 0.5332 | 0 | 0.000168 | 0 | 9e-06
2021-11-24 07:00 | 0.60029 | 0.58743 | 0.41244 | 0.35221 | 0 | 0.003061 | 0 | 3.5e-05
2021-11-24 07:15 | 0.33485 | 0.59879 | 0.27258 | 0.33529 | 0 | 0.005047 | 0 | 6.1e-05
2021-11-24 07:30 | 0.38284 | 0.62145 | 0.33281 | 0.36592 | 0 | 0.010692 | 0 | 8.7e-05
2021-11-24 07:45 | 0.81672 | 0.70035 | 0.77588 | 0.45094 | 0.03819 | 0.065564 | 0.039908 | 0.01113
2021-11-24 08:00 | 4.0223 | 0.96442 | 2.1745 | 1.0576 | 0.16153 | 0.094146 | 0.16546 | 0.04439
2021-11-24 08:15 | 3.8284 | 0.90338 | 0.98823 | 0.78901 | 0.28487 | 0.13969 | 0.29102 | 0.07765
2021-11-24 08:30 | 3.7365 | 0.94427 | 0.77997 | 0.60029 | 0.40821 | 0.18105 | 0.41658 | 0.11091
2021-11-24 08:45 | 3.6854 | 0.92554 | 0.51453 | 0.53145 | 0.5015 | 0.22127 | 0.5117 | 0.13331
2021-11-24 09:00 | 3.7671 | 1.1136 | 0.49411 | 0.61837 | 0.52767 | 0.24695 | 0.5414 | 0.13396
2021-11-24 09:15 | 3.8386 | 1.0854 | 0.53495 | 0.58862 | 0.55384 | 0.22996 | 0.5711 | 0.13461
2021-11-24 09:30 | 0.71054 | 1.0842 | 0.35323 | 0.593 | 0.58001 | 0.22674 | 0.6008 | 0.13525
2021-11-24 09:45 | 0.37977 | 1.0423 | 0.43286 | 0.85522 | 0.60116 | 0.20996 | 0.62375 | 0.13877
2021-11-24 10:00 | 0.5472 | 1.1841 | 0.62887 | 0.73534 | 0.61112 | 0.26587 | 0.63215 | 0.1475
2021-11-24 10:15 | 0.56354 | 1.204 | 0.66971 | 0.77326 | 0.62107 | 0.28559 | 0.64056 | 0.15624
2021-11-24 10:30 | 0.60845 | 1.2206 | 0.4737 | 1.0486 | 0.63102 | 0.31005 | 0.64897 | 0.16497
2021-11-24 10:45 | 0.61662 | 1.2443 | 0.42878 | 0.712 | 0.63865 | 0.33979 | 0.65477 | 0.1743
2021-11-24 11:00 | 0.53087 | 1.0696 | 0.29198 | 0.52955 | 0.64106 | 0.3399 | 0.65497 | 0.18463
2021-11-24 11:15 | 0.39815 | 1.4471 | 0.25522 | 1.226 | 0.64348 | 0.34737 | 0.65517 | 0.19496
2021-11-24 11:30 | 0.39304 | 1.2409 | 0.2981 | 1.0142 | 0.64589 | 0.35737 | 0.65536 | 0.20529
2021-11-24 11:45 | 0.45736 | 1.2188 | 0.40325 | 0.79076 | 0.6468 | 0.35748 | 0.65557 | 0.21425
2021-11-24 12:00 | 0.35731 | 1.2106 | 0.44511 | 0.8208 | 0.64434 | 0.36523 | 0.65577 | 0.22144
2021-11-24 12:15 | 2.1643 | 1.3935 | 0.33792 | 0.90378 | 0.64189 | 0.37458 | 0.65598 | 0.22863
2021-11-24 12:30 | 3.5936 | 1.0463 | 1.4395 | 0.92129 | 0.63943 | 0.38675 | 0.65619 | 0.23582
2021-11-24 12:45 | 3.5425 | 1.007 | 1.7151 | 1.6793 | 0.63416 | 0.39122 | 0.65168 | 0.24352
2021-11-24 13:00 | 2.6747 | 1.3244 | 1.9499 | 1.8934 | 0.62256 | 0.38239 | 0.63697 | 0.25098
2021-11-24 13:15 | 1.0924 | 1.2908 | 0.53903 | 1.5445 | 0.61096 | 0.36777 | 0.62225 | 0.25845
2021-11-24 13:30 | 2.052 | 1.2719 | 0.43694 | 1.5255 | 0.59936 | 0.363 | 0.60754 | 0.26592
2021-11-24 13:45 | 3.4608 | 1.2224 | 0.42061 | 1.0949 | 0.58548 | 0.3538 | 0.58981 | 0.25996
2021-11-24 14:00 | 3.4506 | 1.1696 | 0.3226 | 0.81584 | 0.56645 | 0.33696 | 0.56557 | 0.22943
2021-11-24 14:15 | 0.75138 | 1.1651 | 0.2736 | 0.72761 | 0.54741 | 0.31256 | 0.54132 | 0.19891
2021-11-24 14:30 | 0.37467 | 1.171 | 0.27258 | 0.83874 | 0.52838 | 0.28885 | 0.51708 | 0.16838
2021-11-24 14:45 | 0.2685 | 0.91666 | 0.30014 | 0.40282 | 0.48779 | 0.26553 | 0.47533 | 0.14036
2021-11-24 15:00 | 0.33996 | 0.88175 | 0.46961 | 0.38852 | 0.39856 | 0.23136 | 0.39561 | 0.11506
2021-11-24 15:15 | 0.39407 | 0.98037 | 0.46553 | 0.39188 | 0.30934 | 0.21183 | 0.31589 | 0.089753
2021-11-24 15:30 | 0.3471 | 0.81428 | 0.36956 | 0.31254 | 0.22011 | 0.18383 | 0.23616 | 0.06445
2021-11-24 15:45 | 0.34098 | 0.82396 | 0.35323 | 0.30073 | 0.14613 | 0.12015 | 0.16726 | 0.043411
2021-11-24 16:00 | 0.42878 | 0.85042 | 0.35629 | 0.32887 | 0.10656 | 0.088625 | 0.12187 | 0.031588
2021-11-24 16:15 | 0.69421 | 0.9104 | 0.30525 | 0.40938 | 0.067 | 0.059933 | 0.076486 | 0.019764
2021-11-24 16:30 | 0.46961 | 1.0703 | 0.32873 | 0.57331 | 0.027436 | 0.021901 | 0.0311 | 0.00794
2021-11-24 16:45 | 0.41244 | 1.1099 | 0.40836 | 0.58658 | 0 | 0 | 0 | 0
2021-11-24 17:00 | 0.46961 | 1.0659 | 0.25114 | 0.94275 | 0 | 0 | 0 | 0
2021-11-24 17:15 | 0.51453 | 1.2545 | 0.31648 | 0.99752 | 0 | 0 | 0 | 0
2021-11-24 17:30 | 0.6207 | 1.2445 | 0.31648 | 1.0161 | 0 | 0 | 0 | 0
2021-11-24 17:45 | 0.57987 | 1.2284 | 0.39713 | 0.84224 | 0 | 0 | 0 | 0
2021-11-24 18:00 | 0.66971 | 1.1555 | 0.43694 | 1.0038 | 0 | 0 | 0 | 0
2021-11-24 18:15 | 0.81672 | 1.1781 | 0.44511 | 1.0224 | 0 | 0 | 0 | 0
2021-11-24 18:30 | 0.79222 | 1.3214 | 0.46961 | 1.1908 | 0 | 0 | 0 | 0
2021-11-24 18:45 | 0.75955 | 1.1949 | 0.62479 | 1.1273 | 0 | 0 | 0 | 0
2021-11-24 19:00 | 0.84938 | 1.1051 | 1.0515 | 1.1606 | 0 | 0 | 0 | 0
2021-11-24 19:15 | 1.2557 | 1.6556 | 3.7773 | 1.7355 | 0 | 0 | 0 | 0
2021-11-24 19:30 | 1.7151 | 2.2004 | 3.6548 | 2.3622 | 0 | 0 | 0 | 0
2021-11-24 19:45 | 1.4497 | 2.0597 | 3.6854 | 2.5517 | 0 | 0 | 0 | 0
2021-11-24 20:00 | 1.7559 | 1.2782 | 0.95556 | 1.2452 | 0 | 0 | 0 | 0
2021-11-24 20:15 | 1.1944 | 0.96601 | 0.91064 | 0.82211 | 0 | 0 | 0 | 0
2021-11-24 20:30 | 1.0719 | 1.1159 | 1.4497 | 1.1395 | 0 | 0 | 0 | 0
2021-11-24 20:45 | 3.8692 | 1.1525 | 1.419 | 1.1646 | 0 | 0 | 0 | 0
2021-11-24 21:00 | 2.2256 | 1.1326 | 0.5472 | 1.0107 | 0 | 0 | 0 | 0
2021-11-24 21:15 | 1.1026 | 0.95989 | 0.45328 | 0.58483 | 0 | 0 | 0 | 0
2021-11-24 21:30 | 1.5109 | 0.72709 | 0.5962 | 0.54807 | 0 | 0 | 0 | 0
2021-11-24 21:45 | 2.9606 | 0.60911 | 0.78405 | 0.48449 | 0 | 0 | 0 | 0
2021-11-24 22:00 | 0.44511 | 0.60204 | 0.6207 | 0.4403 | 0 | 0 | 0 | 0
2021-11-24 22:15 | 0.39304 | 0.60204 | 0.39611 | 0.41682 | 0 | 0 | 0 | 0
2021-11-24 22:30 | 0.33281 | 0.58564 | 0.44511 | 0.39888 | 0 | 0 | 0 | 0
2021-11-24 22:45 | 0.39815 | 0.6101 | 0.60029 | 0.38429 | 0 | 0 | 0 | 0
2021-11-24 23:00 | 0.32873 | 2.418 | 3.2567 | 2.3813 | 0 | 0 | 0 | 0
2021-11-24 23:15 | 0.2685 | 2.6334 | 3.4506 | 2.5295 | 0 | 0 | 0 | 0
2021-11-24 23:30 | 0.2001 | 2.6334 | 3.4404 | 2.5451 | 0 | 0 | 0 | 0
2021-11-24 23:45 | 0.19295 | 2.595 | 3.4506 | 2.5582 | 0 | 0 | 0 | 0
2021-11-25 | 0.19601 | 2.3481 | 3.3587 | 2.3332 | 0 | 0 | 0 | 0
2021-11-25 00:15 | 0.2542 | 2.2949 | 3.3894 | 2.2051 | 0 | 0 | 0 | 0
2021-11-25 00:30 | 0.29606 | 2.2949 | 3.4404 | 2.1518 | 0 | 0 | 0 | 0
2021-11-25 00:45 | 0.2103 | 2.2622 | 3.5119 | 2.1195 | 0 | 0 | 0 | 0
2021-11-25 01:00 | 0.30831 | 2.2645 | 3.4915 | 2.1449 | 0 | 0 | 0 | 0
2021-11-25 01:15 | 0.26033 | 1.8988 | 3.4506 | 2.086 | 0 | 0 | 0 | 0
2021-11-25 01:30 | 0.3226 | 2.1702 | 3.4302 | 2.0691 | 0 | 0 | 0 | 0
2021-11-25 01:45 | 0.3226 | 2.0783 | 3.4404 | 2.0972 | 0 | 0 | 0 | 0
2021-11-25 02:00 | 0.26135 | 2.054 | 3.4506 | 2.1033 | 0 | 0 | 0 | 0
2021-11-25 02:15 | 0.25318 | 2.054 | 3.5119 | 2.103 | 0 | 0 | 0 | 0
2021-11-25 02:30 | 0.23991 | 1.9262 | 3.5017 | 2.1017 | 0 | 0 | 0 | 0
2021-11-25 02:45 | 0.43286 | 2.0258 | 3.4404 | 2.1401 | 0 | 0 | 0 | 0
2021-11-25 03:00 | 0.28177 | 2.0258 | 3.4506 | 2.2735 | 0 | 0 | 0 | 0
2021-11-25 03:15 | 0.2685 | 1.9859 | 3.4813 | 2.1065 | 0 | 0 | 0 | 0
2021-11-25 03:30 | 0.26645 | 2.0122 | 3.5119 | 2.1118 | 0 | 0 | 0 | 0
2021-11-25 03:45 | 0.34098 | 1.9886 | 3.4608 | 2.1598 | 0 | 0 | 0 | 0
2021-11-25 04:00 | 0.32362 | 1.9863 | 3.4915 | 2.1643 | 0 | 0 | 0 | 0
2021-11-25 04:15 | 0.27156 | 1.2127 | 3.5936 | 1.668 | 0 | 0 | 0 | 0
2021-11-25 04:30 | 0.24604 | 1.1368 | 3.5527 | 1.3738 | 0 | 0 | 0 | 0
2021-11-25 04:45 | 0.33792 | 1.125 | 3.4915 | 1.2951 | 0 | 0 | 0 | 0
2021-11-25 05:00 | 0.28687 | 0.94818 | 3.4404 | 1.2598 | 0 | 0 | 0 | 0
2021-11-25 05:15 | 0.29912 | 0.90757 | 3.4915 | 1.2468 | 0 | 0 | 0 | 0
2021-11-25 05:30 | 0.27973 | 0.69789 | 3.5221 | 1.2095 | 0 | 0 | 0 | 0
2021-11-25 05:45 | 0.36344 | 0.75662 | 3.5731 | 1.2003 | 0 | 0 | 0 | 0
2021-11-25 06:00 | 0.25216 | 0.72264 | 3.471 | 1.1781 | 0 | 0 | 0 | 0
2021-11-25 06:15 | 0.26645 | 0.6886 | 3.4506 | 1.1828 | 0 | 0 | 0 | 0
2021-11-25 06:30 | 0.2981 | 0.73404 | 3.4813 | 1.2131 | 0 | 0 | 0 | 0
2021-11-25 06:45 | 0.37263 | 0.66066 | 3.5221 | 1.0044 | 0 | 0.000223 | 0 | 1e-06
2021-11-25 07:00 | 0.29504 | 0.60948 | 0.60029 | 0.38969 | 0 | 9.2e-05 | 0 | 3e-06
2021-11-25 07:15 | 0.2685 | 0.57192 | 0.33485 | 0.33777 | 0 | 6e-05 | 0 | 5e-06
2021-11-25 07:30 | 0.36854 | 0.59276 | 0.38284 | 0.37248 | 0 | 3.8e-05 | 0 | 7e-06
2021-11-25 07:45 | 0.68196 | 0.7295 | 0.81672 | 0.51453 | 0.017247 | 0.014997 | 0.03819 | 0.015619
2021-11-25 08:00 | 1.123 | 1.4674 | 4.0223 | 1.4777 | 0.07447 | 0.081184 | 0.16153 | 0.064122
2021-11-25 08:15 | 0.93514 | 1.2859 | 3.8284 | 1.221 | 0.13169 | 0.15598 | 0.28487 | 0.11263
2021-11-25 08:30 | 0.64929 | 0.93052 | 3.7365 | 1.0746 | 0.18891 | 0.22871 | 0.40821 | 0.16113
2021-11-25 08:45 | 0.64112 | 0.89473 | 3.6854 | 0.9926 | 0.22065 | 0.28094 | 0.5015 | 0.19563
2021-11-25 09:00 | 0.58395 | 0.91591 | 3.7671 | 1.083 | 0.19321 | 0.3122 | 0.52767 | 0.20078
2021-11-25 09:15 | 0.84938 | 0.91591 | 3.8386 | 1.06 | 0.16577 | 0.33155 | 0.55384 | 0.20594
2021-11-25 09:30 | 0.44511 | 0.79712 | 0.71054 | 0.63208 | 0.13833 | 0.33752 | 0.58001 | 0.21109
2021-11-25 09:45 | 0.35731 | 1.0526 | 0.37977 | 0.8068 | 0.11408 | 0.35041 | 0.60116 | 0.21777
2021-11-25 10:00 | 0.32873 | 0.87053 | 0.5472 | 0.73767 | 0.097267 | 0.36427 | 0.61112 | 0.22699
2021-11-25 10:15 | 2.2664 | 1.0881 | 0.56354 | 0.79367 | 0.080451 | 0.36912 | 0.62107 | 0.23622
2021-11-25 10:30 | 3.6038 | 1.1095 | 0.60845 | 1.0775 | 0.063635 | 0.39433 | 0.63102 | 0.24544
2021-11-25 10:45 | 3.8386 | 1.0185 | 0.61662 | 0.74205 | 0.052349 | 0.39786 | 0.63865 | 0.25465
2021-11-25 11:00 | 3.7875 | 1.1022 | 0.53087 | 0.5418 | 0.053944 | 0.39798 | 0.64106 | 0.26362
2021-11-25 11:15 | 3.5731 | 1.1258 | 0.39815 | 0.9051 | 0.055539 | 0.3981 | 0.64348 | 0.27259
2021-11-25 11:30 | 3.5629 | 1.1726 | 0.39304 | 0.75678 | 0.057134 | 0.36097 | 0.64589 | 0.28157
2021-11-25 11:45 | 3.5323 | 1.0915 | 0.45736 | 0.66796 | 0.068448 | 0.35202 | 0.6468 | 0.29035
2021-11-25 12:00 | 3.5017 | 1.2526 | 0.35731 | 0.68954 | 0.10244 | 0.36264 | 0.64434 | 0.29926
2021-11-25 12:15 | 3.5221 | 1.0728 | 2.1643 | 0.81336 | 0.13643 | 0.36275 | 0.64189 | 0.30818
2021-11-25 12:30 | 2.0214 | 1.1155 | 3.5936 | 1.3779 | 0.17042 | 0.35149 | 0.63943 | 0.3171
2021-11-25 12:45 | 0.19295 | 1.4414 | 3.5425 | 2.0985 | 0.18343 | 0.34907 | 0.63416 | 0.32316
2021-11-25 13:00 | 0.19703 | 1.4644 | 2.6747 | 2.2402 | 0.14745 | 0.33316 | 0.62256 | 0.32293
2021-11-25 13:15 | 0.26748 | 0.88097 | 1.0924 | 1.6648 | 0.11146 | 0.32547 | 0.61096 | 0.3227
2021-11-25 13:30 | 0.37263 | 0.83081 | 2.052 | 1.7747 | 0.075474 | 0.31777 | 0.59936 | 0.32246
2021-11-25 13:45 | 0.23787 | 0.92437 | 3.4608 | 1.5363 | 0.048616 | 0.3085 | 0.58548 | 0.31289
2021-11-25 14:00 | 0.22051 | 0.83777 | 3.4506 | 1.2691 | 0.043124 | 0.30103 | 0.56645 | 0.28571
2021-11-25 14:15 | 0.24297 | 1.1681 | 0.75138 | 0.79017 | 0.037632 | 0.29475 | 0.54741 | 0.25853
2021-11-25 14:30 | 0.3226 | 1.1026 | 0.37467 | 0.84676 | 0.03214 | 0.29945 | 0.52838 | 0.23135
2021-11-25 14:45 | 0.21847 | 1.1227 | 0.2685 | 0.38809 | 0.026474 | 0.27644 | 0.48779 | 0.20197
2021-11-25 15:00 | 0.2297 | 1.0299 | 0.33996 | 0.37058 | 0.020399 | 0.22587 | 0.39856 | 0.16554
2021-11-25 15:15 | 0.28891 | 1.0335 | 0.39407 | 0.40077 | 0.014325 | 0.15549 | 0.30934 | 0.12911
2021-11-25 15:30 | 0.27462 | 0.89601 | 0.3471 | 0.31502 | 0.00825 | 0.12018 | 0.22011 | 0.092681
2021-11-25 15:45 | 0.22664 | 0.90569 | 0.34098 | 0.30146 | 0.003692 | 0.075114 | 0.14613 | 0.062303
2021-11-25 16:00 | 0.21541 | 0.94925 | 0.42878 | 0.32362 | 0.002695 | 0.05486 | 0.10656 | 0.045373
2021-11-25 16:15 | 0.31137 | 0.93834 | 0.69421 | 0.42863 | 0.001697 | 0.031422 | 0.067 | 0.028443
2021-11-25 16:30 | 0.21643 | 0.86333 | 0.46961 | 0.57914 | 0.0007 | 0.012351 | 0.027436 | 0.011513
2021-11-25 16:45 | 0.21439 | 0.79443 | 0.41244 | 0.59416 | 0 | 0 | 0 | 0
2021-11-25 17:00 | 0.2981 | 0.76142 | 0.46961 | 0.96579 | 0 | 0 | 0 | 0
2021-11-25 17:15 | 0.30729 | 0.80127 | 0.51453 | 1.0143 | 0 | 0 | 0 | 0
2021-11-25 17:30 | 0.23276 | 0.84504 | 0.6207 | 1.0255 | 0 | 0 | 0 | 0
2021-11-25 17:45 | 0.25012 | 0.81801 | 0.57987 | 0.87039 | 0 | 0 | 0 | 0
2021-11-25 18:00 | 0.29606 | 0.83429 | 0.66971 | 0.97641 | 0 | 0 | 0 | 0
2021-11-25 18:15 | 0.24093 | 0.84357 | 0.81672 | 0.9961 | 0 | 0 | 0 | 0
2021-11-25 18:30 | 0.37161 | 0.88095 | 0.79222 | 1.2229 | 0 | 0 | 0 | 0
2021-11-25 18:45 | 0.31341 | 0.87778 | 0.75955 | 1.122 | 0 | 0 | 0 | 0
2021-11-25 19:00 | 0.22153 | 0.88594 | 0.84938 | 1.2323 | 0 | 0 | 0 | 0
2021-11-25 19:15 | 0.22664 | 0.93953 | 1.2557 | 1.7545 | 0 | 0 | 0 | 0
2021-11-25 19:30 | 0.24297 | 1.1303 | 1.7151 | 2.1026 | 0 | 0 | 0 | 0
2021-11-25 19:45 | 0.34813 | 1.1085 | 1.4497 | 2.2061 | 0 | 0 | 0 | 0
2021-11-25 20:00 | 0.37365 | 0.96544 | 1.7559 | 1.3549 | 0 | 0 | 0 | 0
2021-11-25 20:15 | 0.25012 | 0.7619 | 1.1944 | 0.93864 | 0 | 0 | 0 | 0
2021-11-25 20:30 | 0.24502 | 0.78641 | 1.0719 | 1.187 | 0 | 0 | 0 | 0
2021-11-25 20:45 | 0.24297 | 1.1383 | 3.8692 | 1.5656 | 0 | 0 | 0 | 0
2021-11-25 21:00 | 0.20622 | 0.78641 | 2.2256 | 1.1726 | 0 | 0 | 0 | 0
2021-11-25 21:15 | 0.31035 | 0.76411 | 1.1026 | 0.59212 | 0 | 0 | 0 | 0
2021-11-25 21:30 | 0.23889 | 0.77158 | 1.5109 | 0.63266 | 0 | 0 | 0 | 0
2021-11-25 21:45 | 0.32056 | 0.84993 | 2.9606 | 0.83743 | 0 | 0 | 0 | 0
2021-11-25 22:00 | 0.25625 | 0.78411 | 0.44511 | 0.42863 | 0 | 0 | 0 | 0
2021-11-25 22:15 | 0.2103 | 0.7859 | 0.39304 | 0.39946 | 0 | 0 | 0 | 0
2021-11-25 22:30 | 0.30423 | 0.7859 | 0.33281 | 0.39027 | 0 | 0 | 0 | 0
2021-11-25 22:45 | 0.19805 | 0.7859 | 0.39815 | 0.40165 | 0 | 0 | 0 | 0
2021-11-25 23:00 | 3.1342 | 1.9526 | 0.32873 | 1.9762 | 0 | 0 | 0 | 0
2021-11-25 23:15 | 3.3894 | 2.2293 | 0.2685 | 2.0866 | 0 | 0 | 0 | 0
2021-11-25 23:30 | 3.369 | 2.2033 | 0.2001 | 2.0953 | 0 | 0 | 0 | 0
2021-11-25 23:45 | 3.3383 | 2.2033 | 0.19295 | 2.087 | 0 | 0 | 0 | 0
2021-11-26 | 3.3485 | 2.4488 | 0.19601 | 1.8624 | 0 | 0 | 0 | 0
2021-11-26 00:15 | 3.4506 | 2.3643 | 0.2542 | 1.7573 | 0 | 0 | 0 | 0
2021-11-26 00:30 | 3.3587 | 2.4486 | 0.29606 | 1.7099 | 0 | 0 | 0 | 0
2021-11-26 00:45 | 3.3281 | 2.4486 | 0.2103 | 1.6683 | 0 | 0 | 0 | 0
2021-11-26 01:00 | 3.4915 | 2.4842 | 0.30831 | 1.696 | 0 | 0 | 0 | 0
2021-11-26 01:15 | 3.4813 | 2.4842 | 0.26033 | 1.6127 | 0 | 0 | 0 | 0
2021-11-26 01:30 | 3.4098 | 2.582 | 0.3226 | 1.6193 | 0 | 0 | 0 | 0
2021-11-26 01:45 | 3.3894 | 2.3986 | 0.3226 | 1.6533 | 0 | 0 | 0 | 0
2021-11-26 02:00 | 3.471 | 2.337 | 0.26135 | 1.6521 | 0 | 0 | 0 | 0
2021-11-26 02:15 | 3.4302 | 2.337 | 0.25318 | 1.6492 | 0 | 0 | 0 | 0
2021-11-26 02:30 | 3.3996 | 2.4391 | 0.23991 | 1.6299 | 0 | 0 | 0 | 0
2021-11-26 02:45 | 3.4506 | 2.3569 | 0.43286 | 1.6856 | 0 | 0 | 0 | 0
2021-11-26 03:00 | 3.5936 | 2.2412 | 0.28177 | 1.7713 | 0 | 0 | 0 | 0
2021-11-26 03:15 | 3.471 | 2.3727 | 0.2685 | 1.6549 | 0 | 0 | 0 | 0
2021-11-26 03:30 | 3.4098 | 2.3164 | 0.26645 | 1.6613 | 0 | 0 | 0 | 0
2021-11-26 03:45 | 3.4302 | 2.169 | 0.34098 | 1.7083 | 0 | 0 | 0 | 0
2021-11-26 04:00 | 3.5017 | 1.9725 | 0.32362 | 1.7176 | 0 | 0 | 0 | 0
2021-11-26 04:15 | 3.4608 | 2.0034 | 0.27156 | 1.4297 | 0 | 0 | 0 | 0
2021-11-26 04:30 | 3.3996 | 2.0916 | 0.24604 | 1.2649 | 0 | 0 | 0 | 0
2021-11-26 04:45 | 3.4302 | 1.9938 | 0.33792 | 1.2465 | 0 | 0 | 0 | 0
2021-11-26 05:00 | 3.4915 | 1.8208 | 0.28687 | 1.2278 | 0 | 0 | 0 | 0
2021-11-26 05:15 | 3.4302 | 1.8908 | 0.29912 | 1.2316 | 0 | 0 | 0 | 0
2021-11-26 05:30 | 2.3276 | 1.8208 | 0.27973 | 1.2098 | 0 | 0 | 0 | 0
2021-11-26 05:45 | 1.419 | 1.8516 | 0.36344 | 1.2127 | 0 | 0 | 0 | 0
2021-11-26 06:00 | 0.66154 | 1.9186 | 0.25216 | 1.1599 | 0 | 0 | 0 | 0
2021-11-26 06:15 | 0.36242 | 1.773 | 0.26645 | 1.1788 | 0 | 0 | 0 | 0
2021-11-26 06:30 | 0.24093 | 1.773 | 0.2981 | 1.2137 | 0 | 0 | 0 | 0
2021-11-26 06:45 | 0.34302 | 1.0318 | 0.37263 | 1.0075 | 0 | 0.000115 | 0 | 1e-06
2021-11-26 07:00 | 0.391 | 0.61771 | 0.29504 | 0.37525 | 0 | 0.000467 | 0 | 3e-06
2021-11-26 07:15 | 0.27258 | 0.61243 | 0.2685 | 0.32917 | 0 | 0.000339 | 0 | 5e-06
2021-11-26 07:30 | 0.32158 | 0.6901 | 0.36854 | 0.36956 | 0 | 0.000396 | 0 | 7e-06
2021-11-26 07:45 | 0.55128 | 0.76155 | 0.68196 | 0.51978 | 0.000372 | 0.035535 | 0.017247 | 0.016685
2021-11-26 08:00 | 2.0826 | 1.469 | 1.123 | 1.4806 | 0.001639 | 0.15133 | 0.07447 | 0.069469
2021-11-26 08:15 | 1.1128 | 1.2206 | 0.93514 | 1.2 | 0.002906 | 0.26121 | 0.13169 | 0.12225
2021-11-26 08:30 | 0.71871 | 1.2508 | 0.64929 | 1.0897 | 0.004174 | 0.37723 | 0.18891 | 0.17504
2021-11-26 08:45 | 0.59212 | 1.1225 | 0.64112 | 1.0119 | 0.027799 | 0.44904 | 0.22065 | 0.21129
2021-11-26 09:00 | 0.51862 | 1.2944 | 0.58395 | 1.0959 | 0.10541 | 0.48183 | 0.19321 | 0.21172
2021-11-26 09:15 | 0.50228 | 1.2803 | 0.84938 | 1.1096 | 0.18303 | 0.48208 | 0.16577 | 0.21215
2021-11-26 09:30 | 0.3859 | 1.1242 | 0.44511 | 0.63908 | 0.26065 | 0.50715 | 0.13833 | 0.21258
2021-11-26 09:45 | 0.38998 | 1.1665 | 0.35731 | 0.74467 | 0.29487 | 0.55066 | 0.11408 | 0.21368
2021-11-26 10:00 | 1.0413 | 1.1933 | 0.32873 | 0.69888 | 0.22414 | 0.56723 | 0.097267 | 0.21603
2021-11-26 10:15 | 1.1332 | 1.2179 | 2.2664 | 0.98677 | 0.15341 | 0.55987 | 0.080451 | 0.21838
2021-11-26 10:30 | 1.1434 | 1.3234 | 3.6038 | 1.4815 | 0.082677 | 0.55565 | 0.063635 | 0.22073
2021-11-26 10:45 | 1.4293 | 1.2912 | 3.8386 | 1.1813 | 0.034575 | 0.57844 | 0.052349 | 0.22378
2021-11-26 11:00 | 1.2047 | 1.2138 | 3.7875 | 0.95045 | 0.041302 | 0.58859 | 0.053944 | 0.22828
2021-11-26 11:15 | 0.66971 | 1.2317 | 3.5731 | 1.1034 | 0.048029 | 0.58877 | 0.055539 | 0.2328
2021-11-26 11:30 | 0.62479 | 1.1847 | 3.5629 | 0.94929 | 0.054756 | 0.58895 | 0.057134 | 0.2373
2021-11-26 11:45 | 0.66154 | 1.1847 | 3.5323 | 0.85901 | 0.058745 | 0.60134 | 0.068448 | 0.2444
2021-11-26 12:00 | 0.64929 | 1.1847 | 3.5017 | 0.90393 | 0.056091 | 0.61619 | 0.10244 | 0.25739
2021-11-26 12:15 | 0.57987 | 1.2703 | 3.5221 | 1.0584 | 0.053436 | 0.591 | 0.13643 | 0.27037
2021-11-26 12:30 | 0.51862 | 1.4436 | 2.0214 | 1.5815 | 0.050781 | 0.59118 | 0.17042 | 0.28335
2021-11-26 12:45 | 0.51862 | 1.5148 | 0.19295 | 1.9408 | 0.052494 | 0.57516 | 0.18343 | 0.29012
2021-11-26 13:00 | 0.53087 | 1.3614 | 0.19703 | 1.9956 | 0.064826 | 0.56217 | 0.14745 | 0.28294
2021-11-26 13:15 | 0.4737 | 1.3294 | 0.26748 | 1.6452 | 0.077157 | 0.57327 | 0.11146 | 0.27576
2021-11-26 13:30 | 0.53087 | 1.3614 | 0.37263 | 1.7833 | 0.089489 | 0.55972 | 0.075474 | 0.26859
2021-11-26 13:45 | 0.34915 | 1.3954 | 0.23787 | 1.5251 | 0.093127 | 0.53004 | 0.048616 | 0.25921
2021-11-26 14:00 | 0.25012 | 1.3083 | 0.22051 | 1.2595 | 0.075598 | 0.48223 | 0.043124 | 0.24579
2021-11-26 14:15 | 0.26441 | 1.1777 | 0.24297 | 0.69013 | 0.05807 | 0.46602 | 0.037632 | 0.23237
2021-11-26 14:30 | 0.26748 | 1.1449 | 0.3226 | 0.44219 | 0.040541 | 0.45896 | 0.03214 | 0.21895
2021-11-26 14:45 | 0.2491 | 1.1358 | 0.21847 | 0.38546 | 0.026323 | 0.4327 | 0.026474 | 0.19804
2021-11-26 15:00 | 0.33587 | 1.1005 | 0.2297 | 0.37 | 0.020179 | 0.35355 | 0.020399 | 0.16051
2021-11-26 15:15 | 0.43694 | 1.067 | 0.28891 | 0.405 | 0.014034 | 0.27649 | 0.014325 | 0.12297
2021-11-26 15:30 | 0.2981 | 1.0266 | 0.27462 | 0.30568 | 0.00789 | 0.21844 | 0.00825 | 0.085436
2021-11-26 15:45 | 0.39611 | 1.0363 | 0.22664 | 0.30087 | 0.003274 | 0.13797 | 0.003692 | 0.055017
2021-11-26 16:00 | 0.2981 | 1.0798 | 0.21541 | 0.32231 | 0.002391 | 0.10086 | 0.002695 | 0.040088
2021-11-26 16:15 | 0.37058 | 0.93363 | 0.31137 | 0.44059 | 0.001509 | 0.062289 | 0.001697 | 0.02516
2021-11-26 16:30 | 0.38386 | 1.1094 | 0.21643 | 0.56091 | 0.000626 | 0.028533 | 0.0007 | 0.010232
2021-11-26 16:45 | 0.31239 | 1.1246 | 0.21439 | 0.58979 | 0 | 0 | 0 | 0
2021-11-26 17:00 | 0.72688 | 1.1284 | 0.2981 | 0.97527 | 0 | 0 | 0 | 0
2021-11-26 17:15 | 1.7151 | 1.1424 | 0.30729 | 1.0258 | 0 | 0 | 0 | 0
2021-11-26 17:30 | 1.4497 | 1.2034 | 0.23276 | 1.0115 | 0 | 0 | 0 | 0
2021-11-26 17:45 | 1.4497 | 1.1122 | 0.25012 | 0.87053 | 0 | 0 | 0 | 0
2021-11-26 18:00 | 1.123 | 1.1124 | 0.29606 | 0.97175 | 0 | 0 | 0 | 0
2021-11-26 18:15 | 1.3067 | 1.1658 | 0.24093 | 0.99012 | 0 | 0 | 0 | 0
2021-11-26 18:30 | 0.66154 | 1.1216 | 0.37161 | 1.2232 | 0 | 0 | 0 | 0
2021-11-26 18:45 | 0.51453 | 1.1825 | 0.31341 | 1.1293 | 0 | 0 | 0 | 0
2021-11-26 19:00 | 0.55128 | 1.2659 | 0.22153 | 1.2255 | 0 | 0 | 0 | 0
2021-11-26 19:15 | 3.4608 | 1.3097 | 0.22664 | 1.7382 | 0 | 0 | 0 | 0
2021-11-26 19:30 | 4.2007 | 1.3454 | 0.24297 | 2.0807 | 0 | 0 | 0 | 0
2021-11-26 19:45 | 4.6864 | 1.7433 | 0.34813 | 2.2171 | 0 | 0 | 0 | 0
2021-11-26 20:00 | 0.80038 | 1.3085 | 0.37365 | 1.3706 | 0 | 0 | 0 | 0
2021-11-26 20:15 | 0.31954 | 0.97507 | 0.25012 | 0.93616 | 0 | 0 | 0 | 0
2021-11-26 20:30 | 0.34302 | 1.0788 | 0.24502 | 1.1702 | 0 | 0 | 0 | 0
2021-11-26 20:45 | 0.36752 | 1.2111 | 0.24297 | 1.5523 | 0 | 0 | 0 | 0
2021-11-26 21:00 | 0.40427 | 1.1059 | 0.20622 | 1.1679 | 0 | 0 | 0 | 0
2021-11-26 21:15 | 0.40836 | 0.85415 | 0.31035 | 0.60379 | 0 | 0 | 0 | 0
2021-11-26 21:30 | 0.46144 | 0.86265 | 0.23889 | 0.62304 | 0 | 0 | 0 | 0
2021-11-26 21:45 | 0.4737 | 0.91255 | 0.32056 | 0.80972 | 0 | 0 | 0 | 0
2021-11-26 22:00 | 0.50228 | 0.64021 | 0.25625 | 0.41667 | 0 | 0 | 0 | 0
2021-11-26 22:15 | 0.42878 | 0.58564 | 0.2103 | 0.38488 | 0 | 0 | 0 | 0
2021-11-26 22:30 | 0.45328 | 0.56425 | 0.30423 | 0.38254 | 0 | 0 | 0 | 0
2021-11-26 22:45 | 0.3859 | 0.58631 | 0.19805 | 0.37482 | 0 | 0 | 0 | 0
2021-11-26 23:00 | 3.2873 | 1.8398 | 3.1342 | 1.9703 | 0 | 0 | 0 | 0
2021-11-26 23:15 | 3.4608 | 2.1938 | 3.3894 | 2.0851 | 0 | 0 | 0 | 0
2021-11-26 23:30 | 3.4506 | 1.8543 | 3.369 | 2.0807 | 0 | 0 | 0 | 0
2021-11-26 23:45 | 3.5936 | 1.818 | 3.3383 | 2.0797 | 0 | 0 | 0 | 0
2021-11-27 | 3.6854 | 1.7778 | 3.3485 | 1.8624 | 0 | 0 | 0 | 0
2021-11-27 00:15 | 3.4404 | 1.7946 | 3.4506 | 1.7689 | 0 | 0 | 0 | 0
2021-11-27 00:30 | 3.5119 | 1.7946 | 3.3587 | 1.6967 | 0 | 0 | 0 | 0
2021-11-27 00:45 | 3.5119 | 1.5769 | 3.3281 | 1.6566 | 0 | 0 | 0 | 0
2021-11-27 01:00 | 3.6242 | 1.7282 | 3.4915 | 1.7033 | 0 | 0 | 0 | 0
2021-11-27 01:15 | 3.5527 | 1.7837 | 3.4813 | 1.62 | 0 | 0 | 0 | 0
2021-11-27 01:30 | 3.5323 | 1.8895 | 3.4098 | 1.6062 | 0 | 0 | 0 | 0
2021-11-27 01:45 | 3.5425 | 1.8608 | 3.3894 | 1.6489 | 0 | 0 | 0 | 0
2021-11-27 02:00 | 3.5731 | 1.7133 | 3.471 | 1.6579 | 0 | 0 | 0 | 0
2021-11-27 02:15 | 3.5221 | 1.6781 | 3.4302 | 1.6361 | 0 | 0 | 0 | 0
2021-11-27 02:30 | 3.5425 | 1.3627 | 3.3996 | 1.6299 | 0 | 0 | 0 | 0
2021-11-27 02:45 | 3.5221 | 1.6159 | 3.4506 | 1.6725 | 0 | 0 | 0 | 0
2021-11-27 03:00 | 3.5221 | 1.6956 | 3.5936 | 1.7465 | 0 | 0 | 0 | 0
2021-11-27 03:15 | 2.3481 | 1.6148 | 3.471 | 1.6549 | 0 | 0 | 0 | 0
2021-11-27 03:30 | 1.2047 | 1.6548 | 3.4098 | 1.6467 | 0 | 0 | 0 | 0
2021-11-27 03:45 | 1.0209 | 1.5744 | 3.4302 | 1.6937 | 0 | 0 | 0 | 0
2021-11-27 04:00 | 0.65746 | 1.3492 | 3.5017 | 1.7161 | 0 | 0 | 0 | 0
2021-11-27 04:15 | 0.44511 | 1.1023 | 3.4608 | 1.4414 | 0 | 0 | 0 | 0
2021-11-27 04:30 | 0.37977 | 1.019 | 3.3996 | 1.2634 | 0 | 0 | 0 | 0
2021-11-27 04:45 | 0.42061 | 1.0112 | 3.4302 | 1.2348 | 0 | 0 | 0 | 0
2021-11-27 05:00 | 0.38284 | 0.91714 | 3.4915 | 1.2293 | 0 | 0 | 0 | 0
2021-11-27 05:15 | 0.40836 | 0.93567 | 3.4302 | 1.2302 | 0 | 0 | 0 | 0
2021-11-27 05:30 | 0.33383 | 0.91578 | 2.3276 | 1.0493 | 0 | 0 | 0 | 0
2021-11-27 05:45 | 0.37671 | 0.89696 | 1.419 | 0.9137 | 0 | 0 | 0 | 0
2021-11-27 06:00 | 0.40019 | 0.85369 | 0.66154 | 0.77019 | 0 | 0 | 0 | 0
2021-11-27 06:15 | 0.3175 | 0.84228 | 0.36242 | 0.74496 | 0 | 0 | 0 | 0
2021-11-27 06:30 | 0.43286 | 0.86001 | 0.24093 | 0.74205 | 0 | 0 | 0 | 0
2021-11-27 06:45 | 0.41244 | 0.84228 | 0.34302 | 0.75313 | 0 | 0.000105 | 0 | 1e-06
2021-11-27 07:00 | 0.3614 | 0.59113 | 0.391 | 0.37161 | 0 | 0.000371 | 0 | 3e-06
2021-11-27 07:15 | 0.31954 | 0.6056 | 0.27258 | 0.29985 | 0 | 0.000206 | 0 | 5e-06
2021-11-27 07:30 | 0.46144 | 0.62162 | 0.32158 | 0.35192 | 0 | 0.000268 | 0 | 7e-06
2021-11-27 07:45 | 0.41244 | 0.67482 | 0.55128 | 0.52328 | 0.015732 | 0.025959 | 0.000372 | 0.016174
2021-11-27 08:00 | 1.1128 | 1.1905 | 2.0826 | 1.52 | 0.07094 | 0.093043 | 0.001639 | 0.067531
2021-11-27 08:15 | 1.1026 | 1.2471 | 1.1128 | 1.237 | 0.12615 | 0.17752 | 0.002906 | 0.11889
2021-11-27 08:30 | 0.55537 | 1.2521 | 0.71871 | 1.109 | 0.18136 | 0.24778 | 0.004174 | 0.17024
2021-11-27 08:45 | 0.61662 | 1.0944 | 0.59212 | 1.0311 | 0.21479 | 0.29806 | 0.027799 | 0.20858
2021-11-27 09:00 | 0.81672 | 1.1693 | 0.51862 | 1.0842 | 0.19351 | 0.32727 | 0.10541 | 0.21942
2021-11-27 09:15 | 0.80855 | 1.1514 | 0.50228 | 1.1148 | 0.17223 | 0.35274 | 0.18303 | 0.23025
2021-11-27 09:30 | 0.69829 | 1.1754 | 0.3859 | 0.62479 | 0.15095 | 0.37719 | 0.26065 | 0.24108
2021-11-27 09:45 | 0.71871 | 1.1461 | 0.38998 | 0.73213 | 0.16377 | 0.37408 | 0.29487 | 0.24661
2021-11-27 10:00 | 0.6207 | 1.1704 | 1.0413 | 0.79134 | 0.26244 | 0.36168 | 0.22414 | 0.23884
2021-11-27 10:15 | 0.60437 | 1.3295 | 1.1332 | 1.0953 | 0.36112 | 0.36837 | 0.15341 | 0.23107
2021-11-27 10:30 | 0.61254 | 1.4911 | 1.1434 | 1.592 | 0.45979 | 0.36365 | 0.082677 | 0.22329
2021-11-27 10:45 | 0.5472 | 1.3781 | 1.4293 | 1.3266 | 0.49562 | 0.34212 | 0.034575 | 0.21902
2021-11-27 11:00 | 0.71463 | 1.1154 | 1.2047 | 1.0722 | 0.37296 | 0.3451 | 0.041302 | 0.22326
2021-11-27 11:15 | 2.8687 | 1.2863 | 0.66971 | 1.1562 | 0.2503 | 0.34521 | 0.048029 | 0.22749
2021-11-27 11:30 | 2.246 | 1.0396 | 0.62479 | 0.98983 | 0.12764 | 0.35258 | 0.054756 | 0.23172
2021-11-27 11:45 | 3.0423 | 1.0275 | 0.66154 | 0.90831 | 0.064719 | 0.34753 | 0.058745 | 0.23899
2021-11-27 12:00 | 3.1035 | 1.0696 | 0.64929 | 0.96504 | 0.15269 | 0.34261 | 0.056091 | 0.25276
2021-11-27 12:15 | 1.3782 | 1.0976 | 0.57987 | 1.1093 | 0.24067 | 0.37323 | 0.053436 | 0.26652
2021-11-27 12:30 | 0.94739 | 0.99246 | 0.51862 | 1.6238 | 0.32864 | 0.37335 | 0.050781 | 0.28028
2021-11-27 12:45 | 1.8989 | 1.348 | 0.51862 | 1.9727 | 0.398 | 0.37078 | 0.052494 | 0.2882
2021-11-27 13:00 | 4.1891 | 1.2609 | 0.53087 | 2.0309 | 0.42024 | 0.36259 | 0.064826 | 0.28321
2021-11-27 13:15 | 0.391 | 1.4934 | 0.4737 | 1.6646 | 0.44248 | 0.36813 | 0.077157 | 0.27822
2021-11-27 13:30 | 0.35527 | 1.3626 | 0.53087 | 1.8246 | 0.46472 | 0.32948 | 0.089489 | 0.27323
2021-11-27 13:45 | 0.28381 | 1.2594 | 0.34915 | 1.543 | 0.48734 | 0.30255 | 0.093127 | 0.26509
2021-11-27 14:00 | 0.30014 | 1.3575 | 0.25012 | 1.2631 | 0.51094 | 0.28664 | 0.075598 | 0.25044
2021-11-27 14:15 | 0.37671 | 1.1449 | 0.26441 | 0.6961 | 0.53454 | 0.26966 | 0.05807 | 0.23578
2021-11-27 14:30 | 0.40836 | 1.185 | 0.26748 | 0.43796 | 0.55813 | 0.26027 | 0.040541 | 0.22113
2021-11-27 14:45 | 0.35221 | 1.0682 | 0.2491 | 0.37729 | 0.53554 | 0.23685 | 0.026323 | 0.19919
2021-11-27 15:00 | 0.34813 | 1.1271 | 0.33587 | 0.38182 | 0.39566 | 0.20606 | 0.020179 | 0.16127
2021-11-27 15:15 | 0.39917 | 1.1116 | 0.43694 | 0.43082 | 0.25578 | 0.15632 | 0.014034 | 0.12336
2021-11-27 15:30 | 0.32056 | 0.96329 | 0.2981 | 0.31152 | 0.11591 | 0.14616 | 0.00789 | 0.08544
2021-11-27 15:45 | 0.39509 | 0.97796 | 0.39611 | 0.30933 | 0.014416 | 0.093085 | 0.003274 | 0.054755
2021-11-27 16:00 | 0.4737 | 1.0119 | 0.2981 | 0.31896 | 0.010539 | 0.068044 | 0.002391 | 0.039901
2021-11-27 16:15 | 0.41653 | 0.91419 | 0.37058 | 0.45824 | 0.006661 | 0.042294 | 0.001509 | 0.025046
2021-11-27 16:30 | 0.50636 | 1.1116 | 0.38386 | 0.57841 | 0.002784 | 0.019822 | 0.000626 | 0.010191
2021-11-27 16:45 | 0.62479 | 1.2306 | 0.31239 | 0.57083 | 0 | 0 | 0 | 0
2021-11-27 17:00 | 0.83305 | 0.99763 | 0.72688 | 1.0208 | 0 | 0 | 0 | 0
2021-11-27 17:15 | 0.54312 | 1.1019 | 1.7151 | 1.2282 | 0 | 0 | 0 | 0
2021-11-27 17:30 | 0.53087 | 1.1289 | 1.4497 | 1.1567 | 0 | 0 | 0 | 0
2021-11-27 17:45 | 0.53087 | 1.0778 | 1.4497 | 1.0065 | 0 | 0 | 0 | 0
2021-11-27 18:00 | 0.61254 | 1.2661 | 1.123 | 1.0749 | 0 | 0 | 0 | 0
2021-11-27 18:15 | 0.57578 | 1.1506 | 1.3067 | 1.1033 | 0 | 0 | 0 | 0
2021-11-27 18:30 | 0.61662 | 1.1865 | 0.66154 | 1.2617 | 0 | 0 | 0 | 0
2021-11-27 18:45 | 0.64521 | 1.1016 | 0.51453 | 1.1422 | 0 | 0 | 0 | 0
2021-11-27 19:00 | 0.69421 | 1.2577 | 0.55128 | 1.1922 | 0 | 0 | 0 | 0
2021-11-27 19:15 | 0.73913 | 1.3394 | 3.4608 | 2.1054 | 0 | 0 | 0 | 0
2021-11-27 19:30 | 0.77997 | 1.2593 | 4.2007 | 2.2448 | 0 | 0 | 0 | 0
2021-11-27 19:45 | 0.73504 | 1.2931 | 4.6864 | 2.2961 | 0 | 0 | 0 | 0
2021-11-27 20:00 | 0.84122 | 1.2615 | 0.80038 | 1.3508 | 0 | 0 | 0 | 0
2021-11-27 20:15 | 0.89022 | 1.1057 | 0.31954 | 0.90014 | 0 | 0 | 0 | 0
2021-11-27 20:30 | 0.70238 | 1.1844 | 0.34302 | 1.1434 | 0 | 0 | 0 | 0
2021-11-27 20:45 | 0.50228 | 1.2185 | 0.36752 | 1.5156 | 0 | 0 | 0 | 0
2021-11-27 21:00 | 0.45328 | 1.0273 | 0.40427 | 1.1177 | 0 | 0 | 0 | 0
2021-11-27 21:15 | 0.5227 | 0.78308 | 0.40836 | 0.54662 | 0 | 0 | 0 | 0
2021-11-27 21:30 | 0.54312 | 0.85921 | 0.46144 | 0.63441 | 0 | 0 | 0 | 0
2021-11-27 21:45 | 0.46961 | 0.99081 | 0.4737 | 0.83743 | 0 | 0 | 0 | 0
2021-11-27 22:00 | 0.43694 | 0.71453 | 0.50228 | 0.44788 | 0 | 0 | 0 | 0
2021-11-27 22:15 | 0.35527 | 0.71742 | 0.42878 | 0.39538 | 0 | 0 | 0 | 0
2021-11-27 22:30 | 0.48186 | 0.71742 | 0.45328 | 0.37963 | 0 | 0 | 0 | 0
2021-11-27 22:45 | 0.31852 | 0.71742 | 0.3859 | 0.36519 | 0 | 0 | 0 | 0
2021-11-27 23:00 | 0.35833 | 1.0377 | 3.2873 | 1.9718 | 0 | 0 | 0 | 0
2021-11-27 23:15 | 0.35017 | 1.0377 | 3.4608 | 2.0851 | 0 | 0 | 0 | 0
2021-11-27 23:30 | 0.25114 | 1.0377 | 3.4506 | 2.0851 | 0 | 0 | 0 | 0
2021-11-27 23:45 | 0.3226 | 1.0972 | 3.5936 | 2.1074 | 0 | 0 | 0 | 0
2021-11-28 | 0.30116 | 1.0908 | 3.6854 | 1.9135 | 0 | 0 | 0 | 0
2021-11-28 00:15 | 0.3175 | 1.0908 | 3.4404 | 1.7791 | 0 | 0 | 0 | 0
2021-11-28 00:30 | 0.31341 | 1.0406 | 3.5119 | 1.7171 | 0 | 0 | 0 | 0
2021-11-28 00:45 | 0.28177 | 1.1391 | 3.5119 | 1.6639 | 0 | 0 | 0 | 0
2021-11-28 01:00 | 0.38386 | 1.1391 | 3.6242 | 1.7208 | 0 | 0 | 0 | 0
2021-11-28 01:15 | 0.29198 | 1.0406 | 3.5527 | 1.6477 | 0 | 0 | 0 | 0
2021-11-28 01:30 | 0.31239 | 1.0693 | 3.5323 | 1.631 | 0 | 0 | 0 | 0
2021-11-28 01:45 | 0.28177 | 1.0406 | 3.5425 | 1.6737 | 0 | 0 | 0 | 0
2021-11-28 02:00 | 0.28279 | 1.0067 | 3.5731 | 1.6886 | 0 | 0 | 0 | 0
2021-11-28 02:15 | 0.27768 | 1.1052 | 3.5221 | 1.6579 | 0 | 0 | 0 | 0
2021-11-28 02:30 | 0.30729 | 1.1052 | 3.5425 | 1.6358 | 0 | 0 | 0 | 0
2021-11-28 02:45 | 0.26339 | 1.0067 | 3.5221 | 1.6652 | 0 | 0 | 0 | 0
2021-11-28 03:00 | 0.35425 | 1.4615 | 3.5221 | 1.71 | 0 | 0 | 0 | 0
2021-11-28 03:15 | 0.37365 | 1.105 | 2.3481 | 1.4974 | 0 | 0 | 0 | 0
2021-11-28 03:30 | 0.27564 | 1.105 | 1.2047 | 1.3302 | 0 | 0 | 0 | 0
2021-11-28 03:45 | 0.32056 | 1.0448 | 1.0209 | 1.3407 | 0 | 0 | 0 | 0
2021-11-28 04:00 | 0.28891 | 1.105 | 0.65746 | 1.3419 | 0 | 0 | 0 | 0
2021-11-28 04:15 | 0.31239 | 1.0349 | 0.44511 | 1.2556 | 0 | 0 | 0 | 0
2021-11-28 04:30 | 0.33485 | 0.96569 | 0.37977 | 1.1864 | 0 | 0 | 0 | 0
2021-11-28 04:45 | 0.29606 | 0.96569 | 0.42061 | 1.2191 | 0 | 0 | 0 | 0
2021-11-28 05:00 | 0.3369 | 0.8661 | 0.38284 | 1.2204 | 0 | 0 | 0 | 0
2021-11-28 05:15 | 0.28789 | 0.97899 | 0.40836 | 1.2348 | 0 | 0 | 0 | 0
2021-11-28 05:30 | 0.26339 | 0.90904 | 0.33383 | 1.0536 | 0 | 0 | 0 | 0
2021-11-28 05:45 | 0.34098 | 0.87306 | 0.37671 | 0.93645 | 0 | 0 | 0 | 0
2021-11-28 06:00 | 0.30014 | 0.84977 | 0.40019 | 0.78828 | 0 | 0 | 0 | 0
2021-11-28 06:15 | 0.3226 | 0.8324 | 0.3175 | 0.74759 | 0 | 0 | 0 | 0
2021-11-28 06:30 | 0.35731 | 0.89384 | 0.43286 | 0.77005 | 0 | 0 | 0 | 0
2021-11-28 06:45 | 0.31954 | 0.86727 | 0.41244 | 0.77719 | 0 | 2e-06 | 0 | 0
2021-11-28 07:00 | 0.25829 | 0.61925 | 0.3614 | 0.36796 | 0 | 7e-06 | 0 | 0
2021-11-28 07:15 | 0.35119 | 0.63711 | 0.31954 | 0.30189 | 0 | 1e-05 | 0 | 0
2021-11-28 07:30 | 0.34302 | 0.67649 | 0.46144 | 0.37467 | 0 | 1.4e-05 | 0 | 0
2021-11-28 07:45 | 0.28891 | 0.75931 | 0.41244 | 0.53962 | 0.00403 | 0.015057 | 0.015732 | 0.017142
2021-11-28 08:00 | 0.35935 | 1.3202 | 1.1128 | 1.5768 | 0.018591 | 0.075725 | 0.07094 | 0.072677
2021-11-28 08:15 | 0.34915 | 1.2572 | 1.1026 | 1.2312 | 0.033152 | 0.13137 | 0.12615 | 0.12821
2021-11-28 08:30 | 0.41653 | 1.2639 | 0.55537 | 1.0792 | 0.047713 | 0.19553 | 0.18136 | 0.18374
2021-11-28 08:45 | 0.49003 | 1.2746 | 0.61662 | 1.0346 | 0.066573 | 0.23539 | 0.21479 | 0.22517
2021-11-28 09:00 | 2.3889 | 1.3105 | 0.81672 | 1.1332 | 0.096686 | 0.31086 | 0.19351 | 0.23516
2021-11-28 09:15 | 1.7253 | 1.332 | 0.80855 | 1.1475 | 0.1268 | 0.33563 | 0.17223 | 0.24515
2021-11-28 09:30 | 0.53087 | 1.1264 | 0.69829 | 0.54078 | 0.15691 | 0.3614 | 0.15095 | 0.25513
2021-11-28 09:45 | 0.62479 | 1.1805 | 0.71871 | 0.46436 | 0.16837 | 0.3752 | 0.16377 | 0.26398
2021-11-28 10:00 | 0.62887 | 1.2624 | 0.6207 | 0.61458 | 0.1309 | 0.38026 | 0.26244 | 0.27042
2021-11-28 10:15 | 2.7973 | 1.3585 | 0.60437 | 0.9191 | 0.093428 | 0.38532 | 0.36112 | 0.27685
2021-11-28 10:30 | 2.4195 | 1.4511 | 0.61254 | 1.4185 | 0.055958 | 0.35444 | 0.45979 | 0.28329
2021-11-28 10:45 | 0.60845 | 1.3151 | 0.5472 | 1.1597 | 0.028306 | 0.35738 | 0.49562 | 0.28415
2021-11-28 11:00 | 0.58395 | 1.336 | 0.71463 | 1.0909 | 0.026441 | 0.35891 | 0.37296 | 0.27068
2021-11-28 11:15 | 0.62479 | 1.4929 | 2.8687 | 1.4739 | 0.024576 | 0.37558 | 0.2503 | 0.25722
2021-11-28 11:30 | 0.48595 | 1.2596 | 2.246 | 1.2203 | 0.022711 | 0.37569 | 0.12764 | 0.24375
2021-11-28 11:45 | 0.58804 | 1.4022 | 3.0423 | 1.2729 | 0.021237 | 0.37497 | 0.064719 | 0.24203
2021-11-28 12:00 | 0.63296 | 1.3731 | 3.1035 | 1.3522 | 0.020789 | 0.38168 | 0.15269 | 0.26869
2021-11-28 12:15 | 0.62887 | 1.299 | 1.3782 | 1.2569 | 0.020342 | 0.36393 | 0.24067 | 0.29535
2021-11-28 12:30 | 0.42878 | 1.6241 | 0.94739 | 1.7141 | 0.019894 | 0.3701 | 0.32864 | 0.322
2021-11-28 12:45 | 0.4737 | 1.7189 | 1.8989 | 1.7467 | 0.019487 | 0.36485 | 0.398 | 0.34009
2021-11-28 13:00 | 0.49411 | 1.8396 | 4.1891 | 2.1335 | 0.019184 | 0.36067 | 0.42024 | 0.3384
2021-11-28 13:15 | 0.31954 | 1.3669 | 0.391 | 1.2363 | 0.018882 | 0.35228 | 0.44248 | 0.33671
2021-11-28 13:30 | 0.26645 | 1.3105 | 0.35527 | 1.1844 | 0.018579 | 0.33999 | 0.46472 | 0.33503
2021-11-28 13:45 | 2.9402 | 1.1454 | 0.28381 | 0.95045 | 0.018017 | 0.32991 | 0.48734 | 0.3304
2021-11-28 14:00 | 5.0673 | 1.3105 | 0.30014 | 0.90641 | 0.01677 | 0.30942 | 0.51094 | 0.31967
2021-11-28 14:15 | 5.196 | 1.1415 | 0.37671 | 0.54283 | 0.015523 | 0.28936 | 0.53454 | 0.30895
2021-11-28 14:30 | 5.2737 | 1.0349 | 0.40836 | 0.3913 | 0.014275 | 0.25399 | 0.55813 | 0.29823
2021-11-28 14:45 | 4.1436 | 0.98514 | 0.35221 | 0.33952 | 0.013458 | 0.22723 | 0.53554 | 0.27345
2021-11-28 15:00 | 1.1332 | 1.0068 | 0.34813 | 0.38911 | 0.013778 | 0.1765 | 0.39566 | 0.21561
2021-11-28 15:15 | 0.26441 | 0.98961 | 0.39917 | 0.44278 | 0.014098 | 0.13494 | 0.25578 | 0.15777
2021-11-28 15:30 | 0.32056 | 0.91626 | 0.32056 | 0.31429 | 0.014418 | 0.1075 | 0.11591 | 0.099935
2021-11-28 15:45 | 0.23583 | 0.92595 | 0.39509 | 0.32085 | 0.013647 | 0.061422 | 0.014416 | 0.054962
2021-11-28 16:00 | 0.28177 | 1.1367 | 0.4737 | 0.33281 | 0.009984 | 0.047292 | 0.010539 | 0.04006
2021-11-28 16:15 | 0.32567 | 0.89794 | 0.41653 | 0.46684 | 0.006322 | 0.031015 | 0.006661 | 0.025157
2021-11-28 16:30 | 0.30933 | 1.1201 | 0.50636 | 0.61341 | 0.00266 | 0.01382 | 0.002784 | 0.010254
2021-11-28 16:45 | 0.23583 | 1.0674 | 0.62479 | 0.62887 | 0 | 0 | 0 | 0
2021-11-28 17:00 | 0.30627 | 1.1296 | 0.83305 | 1.1084 | 0 | 0 | 0 | 0
2021-11-28 17:15 | 0.28381 | 1.2749 | 0.54312 | 1.2753 | 0 | 0 | 0 | 0
2021-11-28 17:30 | 0.2685 | 1.0904 | 0.53087 | 1.2048 | 0 | 0 | 0 | 0
2021-11-28 17:45 | 0.31444 | 1.0831 | 0.53087 | 1.0455 | 0 | 0 | 0 | 0
2021-11-28 18:00 | 0.33485 | 1.189 | 0.61254 | 1.0929 | 0 | 0 | 0 | 0
2021-11-28 18:15 | 0.34506 | 1.3891 | 0.57578 | 1.1282 | 0 | 0 | 0 | 0
2021-11-28 18:30 | 0.391 | 1.409 | 0.61662 | 1.2978 | 0 | 0 | 0 | 0
2021-11-28 18:45 | 0.36752 | 1.2173 | 0.64521 | 1.182 | 0 | 0 | 0 | 0
2021-11-28 19:00 | 0.3471 | 1.0471 | 0.69421 | 1.2185 | 0 | 0 | 0 | 0
2021-11-28 19:15 | 0.39202 | 1.6967 | 0.73913 | 2.1357 | 0 | 0 | 0 | 0
2021-11-28 19:30 | 0.60029 | 1.5464 | 0.77997 | 2.2803 | 0 | 0 | 0 | 0
2021-11-28 19:45 | 1.2761 | 1.5464 | 0.73504 | 2.3118 | 0 | 0 | 0 | 0
2021-11-28 20:00 | 1.6539 | 1.4898 | 0.84122 | 1.3776 | 0 | 0 | 0 | 0
2021-11-28 20:15 | 1.5313 | 0.96906 | 0.89022 | 0.92406 | 0 | 0 | 0 | 0
2021-11-28 20:30 | 0.75546 | 1.0722 | 0.70238 | 1.1177 | 0 | 0 | 0 | 0
2021-11-28 20:45 | 0.55945 | 1.3531 | 0.50228 | 1.4643 | 0 | 0 | 0 | 0
2021-11-28 21:00 | 0.55945 | 1.1122 | 0.45328 | 1.1242 | 0 | 0 | 0 | 0
2021-11-28 21:15 | 0.53903 | 0.73877 | 0.5227 | 0.56178 | 0 | 0 | 0 | 0
2021-11-28 21:30 | 0.44103 | 0.7948 | 0.54312 | 0.65016 | 0 | 0 | 0 | 0
2021-11-28 21:45 | 0.44511 | 0.87133 | 0.46961 | 0.83393 | 0 | 0 | 0 | 0
2021-11-28 22:00 | 0.46553 | 0.61937 | 0.43694 | 0.4508 | 0 | 0 | 0 | 0
2021-11-28 22:15 | 0.46144 | 0.62116 | 0.35527 | 0.38838 | 0 | 0 | 0 | 0
2021-11-28 22:30 | 0.46144 | 0.63548 | 0.48186 | 0.4069 | 0 | 0 | 0 | 0
2021-11-28 22:45 | 0.45328 | 0.63727 | 0.31852 | 0.36869 | 0 | 0 | 0 | 0
2021-11-28 23:00 | 0.44919 | 0.96801 | 0.35833 | 1.9823 | 0 | 0 | 0 | 0
2021-11-28 23:15 | 0.40632 | 0.90069 | 0.35017 | 2.0947 | 0 | 0 | 0 | 0
2021-11-28 23:30 | 0.29402 | 0.87469 | 0.25114 | 2.071 | 0 | 0 | 0 | 0
2021-11-28 23:45 | 0.31444 | 0.96844 | 0.3226 | 2.1006 | 0 | 0 | 0 | 0
2021-11-29 | 0.28381 | 1.4911 | 0.30116 | 1.8906 | 0 | 0 | 0 | 0
2021-11-29 00:15 | 0.20214 | 1.2677 | 0.3175 | 1.7615 | 0 | 0 | 0 | 0
2021-11-29 00:30 | 0.27666 | 1.2628 | 0.31341 | 1.7228 | 0 | 0 | 0 | 0
2021-11-29 00:45 | 0.29708 | 1.3195 | 0.28177 | 1.6763 | 0 | 0 | 0 | 0
2021-11-29 01:00 | 0.38896 | 1.3523 | 0.38386 | 1.7307 | 0 | 0 | 0 | 0
2021-11-29 01:15 | 0.24808 | 1.2469 | 0.29198 | 1.6553 | 0 | 0 | 0 | 0
2021-11-29 01:30 | 0.3471 | 1.2452 | 0.31239 | 1.6381 | 0 | 0 | 0 | 0
2021-11-29 01:45 | 0.29198 | 1.2469 | 0.28177 | 1.6629 | 0 | 0 | 0 | 0
2021-11-29 02:00 | 0.34302 | 1.1981 | 0.28279 | 1.6751 | 0 | 0 | 0 | 0
2021-11-29 02:15 | 0.25829 | 1.1964 | 0.27768 | 1.6565 | 0 | 0 | 0 | 0
2021-11-29 02:30 | 0.32362 | 1.1981 | 0.30729 | 1.6428 | 0 | 0 | 0 | 0
2021-11-29 02:45 | 0.35527 | 1.2267 | 0.26339 | 1.6508 | 0 | 0 | 0 | 0
2021-11-29 03:00 | 0.37365 | 1.3037 | 0.35425 | 1.6667 | 0 | 0 | 0 | 0
2021-11-29 03:15 | 0.2787 | 1.1144 | 0.37365 | 1.4975 | 0 | 0 | 0 | 0
2021-11-29 03:30 | 0.35527 | 1.1095 | 0.27564 | 1.317 | 0 | 0 | 0 | 0
2021-11-29 03:45 | 0.28381 | 1.1469 | 0.32056 | 1.3302 | 0 | 0 | 0 | 0
2021-11-29 04:00 | 0.33281 | 1.1766 | 0.28891 | 1.3286 | 0 | 0 | 0 | 0
2021-11-29 04:15 | 0.33792 | 0.94843 | 0.31239 | 1.2486 | 0 | 0 | 0 | 0
2021-11-29 04:30 | 0.31341 | 0.91134 | 0.33485 | 1.1961 | 0 | 0 | 0 | 0
2021-11-29 04:45 | 0.29912 | 0.91134 | 0.29606 | 1.2236 | 0 | 0 | 0 | 0
2021-11-29 05:00 | 0.26952 | 0.88077 | 0.3369 | 1.2206 | 0 | 0 | 0 | 0
2021-11-29 05:15 | 0.2685 | 0.92424 | 0.28789 | 1.2213 | 0 | 0 | 0 | 0
2021-11-29 05:30 | 0.27768 | 0.90869 | 0.26339 | 1.0536 | 0 | 0 | 0 | 0
2021-11-29 05:45 | 0.2542 | 0.8807 | 0.34098 | 0.95104 | 0 | 0 | 0 | 0
2021-11-29 06:00 | 0.25522 | 0.81611 | 0.30014 | 0.79353 | 0 | 0 | 0 | 0
2021-11-29 06:15 | 0.2542 | 0.90528 | 0.3226 | 0.7543 | 0 | 0 | 0 | 0
2021-11-29 06:30 | 0.30321 | 0.89019 | 0.35731 | 0.7645 | 0 | 0 | 0 | 0
2021-11-29 06:45 | 0.30627 | 0.89019 | 0.31954 | 0.78551 | 0 | 1e-06 | 0 | 0
2021-11-29 07:00 | 0.27462 | 0.66244 | 0.25829 | 0.37175 | 0 | 3e-06 | 0 | 0
2021-11-29 07:15 | 0.2542 | 0.7578 | 0.35119 | 0.31064 | 0 | 4e-06 | 0 | 0
2021-11-29 07:30 | 0.30729 | 0.79937 | 0.34302 | 0.36884 | 0 | 5e-06 | 0 | 0
2021-11-29 07:45 | 0.26645 | 1.1007 | 0.28891 | 0.5421 | 0.035871 | 0.016052 | 0.00403 | 0.017575
2021-11-29 08:00 | 0.29708 | 1.6654 | 0.35935 | 1.5878 | 0.16946 | 0.061463 | 0.018591 | 0.074761
2021-11-29 08:15 | 0.28585 | 1.566 | 0.34915 | 1.2239 | 0.30304 | 0.10691 | 0.033152 | 0.13195
2021-11-29 08:30 | 0.47778 | 1.5585 | 0.41653 | 1.0226 | 0.43663 | 0.14592 | 0.047713 | 0.18913
2021-11-29 08:45 | 1.6539 | 1.4892 | 0.49003 | 0.98443 | 0.5173 | 0.17939 | 0.066573 | 0.23282
2021-11-29 09:00 | 0.8208 | 1.4879 | 2.3889 | 1.3467 | 0.45355 | 0.21869 | 0.096686 | 0.24667
2021-11-29 09:15 | 0.5962 | 1.3556 | 1.7253 | 1.3111 | 0.38981 | 0.23168 | 0.1268 | 0.26052
2021-11-29 09:30 | 0.84122 | 1.2785 | 0.53087 | 0.52328 | 0.32607 | 0.24162 | 0.15691 | 0.27437
2021-11-29 09:45 | 0.80855 | 1.301 | 0.62479 | 0.48536 | 0.27025 | 0.24846 | 0.16837 | 0.28438
2021-11-29 10:00 | 0.80447 | 1.4708 | 0.62887 | 0.63091 | 0.23608 | 0.26046 | 0.1309 | 0.28494
2021-11-29 10:15 | 0.75138 | 1.3378 | 2.7973 | 1.244 | 0.20191 | 0.27975 | 0.093428 | 0.28549
2021-11-29 10:30 | 0.81263 | 1.4563 | 2.4195 | 1.3558 | 0.16774 | 0.27094 | 0.055958 | 0.28605
2021-11-29 10:45 | 0.91064 | 1.5022 | 0.60845 | 1.1335 | 0.13779 | 0.24656 | 0.028306 | 0.28259
2021-11-29 11:00 | 0.61254 | 1.415 | 0.58395 | 1.0909 | 0.1194 | 0.24952 | 0.026441 | 0.26879
2021-11-29 11:15 | 1.9397 | 1.3866 | 0.62479 | 1.4698 | 0.101 | 0.2496 | 0.024576 | 0.25499
2021-11-29 11:30 | 0.7963 | 1.3166 | 0.48595 | 1.2156 | 0.08261 | 0.25456 | 0.022711 | 0.24119
2021-11-29 11:45 | 0.62479 | 1.5296 | 0.58804 | 1.2962 | 0.070925 | 0.24354 | 0.021237 | 0.2388
2021-11-29 12:00 | 0.7473 | 1.4443 | 0.63296 | 1.3814 | 0.077645 | 0.24942 | 0.020789 | 0.26419
2021-11-29 12:15 | 1.1638 | 1.6639 | 0.62887 | 1.2744 | 0.084364 | 0.24331 | 0.020342 | 0.28958
2021-11-29 12:30 | 1.9091 | 1.6439 | 0.42878 | 1.3174 | 0.091083 | 0.23849 | 0.019894 | 0.31496
2021-11-29 12:45 | 1.4701 | 1.7179 | 0.4737 | 1.2255 | 0.09497 | 0.24292 | 0.019487 | 0.33114
2021-11-29 13:00 | 0.43694 | 1.6881 | 0.49411 | 1.6189 | 0.09107 | 0.24219 | 0.019184 | 0.32629
2021-11-29 13:15 | 0.46144 | 1.4989 | 0.31954 | 0.85464 | 0.08717 | 0.2366 | 0.018882 | 0.32144
2021-11-29 13:30 | 1.3272 | 1.3316 | 0.26645 | 0.74555 | 0.083271 | 0.23612 | 0.018579 | 0.31658
2021-11-29 13:45 | 0.27768 | 1.3712 | 2.9402 | 1.1517 | 0.080481 | 0.22918 | 0.018017 | 0.31155
2021-11-29 14:00 | 1.2047 | 1.3457 | 5.0673 | 1.5656 | 0.080746 | 0.21455 | 0.01677 | 0.30595
2021-11-29 14:15 | 2.981 | 1.3344 | 5.196 | 1.2221 | 0.081011 | 0.20734 | 0.015523 | 0.30036
2021-11-29 14:30 | 0.46144 | 1.3196 | 5.2737 | 1.0871 | 0.081276 | 0.20723 | 0.014275 | 0.29476
2021-11-29 14:45 | 0.34506 | 1.4373 | 4.1436 | 0.87196 | 0.07605 | 0.1878 | 0.013458 | 0.2731
2021-11-29 15:00 | 0.34404 | 1.362 | 1.1332 | 0.47865 | 0.055684 | 0.14415 | 0.013778 | 0.2144
2021-11-29 15:15 | 0.24093 | 1.3088 | 0.26441 | 0.39596 | 0.035319 | 0.1187 | 0.014098 | 0.15569
2021-11-29 15:30 | 0.26952 | 1.4209 | 0.32056 | 0.31648 | 0.014953 | 0.090112 | 0.014418 | 0.096982
2021-11-29 15:45 | 0.33179 | 1.4745 | 0.23583 | 0.3086 | 0 | 0.07878 | 0.013647 | 0.051754
2021-11-29 16:00 | 0.26952 | 1.4742 | 0.28177 | 0.32902 | 0 | 0.050441 | 0.009984 | 0.037734
2021-11-29 16:15 | 0.26237 | 1.0285 | 0.32567 | 0.4699 | 0 | 0.033755 | 0.006322 | 0.023714
2021-11-29 16:30 | 2.9096 | 1.3308 | 0.30933 | 0.61093 | 0 | 0.013468 | 0.00266 | 0.009694
2021-11-29 16:45 | 4.5414 | 1.3572 | 0.23583 | 0.61006 | 0 | 0 | 0 | 0
2021-11-29 17:00 | 5.558 | 1.3306 | 0.30627 | 1.1008 | 0 | 0 | 0 | 0
2021-11-29 17:15 | 5.5961 | 1.4539 | 0.28381 | 1.2735 | 0 | 0 | 0 | 0
2021-11-29 17:30 | 4.1806 | 1.4008 | 0.2685 | 1.211 | 0 | 0 | 0 | 0
2021-11-29 17:45 | 4.053 | 1.2694 | 0.31444 | 1.0457 | 0 | 0 | 0 | 0
2021-11-29 18:00 | 4.4151 | 1.4402 | 0.33485 | 1.0533 | 0 | 0 | 0 | 0
2021-11-29 18:15 | 4.1255 | 1.4402 | 0.34506 | 1.0813 | 0 | 0 | 0 | 0
2021-11-29 18:30 | 3.9713 | 1.5833 | 0.391 | 1.2603 | 0 | 0 | 0 | 0
2021-11-29 18:45 | 3.9407 | 1.4817 | 0.36752 | 1.1592 | 0 | 0 | 0 | 0
2021-11-29 19:00 | 4.0121 | 1.5131 | 0.3471 | 1.2021 | 0 | 0 | 0 | 0
2021-11-29 19:15 | 3.9407 | 2.0214 | 0.39202 | 2.0663 | 0 | 0 | 0 | 0
2021-11-29 19:30 | 4.0872 | 2.0077 | 0.60029 | 2.2617 | 0 | 0 | 0 | 0
2021-11-29 19:45 | 5.581 | 2.044 | 1.2761 | 2.3926 | 0 | 0 | 0 | 0
2021-11-29 20:00 | 2.7973 | 1.5254 | 1.6539 | 1.4966 | 0 | 0 | 0 | 0
2021-11-29 20:15 | 2.3889 | 1.2797 | 1.5313 | 1.0606 | 0 | 0 | 0 | 0
2021-11-29 20:30 | 2.1439 | 1.2378 | 0.75546 | 0.97481 | 0 | 0 | 0 | 0
2021-11-29 20:45 | 2.1337 | 1.44 | 0.55945 | 1.2962 | 0 | 0 | 0 | 0
2021-11-29 21:00 | 1.9193 | 1.3892 | 0.55945 | 1.0393 | 0 | 0 | 0 | 0
2021-11-29 21:15 | 0.75546 | 0.91703 | 0.53903 | 0.56237 | 0 | 0 | 0 | 0
2021-11-29 21:30 | 0.71871 | 1.0912 | 0.44103 | 0.64492 | 0 | 0 | 0 | 0
2021-11-29 21:45 | 0.63704 | 1.0249 | 0.44511 | 0.83334 | 0 | 0 | 0 | 0
2021-11-29 22:00 | 0.59212 | 0.72059 | 0.46553 | 0.4543 | 0 | 0 | 0 | 0
2021-11-29 22:15 | 0.60029 | 0.68403 | 0.46144 | 0.38896 | 0 | 0 | 0 | 0
2021-11-29 22:30 | 0.69421 | 0.70265 | 0.46144 | 0.41711 | 0 | 0 | 0 | 0
2021-11-29 22:45 | 0.77997 | 0.71436 | 0.45328 | 0.38167 | 0 | 0 | 0 | 0
2021-11-29 23:00 | 3.369 | 1.8042 | 0.44919 | 1.9956 | 0 | 0 | 0 | 0
2021-11-29 23:15 | 3.5731 | 2.1143 | 0.40632 | 2.1022 | 0 | 0 | 0 | 0
2021-11-29 23:30 | 3.6344 | 2.045 | 0.29402 | 2.0593 | 0 | 0 | 0 | 0
2021-11-29 23:45 | 3.6242 | 2.0939 | 0.31444 | 2.0801 | 0 | 0 | 0 | 0
2021-11-30 | 3.665 | 1.3623 | 0.28381 | 1.8617 | 0 | 0 | 0 | 0
2021-11-30 00:15 | 3.6344 | 1.0152 | 0.20214 | 1.7145 | 0 | 0 | 0 | 0
2021-11-30 00:30 | 3.6038 | 1.0692 | 0.27666 | 1.6924 | 0 | 0 | 0 | 0
2021-11-30 00:45 | 3.614 | 0.94931 | 0.29708 | 1.6592 | 0 | 0 | 0 | 0
2021-11-30 01:00 | 3.614 | 1.0363 | 0.38896 | 1.7116 | 0 | 0 | 0 | 0
2021-11-30 01:15 | 3.6344 | 0.90672 | 0.24808 | 1.6458 | 0 | 0 | 0 | 0
2021-11-30 01:30 | 3.5731 | 0.87108 | 0.3471 | 1.6562 | 0 | 0 | 0 | 0
2021-11-30 01:45 | 3.5323 | 0.89708 | 0.29198 | 1.6585 | 0 | 0 | 0 | 0
2021-11-30 02:00 | 3.4506 | 0.90067 | 0.34302 | 1.6754 | 0 | 0 | 0 | 0
2021-11-30 02:15 | 3.4506 | 0.86818 | 0.25829 | 1.6544 | 0 | 0 | 0 | 0
2021-11-30 02:30 | 3.5017 | 0.89418 | 0.32362 | 1.6506 | 0 | 0 | 0 | 0
2021-11-30 02:45 | 3.5833 | 0.89102 | 0.35527 | 1.6689 | 0 | 0 | 0 | 0
2021-11-30 03:00 | 3.5731 | 1.0645 | 0.37365 | 1.6851 | 0 | 0 | 0 | 0
2021-11-30 03:15 | 3.5119 | 1.1707 | 0.2787 | 1.4959 | 0 | 0 | 0 | 0
2021-11-30 03:30 | 3.4506 | 1.0724 | 0.35527 | 1.3216 | 0 | 0 | 0 | 0
2021-11-30 03:45 | 3.5017 | 1.0724 | 0.28381 | 1.3072 | 0 | 0 | 0 | 0
2021-11-30 04:00 | 3.4813 | 1.0813 | 0.33281 | 1.2857 | 0 | 0 | 0 | 0
2021-11-30 04:15 | 3.5731 | 0.92507 | 0.33792 | 1.2478 | 0 | 0 | 0 | 0
2021-11-30 04:30 | 3.4813 | 0.83188 | 0.31341 | 1.209 | 0 | 0 | 0 | 0
2021-11-30 04:45 | 3.5323 | 0.81858 | 0.29912 | 1.2166 | 0 | 0 | 0 | 0
2021-11-30 05:00 | 3.5119 | 0.79816 | 0.26952 | 1.2045 | 0 | 0 | 0 | 0
2021-11-30 05:15 | 3.5119 | 0.79921 | 0.2685 | 1.2019 | 0 | 0 | 0 | 0
2021-11-30 05:30 | 3.471 | 0.84792 | 0.27768 | 1.0429 | 0 | 0 | 0 | 0
2021-11-30 05:45 | 3.471 | 0.8536 | 0.2542 | 0.95264 | 0 | 0 | 0 | 0
2021-11-30 06:00 | 3.4813 | 0.81032 | 0.25522 | 0.79819 | 0 | 0 | 0 | 0
2021-11-30 06:15 | 3.4302 | 0.82283 | 0.2542 | 0.74467 | 0 | 0 | 0 | 0
2021-11-30 06:30 | 2.1745 | 0.84462 | 0.30321 | 0.76844 | 0 | 0 | 0 | 0
2021-11-30 06:45 | 1.6334 | 0.8269 | 0.30627 | 0.78813 | 0 | 1e-06 | 0 | 0
2021-11-30 07:00 | 0.42469 | 0.66345 | 0.27462 | 0.37044 | 0 | 3e-06 | 0 | 0
2021-11-30 07:15 | 0.42469 | 0.67482 | 0.2542 | 0.29621 | 0 | 4e-06 | 0 | 0
2021-11-30 07:30 | 0.40632 | 0.66735 | 0.30729 | 0.35965 | 0 | 5e-06 | 0 | 0
2021-11-30 07:45 | 0.4982 | 0.78668 | 0.26645 | 0.54195 | 0.000324 | 0.016012 | 0.035871 | 0.021621
2021-11-30 08:00 | 2.736 | 1.4602 | 0.29708 | 1.596 | 0.001569 | 0.070768 | 0.16946 | 0.094585
2021-11-30 08:15 | 1.5211 | 1.102 | 0.28585 | 1.2289 | 0.002814 | 0.12837 | 0.30304 | 0.16755
2021-11-30 08:30 | 0.8453 | 1.1543 | 0.47778 | 1.0477 | 0.004059 | 0.16823 | 0.43663 | 0.24051
2021-11-30 08:45 | 0.85755 | 1.124 | 1.6539 | 1.1705 | 0.005001 | 0.20553 | 0.5173 | 0.29433
2021-11-30 09:00 | 0.56762 | 1.4158 | 0.8208 | 1.3415 | 0.005084 | 0.21979 | 0.45355 | 0.30163
2021-11-30 09:15 | 0.51045 | 1.2884 | 0.5962 | 1.265 | 0.005166 | 0.25086 | 0.38981 | 0.30894
2021-11-30 09:30 | 0.52678 | 1.0941 | 0.84122 | 0.56645 | 0.005249 | 0.2639 | 0.32607 | 0.31624
2021-11-30 09:45 | 0.51453 | 1.0193 | 0.80855 | 0.53028 | 0.014988 | 0.27398 | 0.27025 | 0.31946
2021-11-30 10:00 | 0.51862 | 1.2054 | 0.80447 | 0.65716 | 0.052265 | 0.27492 | 0.23608 | 0.31344
2021-11-30 10:15 | 0.4737 | 1.3314 | 0.75138 | 1.2551 | 0.089541 | 0.26144 | 0.20191 | 0.30742
2021-11-30 10:30 | 0.4982 | 1.3793 | 0.81263 | 1.382 | 0.12682 | 0.20647 | 0.16774 | 0.3014
2021-11-30 10:45 | 0.53903 | 1.2815 | 0.91064 | 1.1971 | 0.14744 | 0.18961 | 0.13779 | 0.29172
2021-11-30 11:00 | 0.66971 | 1.2421 | 0.61254 | 1.1037 | 0.12047 | 0.19743 | 0.1194 | 0.27287
2021-11-30 11:15 | 0.55537 | 1.3691 | 1.9397 | 1.4756 | 0.093508 | 0.2045 | 0.101 | 0.25401
2021-11-30 11:30 | 0.58395 | 1.2149 | 0.7963 | 1.201 | 0.066543 | 0.20456 | 0.08261 | 0.23516
2021-11-30 11:45 | 0.59212 | 1.3779 | 0.62479 | 1.3299 | 0.05084 | 0.18399 | 0.070925 | 0.22664
2021-11-30 12:00 | 0.60845 | 1.3905 | 0.7473 | 1.3482 | 0.067372 | 0.20469 | 0.077645 | 0.24425
2021-11-30 12:15 | 1.1842 | 1.3474 | 1.1638 | 1.3964 | 0.083903 | 0.20475 | 0.084364 | 0.26187
2021-11-30 12:30 | 2.0418 | 1.4897 | 1.9091 | 1.5512 | 0.10043 | 0.1978 | 0.091083 | 0.27949
2021-11-30 12:45 | 1.9907 | 1.4918 | 1.4701 | 1.4017 | 0.106 | 0.19644 | 0.09497 | 0.2906
2021-11-30 13:00 | 1.3067 | 1.3336 | 0.43694 | 1.4961 | 0.08012 | 0.18221 | 0.09107 | 0.28604
2021-11-30 13:15 | 1.2659 | 0.86979 | 0.46144 | 0.50636 | 0.054243 | 0.178 | 0.08717 | 0.28148
2021-11-30 13:30 | 0.43694 | 1.108 | 1.3272 | 0.76305 | 0.028365 | 0.17156 | 0.083271 | 0.27692
2021-11-30 13:45 | 0.42878 | 1.2003 | 0.27768 | 1.1386 | 0.008958 | 0.16656 | 0.080481 | 0.27184
2021-11-30 14:00 | 0.44919 | 1.5504 | 1.2047 | 1.5451 | 0.008138 | 0.16726 | 0.080746 | 0.2656
2021-11-30 14:15 | 0.5472 | 1.4575 | 2.981 | 1.4409 | 0.007318 | 0.16164 | 0.081011 | 0.25936
2021-11-30 14:30 | 0.44103 | 1.2807 | 0.46144 | 1.0544 | 0.006498 | 0.16481 | 0.081276 | 0.25312
2021-11-30 14:45 | 0.42878 | 1.3225 | 0.34506 | 0.83959 | 0.00551 | 0.15813 | 0.07605 | 0.23442
2021-11-30 15:00 | 0.45328 | 0.96023 | 0.34404 | 0.45722 | 0.004038 | 0.14056 | 0.055684 | 0.1857
2021-11-30 15:15 | 0.49411 | 0.82286 | 0.24093 | 0.35571 | 0.002566 | 0.11971 | 0.035319 | 0.13697
2021-11-30 15:30 | 0.42878 | 0.77704 | 0.26952 | 0.31429 | 0.001093 | 0.095694 | 0.014953 | 0.088242
2021-11-30 15:45 | 0.48595 | 0.83059 | 0.33179 | 0.32567 | 0 | 0.057839 | 0 | 0.049774
2021-11-30 16:00 | 0.58395 | 0.87105 | 0.26952 | 0.33194 | 0 | 0.052735 | 0 | 0.036292
2021-11-30 16:15 | 0.51045 | 0.83088 | 0.26237 | 0.38371 | 0 | 0.032946 | 0 | 0.022811
2021-11-30 16:30 | 0.44103 | 1.1729 | 2.9096 | 0.73198 | 0 | 0.010119 | 0 | 0.00933
2021-11-30 16:45 | 0.46961 | 1.1264 | 4.5414 | 0.96423 | 0 | 0 | 0 | 0
2021-11-30 17:00 | 0.58395 | 1.0931 | 5.558 | 1.2062 | 0 | 0 | 0 | 0
2021-11-30 17:15 | 0.48186 | 1.245 | 5.5961 | 1.3252 | 0 | 0 | 0 | 0
2021-11-30 17:30 | 0.61662 | 1.2215 | 4.1806 | 1.0857 | 0 | 0 | 0 | 0
2021-11-30 17:45 | 0.50228 | 1.3174 | 4.053 | 1.0821 | 0 | 0 | 0 | 0
2021-11-30 18:00 | 0.50636 | 1.3005 | 4.4151 | 1.1269 | 0 | 0 | 0 | 0
2021-11-30 18:15 | 0.53495 | 1.277 | 4.1255 | 1.1223 | 0 | 0 | 0 | 0
2021-11-30 18:30 | 0.58395 | 1.283 | 3.9713 | 1.0391 | 0 | 0 | 0 | 0
2021-11-30 18:45 | 0.66971 | 1.2824 | 3.9407 | 1.0237 | 0 | 0 | 0 | 0
2021-11-30 19:00 | 0.65337 | 1.3205 | 4.0121 | 1.1039 | 0 | 0 | 0 | 0
2021-11-30 19:15 | 0.4737 | 1.8981 | 3.9407 | 1.9703 | 0 | 0 | 0 | 0
2021-11-30 19:30 | 0.44103 | 1.8466 | 4.0872 | 2.183 | 0 | 0 | 0 | 0
2021-11-30 19:45 | 1.2047 | 1.9911 | 5.581 | 2.5374 | 0 | 0 | 0 | 0
2021-11-30 20:00 | 1.5518 | 1.4205 | 2.7973 | 1.3111 | 0 | 0 | 0 | 0
2021-11-30 20:15 | 1.613 | 1.278 | 2.3889 | 1.0693 | 0 | 0 | 0 | 0
2021-11-30 20:30 | 0.60845 | 1.1578 | 2.1439 | 0.95877 | 0 | 0 | 0 | 0
2021-11-30 20:45 | 0.63704 | 1.4339 | 2.1337 | 1.2992 | 0 | 0 | 0 | 0
2021-11-30 21:00 | 2.5931 | 1.0308 | 1.9193 | 0.90218 | 0 | 0 | 0 | 0
2021-11-30 21:15 | 2.3276 | 0.90626 | 0.75546 | 0.58454 | 0 | 0 | 0 | 0
2021-11-30 21:30 | 2.1643 | 0.93785 | 0.71871 | 0.64433 | 0 | 0 | 0 | 0
2021-11-30 21:45 | 1.0719 | 1.0414 | 0.63704 | 0.87009 | 0 | 0 | 0 | 0
2021-11-30 22:00 | 3.1648 | 0.66411 | 0.59212 | 0.47413 | 0 | 0 | 0 | 0
2021-11-30 22:15 | 1.0719 | 0.66171 | 0.60029 | 0.40646 | 0 | 0 | 0 | 0
2021-11-30 22:30 | 0.46144 | 0.66061 | 0.69421 | 0.45328 | 0 | 0 | 0 | 0
2021-11-30 22:45 | 0.49003 | 0.66411 | 0.77997 | 0.44774 | 0 | 0 | 0 | 0
2021-11-30 23:00 | 0.36854 | 1.8288 | 3.369 | 2.0262 | 0 | 0 | 0 | 0
2021-11-30 23:15 | 0.34915 | 1.9602 | 3.5731 | 2.1284 | 0 | 0 | 0 | 0
2021-11-30 23:30 | 0.3665 | 1.7608 | 3.6344 | 2.0914 | 0 | 0 | 0 | 0
2021-11-30 23:45 | 0.43286 | 1.8445 | 3.6242 | 2.1195 | 0 | 0 | 0 | 0
2021-12-01 | 0.45736 | 2.1239 | 3.665 | 2.1198 | 0 | 0 | 0 | 0
2021-12-01 00:15 | 0.37467 | 1.7581 | 3.6344 | 2.0984 | 0 | 0 | 0 | 0
2021-12-01 00:30 | 0.3614 | 2.0998 | 3.6038 | 2.1144 | 0 | 0 | 0 | 0
2021-12-01 00:45 | 0.36752 | 2.0998 | 3.614 | 2.1079 | 0 | 0 | 0 | 0
2021-12-01 01:00 | 0.45736 | 2.1086 | 3.614 | 2.186 | 0 | 0 | 0 | 0
2021-12-01 01:15 | 0.35119 | 1.9597 | 3.6344 | 2.1313 | 0 | 0 | 0 | 0
2021-12-01 01:30 | 0.31648 | 1.9501 | 3.5731 | 2.1325 | 0 | 0 | 0 | 0
2021-12-01 01:45 | 0.32669 | 1.8184 | 3.5323 | 2.1144 | 0 | 0 | 0 | 0
2021-12-01 02:00 | 0.38692 | 1.7523 | 3.4506 | 2.1189 | 0 | 0 | 0 | 0
2021-12-01 02:15 | 0.293 | 1.6842 | 3.4506 | 2.1006 | 0 | 0 | 0 | 0
2021-12-01 02:30 | 0.31341 | 1.7511 | 3.5017 | 2.1166 | 0 | 0 | 0 | 0
2021-12-01 02:45 | 0.39407 | 1.7523 | 3.5833 | 2.1497 | 0 | 0 | 0 | 0
2021-12-01 03:00 | 0.32873 | 1.7466 | 3.5731 | 2.1642 | 0 | 0 | 0 | 0
2021-12-01 03:15 | 0.3175 | 1.6782 | 3.5119 | 1.9619 | 0 | 0 | 0 | 0
2021-12-01 03:30 | 0.3369 | 1.7067 | 3.4506 | 1.782 | 0 | 0 | 0 | 0
2021-12-01 03:45 | 0.39202 | 1.6052 | 3.5017 | 1.7656 | 0 | 0 | 0 | 0
2021-12-01 04:00 | 0.31239 | 1.6197 | 3.4813 | 1.7253 | 0 | 0 | 0 | 0
2021-12-01 04:15 | 0.31341 | 1.5721 | 3.5731 | 1.7135 | 0 | 0 | 0 | 0
2021-12-01 04:30 | 0.39202 | 1.4489 | 3.4813 | 1.6725 | 0 | 0 | 0 | 0
2021-12-01 04:45 | 0.3369 | 1.5489 | 3.5323 | 1.6868 | 0 | 0 | 0 | 0
2021-12-01 05:00 | 0.30525 | 1.3169 | 3.5119 | 1.6743 | 0 | 0 | 0 | 0
2021-12-01 05:15 | 0.31035 | 1.3169 | 3.5119 | 1.6711 | 0 | 0 | 0 | 0
2021-12-01 05:30 | 0.42061 | 1.4845 | 3.471 | 1.4965 | 0 | 0 | 0 | 0
2021-12-01 05:45 | 0.33894 | 1.4309 | 3.471 | 1.3998 | 0 | 0 | 0 | 0
2021-12-01 06:00 | 0.3226 | 1.5373 | 3.4813 | 1.2602 | 0 | 0 | 0 | 0
2021-12-01 06:15 | 0.30933 | 1.6529 | 3.4302 | 1.2006 | 0 | 0 | 0 | 0
2021-12-01 06:30 | 0.37773 | 1.6403 | 2.1745 | 1.0412 | 0 | 0 | 0 | 0
2021-12-01 06:45 | 0.29198 | 1.583 | 1.6334 | 0.98706 | 0 | 1e-06 | 0 | 0
2021-12-01 07:00 | 0.35731 | 0.6029 | 0.42469 | 0.37219 | 0 | 3e-06 | 0 | 0
2021-12-01 07:15 | 0.40836 | 0.58076 | 0.42469 | 0.31794 | 0 | 4e-06 | 0 | 0
2021-12-01 07:30 | 0.39611 | 0.5907 | 0.40632 | 0.37015 | 0 | 5e-06 | 0 | 0
2021-12-01 07:45 | 0.58804 | 0.74114 | 0.4982 | 0.50228 | 0.001309 | 0.017437 | 0.000324 | 0.015966
2021-12-01 08:00 | 0.93514 | 1.4614 | 2.736 | 1.6762 | 0.006504 | 0.05846 | 0.001569 | 0.071171
2021-12-01 08:15 | 1.0515 | 1.553 | 1.5211 | 1.305 | 0.011699 | 0.08817 | 0.002814 | 0.12638
2021-12-01 08:30 | 0.48595 | 1.4337 | 0.8453 | 1.0571 | 0.016893 | 0.11352 | 0.004059 | 0.18158
2021-12-01 08:45 | 0.67788 | 1.3366 | 0.85755 | 1.2195 | 0.020011 | 0.13157 | 0.005001 | 0.22195
2021-12-01 09:00 | 0.72688 | 1.3255 | 0.56762 | 1.352 | 0.016956 | 0.15044 | 0.005084 | 0.22502
2021-12-01 09:15 | 1.7253 | 1.3729 | 0.51045 | 1.2615 | 0.013902 | 0.15869 | 0.005166 | 0.22809
2021-12-01 09:30 | 3.6854 | 1.0125 | 0.52678 | 0.59125 | 0.010847 | 0.16694 | 0.005249 | 0.23117
2021-12-01 09:45 | 3.5323 | 0.92895 | 0.51453 | 0.54195 | 0.010507 | 0.17388 | 0.014988 | 0.2325
2021-12-01 10:00 | 3.5425 | 1.0957 | 0.51862 | 0.64141 | 0.018251 | 0.18059 | 0.052265 | 0.2306
2021-12-01 10:15 | 3.6242 | 1.1326 | 0.4737 | 1.2271 | 0.025996 | 0.16857 | 0.089541 | 0.2287
2021-12-01 10:30 | 3.6038 | 1.2613 | 0.4982 | 1.3855 | 0.03374 | 0.16204 | 0.12682 | 0.22681
2021-12-01 10:45 | 3.5936 | 1.1663 | 0.53903 | 1.2128 | 0.040375 | 0.1512 | 0.14744 | 0.21925
2021-12-01 11:00 | 3.5629 | 1.1447 | 0.66971 | 1.1577 | 0.043703 | 0.16241 | 0.12047 | 0.19651
2021-12-01 11:15 | 3.6548 | 1.1745 | 0.55537 | 1.5185 | 0.04703 | 0.17405 | 0.093508 | 0.17378
2021-12-01 11:30 | 3.5731 | 1.088 | 0.58395 | 1.2418 | 0.050357 | 0.16671 | 0.066543 | 0.15104
2021-12-01 11:45 | 3.471 | 1.221 | 0.59212 | 1.3569 | 0.05408 | 0.16676 | 0.05084 | 0.14025
2021-12-01 12:00 | 3.4608 | 1.0978 | 0.60845 | 1.3715 | 0.058987 | 0.18017 | 0.067372 | 0.1602
2021-12-01 12:15 | 3.4915 | 1.4595 | 1.1842 | 1.5173 | 0.063894 | 0.18618 | 0.083903 | 0.18015
2021-12-01 12:30 | 3.5221 | 1.4173 | 2.0418 | 1.6372 | 0.068802 | 0.18624 | 0.10043 | 0.2001
2021-12-01 12:45 | 3.471 | 1.2799 | 1.9907 | 1.4411 | 0.076644 | 0.18537 | 0.106 | 0.21265
2021-12-01 13:00 | 3.4608 | 1.3472 | 1.3067 | 1.4042 | 0.093275 | 0.18078 | 0.08012 | 0.20649
2021-12-01 13:15 | 4.1306 | 1.2395 | 1.2659 | 0.6102 | 0.10991 | 0.17096 | 0.054243 | 0.20034
2021-12-01 13:30 | 3.5833 | 1.17 | 0.43694 | 0.76305 | 0.12654 | 0.14713 | 0.028365 | 0.19418
2021-12-01 13:45 | 3.5323 | 1.2773 | 0.42878 | 1.1398 | 0.13246 | 0.16832 | 0.008958 | 0.18886
2021-12-01 14:00 | 3.5119 | 1.244 | 0.44919 | 1.5632 | 0.10627 | 0.16165 | 0.008138 | 0.18597
2021-12-01 14:15 | 3.5017 | 1.1683 | 0.5472 | 1.48 | 0.080081 | 0.15622 | 0.007318 | 0.18307
2021-12-01 14:30 | 3.4404 | 1.1533 | 0.44103 | 1.0785 | 0.053891 | 0.15877 | 0.006498 | 0.18018
2021-12-01 14:45 | 3.5323 | 1.0267 | 0.42878 | 0.85796 | 0.032103 | 0.15888 | 0.00551 | 0.16731
2021-12-01 15:00 | 3.91 | 1.0254 | 0.45328 | 0.45488 | 0.023544 | 0.12381 | 0.004038 | 0.12976
2021-12-01 15:15 | 3.8896 | 0.88889 | 0.49411 | 0.35979 | 0.014984 | 0.089744 | 0.002566 | 0.092209
2021-12-01 15:30 | 3.614 | 0.82599 | 0.42878 | 0.32275 | 0.006425 | 0.071309 | 0.001093 | 0.054661
2021-12-01 15:45 | 3.5833 | 0.87004 | 0.48595 | 0.34463 | 0 | 0.069279 | 0 | 0.02588
2021-12-01 16:00 | 3.6344 | 1.0692 | 0.58395 | 0.36446 | 0 | 0.05048 | 0 | 0.018882
2021-12-01 16:15 | 3.6854 | 0.81505 | 0.51045 | 0.41302 | 0 | 0.033597 | 0 | 0.011884
2021-12-01 16:30 | 3.6854 | 1.1465 | 0.44103 | 0.74803 | 0 | 0.013406 | 0 | 0.004887
2021-12-01 16:45 | 3.614 | 1.0433 | 0.46961 | 0.97298 | 0 | 0 | 0 | 0
2021-12-01 17:00 | 3.369 | 1.2674 | 0.58395 | 1.2537 | 0 | 0 | 0 | 0
2021-12-01 17:15 | 2.001 | 1.3206 | 0.48186 | 1.3488 | 0 | 0 | 0 | 0
2021-12-01 17:30 | 1.613 | 1.3956 | 0.61662 | 1.1285 | 0 | 0 | 0 | 0
2021-12-01 17:45 | 1.1332 | 1.323 | 0.50228 | 1.0972 | 0 | 0 | 0 | 0
2021-12-01 18:00 | 1.2353 | 1.2648 | 0.50636 | 1.1368 | 0 | 0 | 0 | 0
2021-12-01 18:15 | 0.64929 | 1.2698 | 0.53495 | 1.1351 | 0 | 0 | 0 | 0
2021-12-01 18:30 | 0.61254 | 1.3061 | 0.58395 | 1.0555 | 0 | 0 | 0 | 0
2021-12-01 18:45 | 0.57987 | 1.2105 | 0.66971 | 1.0301 | 0 | 0 | 0 | 0
2021-12-01 19:00 | 0.73913 | 1.2996 | 0.65337 | 1.047 | 0 | 0 | 0 | 0
2021-12-01 19:15 | 1.0127 | 1.2723 | 0.4737 | 1.4984 | 0 | 0 | 0 | 0
2021-12-01 19:30 | 1.8478 | 1.3424 | 0.44103 | 1.7239 | 0 | 0 | 0 | 0
2021-12-01 19:45 | 1.7049 | 1.5273 | 1.2047 | 2.183 | 0 | 0 | 0 | 0
2021-12-01 20:00 | 1.858 | 1.267 | 1.5518 | 1.3963 | 0 | 0 | 0 | 0
2021-12-01 20:15 | 1.0924 | 1.1812 | 1.613 | 1.1697 | 0 | 0 | 0 | 0
2021-12-01 20:30 | 0.85347 | 1.0116 | 0.60845 | 0.83859 | 0 | 0 | 0 | 0
2021-12-01 20:45 | 1.368 | 1.4211 | 0.63704 | 1.1874 | 0 | 0 | 0 | 0
2021-12-01 21:00 | 0.51862 | 1.3023 | 2.5931 | 1.1944 | 0 | 0 | 0 | 0
2021-12-01 21:15 | 0.36854 | 0.97888 | 2.3276 | 0.8523 | 0 | 0 | 0 | 0
2021-12-01 21:30 | 0.43286 | 0.98494 | 2.1643 | 0.86835 | 0 | 0 | 0 | 0
2021-12-01 21:45 | 0.43286 | 1.2439 | 1.0719 | 0.91122 | 0 | 0 | 0 | 0
2021-12-01 22:00 | 0.50636 | 0.99028 | 3.1648 | 0.83757 | 0 | 0 | 0 | 0
2021-12-01 22:15 | 0.60437 | 0.73269 | 1.0719 | 0.50301 | 0 | 0 | 0 | 0
2021-12-01 22:30 | 0.58395 | 0.627 | 0.46144 | 0.45561 | 0 | 0 | 0 | 0
2021-12-01 22:45 | 0.51045 | 0.65564 | 0.49003 | 0.43199 | 0 | 0 | 0 | 0
2021-12-01 23:00 | 1.4395 | 1.0754 | 0.36854 | 1.6136 | 0 | 0 | 0 | 0
2021-12-01 23:15 | 0.75955 | 1.0754 | 0.34915 | 1.6854 | 0 | 0 | 0 | 0
2021-12-01 23:30 | 0.46553 | 1.0754 | 0.3665 | 1.6522 | 0 | 0 | 0 | 0
2021-12-01 23:45 | 0.3226 | 1.0754 | 0.43286 | 1.6884 | 0 | 0 | 0 | 0
2021-12-02 | 0.32975 | 0.98078 | 0.45736 | 1.7053 | 0 | 0 | 0 | 0
2021-12-02 00:15 | 0.43694 | 0.98078 | 0.37467 | 1.6677 | 0 | 0 | 0 | 0
2021-12-02 00:30 | 0.3614 | 0.98078 | 0.3614 | 1.6746 | 0 | 0 | 0 | 0
2021-12-02 00:45 | 0.34506 | 0.98078 | 0.36752 | 1.6587 | 0 | 0 | 0 | 0
2021-12-02 01:00 | 0.29606 | 0.98078 | 0.45736 | 1.7526 | 0 | 0 | 0 | 0
2021-12-02 01:15 | 0.28687 | 0.98078 | 0.35119 | 1.6886 | 0 | 0 | 0 | 0
2021-12-02 01:30 | 0.32975 | 0.98078 | 0.31648 | 1.6877 | 0 | 0 | 0 | 0
2021-12-02 01:45 | 0.293 | 0.98078 | 0.32669 | 1.6696 | 0 | 0 | 0 | 0
2021-12-02 02:00 | 0.26748 | 0.94411 | 0.38692 | 1.6813 | 0 | 0 | 0 | 0
2021-12-02 02:15 | 0.28585 | 0.95887 | 0.293 | 1.6407 | 0 | 0 | 0 | 0
2021-12-02 02:30 | 0.34506 | 0.95887 | 0.31341 | 1.6611 | 0 | 0 | 0 | 0
2021-12-02 02:45 | 0.40223 | 1.2086 | 0.39407 | 1.7145 | 0 | 0 | 0 | 0
2021-12-02 03:00 | 0.29606 | 0.97179 | 0.32873 | 1.7182 | 0 | 0 | 0 | 0
2021-12-02 03:15 | 0.26033 | 0.95816 | 0.3175 | 1.5099 | 0 | 0 | 0 | 0
2021-12-02 03:30 | 0.25216 | 0.91273 | 0.3369 | 1.3285 | 0 | 0 | 0 | 0
2021-12-02 03:45 | 0.31444 | 0.91273 | 0.39202 | 1.3272 | 0 | 0 | 0 | 0
2021-12-02 04:00 | 0.39304 | 0.95745 | 0.31239 | 1.2712 | 0 | 0 | 0 | 0
2021-12-02 04:15 | 0.36752 | 0.9096 | 0.31341 | 1.2449 | 0 | 0 | 0 | 0
2021-12-02 04:30 | 0.28177 | 0.88035 | 0.39202 | 1.221 | 0 | 0 | 0 | 0
2021-12-02 04:45 | 0.31852 | 0.92436 | 0.3369 | 1.2362 | 0 | 0 | 0 | 0
2021-12-02 05:00 | 0.31239 | 0.89522 | 0.30525 | 1.2264 | 0 | 0 | 0 | 0
2021-12-02 05:15 | 0.32362 | 0.83023 | 0.31035 | 1.2166 | 0 | 0 | 0 | 0
2021-12-02 05:30 | 0.41244 | 0.83023 | 0.42061 | 1.0534 | 0 | 0 | 0 | 0
2021-12-02 05:45 | 0.28891 | 0.74695 | 0.33894 | 0.93777 | 0 | 0 | 0 | 0
2021-12-02 06:00 | 0.25114 | 0.70368 | 0.3226 | 0.81045 | 0 | 0 | 0 | 0
2021-12-02 06:15 | 0.27258 | 0.67557 | 0.30933 | 0.75182 | 0 | 0 | 0 | 0
2021-12-02 06:30 | 0.37773 | 0.75973 | 0.37773 | 0.59781 | 0 | 0 | 0 | 0
2021-12-02 06:45 | 0.27768 | 0.66151 | 0.29198 | 0.52562 | 0 | 0 | 0 | 0
2021-12-02 07:00 | 0.32362 | 0.56425 | 0.35731 | 0.33748 | 0 | 0 | 0 | 0
2021-12-02 07:15 | 0.28177 | 0.5499 | 0.40836 | 0.32844 | 0 | 0 | 0 | 0
2021-12-02 07:30 | 0.44511 | 0.54753 | 0.39611 | 0.37204 | 0 | 1e-06 | 0 | 0
2021-12-02 07:45 | 0.44919 | 0.69112 | 0.58804 | 0.46961 | 0.002389 | 0.010281 | 0.001309 | 0.010698
2021-12-02 08:00 | 1.2047 | 1.2837 | 0.93514 | 1.2351 | 0.012186 | 0.063901 | 0.006504 | 0.049024
2021-12-02 08:15 | 1.3272 | 1.1809 | 1.0515 | 0.90831 | 0.021982 | 0.10222 | 0.011699 | 0.087351
2021-12-02 08:30 | 0.89022 | 1.0698 | 0.48595 | 0.5927 | 0.031779 | 0.11338 | 0.016893 | 0.12568
2021-12-02 08:45 | 0.40223 | 1.0284 | 0.67788 | 0.78988 | 0.038367 | 0.12602 | 0.020011 | 0.15316
2021-12-02 09:00 | 0.83305 | 1.0931 | 0.72688 | 0.91764 | 0.034987 | 0.13189 | 0.016956 | 0.15206
2021-12-02 09:15 | 0.90247 | 1.1828 | 1.7253 | 0.95964 | 0.031608 | 0.16157 | 0.013902 | 0.15096
2021-12-02 09:30 | 2.1643 | 1.0173 | 3.6854 | 1.0162 | 0.028228 | 0.16997 | 0.010847 | 0.14986
2021-12-02 09:45 | 1.317 | 0.8551 | 3.5323 | 0.99231 | 0.03486 | 0.19167 | 0.010507 | 0.14812
2021-12-02 10:00 | 0.68196 | 0.88919 | 3.5425 | 1.0693 | 0.072649 | 0.2008 | 0.018251 | 0.14591
2021-12-02 10:15 | 0.60845 | 1.3784 | 3.6242 | 1.6644 | 0.11044 | 0.19459 | 0.025996 | 0.14369
2021-12-02 10:30 | 0.51045 | 1.4115 | 3.6038 | 1.8134 | 0.14823 | 0.20632 | 0.03374 | 0.14148
2021-12-02 10:45 | 0.4982 | 1.4395 | 3.5936 | 1.6381 | 0.18164 | 0.20817 | 0.040375 | 0.13378
2021-12-02 11:00 | 0.61662 | 1.3964 | 3.5629 | 1.5908 | 0.20143 | 0.2185 | 0.043703 | 0.11117
2021-12-02 11:15 | 2.0112 | 1.4501 | 3.6548 | 1.9837 | 0.22121 | 0.20302 | 0.04703 | 0.08857
2021-12-02 11:30 | 2.246 | 1.4455 | 3.5731 | 1.6961 | 0.24099 | 0.21319 | 0.050357 | 0.065965
2021-12-02 11:45 | 0.58395 | 1.4292 | 3.471 | 1.7874 | 0.24758 | 0.21876 | 0.05408 | 0.055571
2021-12-02 12:00 | 0.51045 | 1.4501 | 3.4608 | 1.8149 | 0.21294 | 0.20775 | 0.058987 | 0.076574
2021-12-02 12:15 | 0.55128 | 1.3988 | 3.4915 | 1.7069 | 0.1783 | 0.20174 | 0.063894 | 0.097576
2021-12-02 12:30 | 0.44919 | 1.4729 | 3.5221 | 1.627 | 0.14366 | 0.21297 | 0.068802 | 0.11858
2021-12-02 12:45 | 1.1638 | 0.8881 | 3.471 | 1.4309 | 0.11762 | 0.21254 | 0.076644 | 0.133
2021-12-02 13:00 | 3.0627 | 0.88694 | 3.4608 | 1.5165 | 0.11847 | 0.19382 | 0.093275 | 0.13088
2021-12-02 13:15 | 0.24399 | 0.90888 | 4.1306 | 1.0442 | 0.11933 | 0.17969 | 0.10991 | 0.12876
2021-12-02 13:30 | 0.24297 | 0.92497 | 3.5833 | 0.98181 | 0.12018 | 0.17445 | 0.12654 | 0.12663
2021-12-02 13:45 | 0.34098 | 0.90994 | 3.5323 | 1.15 | 0.12061 | 0.16523 | 0.13246 | 0.12414
2021-12-02 14:00 | 0.39202 | 0.88049 | 3.5119 | 1.572 | 0.11969 | 0.1577 | 0.10627 | 0.12023
2021-12-02 14:15 | 0.22256 | 0.88578 | 3.5017 | 1.8729 | 0.11877 | 0.16614 | 0.080081 | 0.11631
2021-12-02 14:30 | 0.21643 | 0.86036 | 3.4404 | 1.5164 | 0.11785 | 0.1685 | 0.053891 | 0.11239
2021-12-02 14:45 | 0.22664 | 0.86036 | 3.5323 | 1.3242 | 0.11272 | 0.16712 | 0.032103 | 0.10221
2021-12-02 15:00 | 0.23991 | 0.84482 | 3.91 | 0.96489 | 0.09438 | 0.12895 | 0.023544 | 0.076183
2021-12-02 15:15 | 0.35017 | 0.83807 | 3.8896 | 0.85916 | 0.076039 | 0.099185 | 0.014984 | 0.050159
2021-12-02 15:30 | 0.33179 | 0.84739 | 3.614 | 0.78944 | 0.057699 | 0.072902 | 0.006425 | 0.024134
2021-12-02 15:45 | 0.2491 | 0.84537 | 3.5833 | 0.80782 | 0.041141 | 0.059022 | 0 | 0.005004
2021-12-02 16:00 | 0.27054 | 0.86626 | 3.6344 | 0.82241 | 0.030197 | 0.044154 | 0 | 0.003658
2021-12-02 16:15 | 0.27156 | 0.85341 | 3.6854 | 0.84034 | 0.019253 | 0.026191 | 0 | 0.002313
2021-12-02 16:30 | 0.33485 | 0.88664 | 3.6854 | 1.2074 | 0.008309 | 0.011381 | 0 | 0.000967
2021-12-02 16:45 | 0.28891 | 0.82052 | 3.614 | 1.4303 | 0 | 0 | 0 | 0
2021-12-02 17:00 | 0.26952 | 0.93368 | 3.369 | 1.6679 | 0 | 0 | 0 | 0
2021-12-02 17:15 | 0.26952 | 0.91775 | 2.001 | 1.5612 | 0 | 0 | 0 | 0
2021-12-02 17:30 | 0.32669 | 0.97845 | 1.613 | 1.2703 | 0 | 0 | 0 | 0
2021-12-02 17:45 | 0.35527 | 0.97058 | 1.1332 | 1.1762 | 0 | 0 | 0 | 0
2021-12-02 18:00 | 0.35527 | 0.97058 | 1.2353 | 1.2176 | 0 | 0 | 0 | 0
2021-12-02 18:15 | 0.25625 | 0.97986 | 0.64929 | 1.1112 | 0 | 0 | 0 | 0
2021-12-02 18:30 | 0.26748 | 0.98165 | 0.61254 | 1.0298 | 0 | 0 | 0 | 0
2021-12-02 18:45 | 0.35017 | 0.9569 | 0.57987 | 1.0044 | 0 | 0 | 0 | 0
2021-12-02 19:00 | 0.41244 | 0.93786 | 0.73913 | 1.0313 | 0 | 0 | 0 | 0
2021-12-02 19:15 | 0.30423 | 0.84709 | 1.0127 | 1.4637 | 0 | 0 | 0 | 0
2021-12-02 19:30 | 0.31954 | 0.9384 | 1.8478 | 1.7429 | 0 | 0 | 0 | 0
2021-12-02 19:45 | 0.31035 | 1.0631 | 1.7049 | 2.2195 | 0 | 0 | 0 | 0
2021-12-02 20:00 | 0.29912 | 0.9402 | 1.858 | 1.4109 | 0 | 0 | 0 | 0
2021-12-02 20:15 | 0.44919 | 0.88479 | 1.0924 | 1.1551 | 0 | 0 | 0 | 0
2021-12-02 20:30 | 0.37671 | 0.78634 | 0.85347 | 0.80738 | 0 | 0 | 0 | 0
2021-12-02 20:45 | 0.29708 | 0.90453 | 1.368 | 0.83013 | 0 | 0 | 0 | 0
2021-12-02 21:00 | 0.2736 | 0.86978 | 0.51862 | 0.9506 | 0 | 0 | 0 | 0
2021-12-02 21:15 | 0.27973 | 0.79645 | 0.36854 | 0.74744 | 0 | 0 | 0 | 0
2021-12-02 21:30 | 0.35017 | 0.77927 | 0.43286 | 0.71434 | 0 | 0 | 0 | 0
2021-12-02 21:45 | 0.46144 | 0.75213 | 0.43286 | 0.55012 | 0 | 0 | 0 | 0
2021-12-02 22:00 | 0.51045 | 0.8309 | 0.50636 | 0.84632 | 0 | 0 | 0 | 0
2021-12-02 22:15 | 0.39407 | 0.66162 | 0.60437 | 0.5332 | 0 | 0 | 0 | 0
2021-12-02 22:30 | 0.35221 | 0.63625 | 0.58395 | 0.49149 | 0 | 0 | 0 | 0
2021-12-02 22:45 | 0.37977 | 0.75016 | 0.51045 | 0.44803 | 0 | 0 | 0 | 0
2021-12-02 23:00 | 3.2975 | 1.6296 | 1.4395 | 1.7723 | 0 | 0 | 0 | 0
2021-12-02 23:15 | 3.5119 | 1.7976 | 0.75955 | 1.7555 | 0 | 0 | 0 | 0
2021-12-02 23:30 | 3.4098 | 1.7808 | 0.46553 | 1.6902 | 0 | 0 | 0 | 0
2021-12-02 23:45 | 3.3894 | 1.8014 | 0.3226 | 1.7069 | 0 | 0 | 0 | 0
2021-12-03 | 3.4404 | 2.3696 | 0.32975 | 1.7244 | 0 | 0 | 0 | 0
2021-12-03 00:15 | 3.5323 | 2.3696 | 0.43694 | 1.6938 | 0 | 0 | 0 | 0
2021-12-03 00:30 | 3.4302 | 2.3696 | 0.3614 | 1.6839 | 0 | 0 | 0 | 0
2021-12-03 00:45 | 3.4915 | 2.3039 | 0.34506 | 1.6779 | 0 | 0 | 0 | 0
2021-12-03 01:00 | 3.4098 | 2.3696 | 0.29606 | 1.7508 | 0 | 0 | 0 | 0
2021-12-03 01:15 | 3.4302 | 2.3024 | 0.28687 | 1.6924 | 0 | 0 | 0 | 0
2021-12-03 01:30 | 3.471 | 2.2384 | 0.32975 | 1.6887 | 0 | 0 | 0 | 0
2021-12-03 01:45 | 3.3894 | 2.2428 | 0.293 | 1.6654 | 0 | 0 | 0 | 0
2021-12-03 02:00 | 3.3894 | 2.2214 | 0.26748 | 1.6821 | 0 | 0 | 0 | 0
2021-12-03 02:15 | 3.4813 | 2.0642 | 0.28585 | 1.6454 | 0 | 0 | 0 | 0
2021-12-03 02:30 | 3.5323 | 2.0902 | 0.34506 | 1.6762 | 0 | 0 | 0 | 0
2021-12-03 02:45 | 3.4302 | 2.2311 | 0.40223 | 1.7101 | 0 | 0 | 0 | 0
2021-12-03 03:00 | 3.4098 | 2.1638 | 0.29606 | 1.7202 | 0 | 0 | 0 | 0
2021-12-03 03:15 | 3.4098 | 1.9129 | 0.26033 | 1.5087 | 0 | 0 | 0 | 0
2021-12-03 03:30 | 3.4098 | 2.0112 | 0.25216 | 1.3264 | 0 | 0 | 0 | 0
2021-12-03 03:45 | 3.4404 | 2.1377 | 0.31444 | 1.3234 | 0 | 0 | 0 | 0
2021-12-03 04:00 | 3.4098 | 2.0065 | 0.39304 | 1.2811 | 0 | 0 | 0 | 0
2021-12-03 04:15 | 3.4302 | 1.9296 | 0.36752 | 1.2586 | 0 | 0 | 0 | 0
2021-12-03 04:30 | 3.3894 | 1.9898 | 0.28177 | 1.2261 | 0 | 0 | 0 | 0
2021-12-03 04:45 | 3.4813 | 1.9691 | 0.31852 | 1.2334 | 0 | 0 | 0 | 0
2021-12-03 05:00 | 3.471 | 1.8787 | 0.31239 | 1.23 | 0 | 0 | 0 | 0
2021-12-03 05:15 | 3.42 | 1.8787 | 0.32362 | 1.2201 | 0 | 0 | 0 | 0
2021-12-03 05:30 | 3.42 | 1.3393 | 0.41244 | 1.0724 | 0 | 0 | 0 | 0
2021-12-03 05:45 | 3.4915 | 1.2884 | 0.28891 | 0.92712 | 0 | 0 | 0 | 0
2021-12-03 06:00 | 3.5119 | 1.1553 | 0.25114 | 0.8103 | 0 | 0 | 0 | 0
2021-12-03 06:15 | 3.3894 | 0.94051 | 0.27258 | 0.75269 | 0 | 0 | 0 | 0
2021-12-03 06:30 | 3.4098 | 0.96595 | 0.37773 | 0.60918 | 0 | 0 | 0 | 0
2021-12-03 06:45 | 3.3485 | 0.74078 | 0.27768 | 0.51205 | 0 | 0 | 0 | 0
2021-12-03 07:00 | 0.51045 | 0.55292 | 0.32362 | 0.34156 | 0 | 0 | 0 | 0
2021-12-03 07:15 | 0.38896 | 0.57078 | 0.28177 | 0.33033 | 0 | 1e-06 | 0 | 0
2021-12-03 07:30 | 0.48595 | 0.59567 | 0.44511 | 0.38298 | 0 | 1e-06 | 0 | 0
2021-12-03 07:45 | 0.35629 | 0.6977 | 0.44919 | 0.43636 | 0.000613 | 0.015747 | 0.002389 | 0.008575
2021-12-03 08:00 | 3.8896 | 1.4826 | 1.2047 | 1.2468 | 0.003212 | 0.070132 | 0.012186 | 0.040127
2021-12-03 08:15 | 4.1841 | 1.3791 | 1.3272 | 0.96431 | 0.005812 | 0.11709 | 0.021982 | 0.071678
2021-12-03 08:30 | 3.6548 | 1.2624 | 0.89022 | 0.62712 | 0.008412 | 0.14703 | 0.031779 | 0.10323
2021-12-03 08:45 | 3.5833 | 1.0306 | 0.40223 | 0.75575 | 0.014091 | 0.14286 | 0.038367 | 0.12712
2021-12-03 09:00 | 2.1337 | 1.0738 | 0.83305 | 0.95322 | 0.029777 | 0.14952 | 0.034987 | 0.12946
2021-12-03 09:15 | 0.57987 | 1.084 | 0.90247 | 0.96723 | 0.045463 | 0.15233 | 0.031608 | 0.13179
2021-12-03 09:30 | 0.46144 | 1.1045 | 2.1643 | 1.2618 | 0.061149 | 0.16703 | 0.028228 | 0.13413
2021-12-03 09:45 | 0.64521 | 1.0428 | 1.317 | 1.1294 | 0.07944 | 0.17341 | 0.03486 | 0.1368
2021-12-03 10:00 | 0.76363 | 1.2631 | 0.68196 | 1.1198 | 0.10621 | 0.19173 | 0.072649 | 0.14239
2021-12-03 10:15 | 0.55128 | 1.3977 | 0.60845 | 1.4275 | 0.13299 | 0.21023 | 0.11044 | 0.14798
2021-12-03 10:30 | 0.54312 | 1.3807 | 0.51045 | 1.3715 | 0.15976 | 0.25433 | 0.14823 | 0.15357
2021-12-03 10:45 | 0.55128 | 1.2631 | 0.4982 | 1.1609 | 0.17703 | 0.26365 | 0.18164 | 0.15225
2021-12-03 11:00 | 0.38488 | 1.313 | 0.61662 | 1.1379 | 0.16333 | 0.27112 | 0.20143 | 0.13224
2021-12-03 11:15 | 0.4737 | 1.4057 | 2.0112 | 1.7606 | 0.14963 | 0.28175 | 0.22121 | 0.11224
2021-12-03 11:30 | 0.59212 | 1.2518 | 2.246 | 1.508 | 0.13593 | 0.27844 | 0.24099 | 0.092231
2021-12-03 11:45 | 0.38998 | 1.3719 | 0.58395 | 1.3663 | 0.1246 | 0.27853 | 0.24758 | 0.081161
2021-12-03 12:00 | 0.26441 | 1.3719 | 0.51045 | 1.3875 | 0.121 | 0.28601 | 0.21294 | 0.09236
2021-12-03 12:15 | 0.23685 | 1.1842 | 0.55128 | 1.2825 | 0.1174 | 0.29623 | 0.1783 | 0.10356
2021-12-03 12:30 | 0.20826 | 1.1642 | 0.44919 | 1.4024 | 0.1138 | 0.32781 | 0.14366 | 0.11476
2021-12-03 12:45 | 0.29402 | 1.1965 | 1.1638 | 1.5696 | 0.10646 | 0.29977 | 0.11762 | 0.1236
2021-12-03 13:00 | 0.48595 | 1.4588 | 3.0627 | 1.9259 | 0.086891 | 0.29992 | 0.11847 | 0.12674
2021-12-03 13:15 | 0.44103 | 1.1078 | 0.24399 | 1.0409 | 0.06732 | 0.28901 | 0.11933 | 0.12988
2021-12-03 13:30 | 0.53903 | 1.1632 | 0.24297 | 0.96329 | 0.047749 | 0.28218 | 0.12018 | 0.13302
2021-12-03 13:45 | 0.58395 | 1.1213 | 0.34098 | 1.1647 | 0.035538 | 0.26641 | 0.12061 | 0.13443
2021-12-03 14:00 | 0.53087 | 1.1628 | 0.39202 | 1.5965 | 0.047475 | 0.25586 | 0.11969 | 0.13117
2021-12-03 14:15 | 0.44919 | 1.1504 | 0.22256 | 1.8699 | 0.059411 | 0.21875 | 0.11877 | 0.1279
2021-12-03 14:30 | 0.36854 | 1.2168 | 0.21643 | 1.5013 | 0.071348 | 0.17247 | 0.11785 | 0.12464
2021-12-03 14:45 | 0.35833 | 1.2168 | 0.22664 | 1.3254 | 0.075917 | 0.17218 | 0.11272 | 0.11453
2021-12-03 15:00 | 0.41653 | 1.0978 | 0.23991 | 0.96635 | 0.056266 | 0.13769 | 0.09438 | 0.086752
2021-12-03 15:15 | 0.53495 | 1.1109 | 0.35017 | 0.86791 | 0.036615 | 0.11744 | 0.076039 | 0.058975
2021-12-03 15:30 | 0.31239 | 1.0686 | 0.33179 | 0.79761 | 0.016964 | 0.10403 | 0.057699 | 0.031198
2021-12-03 15:45 | 0.31444 | 1.0871 | 0.2491 | 0.81103 | 0.00178 | 0.040757 | 0.041141 | 0.010354
2021-12-03 16:00 | 0.37569 | 1.0875 | 0.27054 | 0.83028 | 0.001308 | 0.030658 | 0.030197 | 0.007587
2021-12-03 16:15 | 0.44511 | 1.1045 | 0.27156 | 0.83466 | 0.000835 | 0.016894 | 0.019253 | 0.004821
2021-12-03 16:30 | 0.64929 | 1.081 | 0.33485 | 1.2243 | 0.000363 | 0.008967 | 0.008309 | 0.002054
2021-12-03 16:45 | 0.70238 | 1.1515 | 0.28891 | 1.441 | 0 | 0 | 0 | 0
2021-12-03 17:00 | 0.68196 | 1.4167 | 0.26952 | 1.6638 | 0 | 0 | 0 | 0
2021-12-03 17:15 | 1.6232 | 1.4161 | 0.26952 | 1.5558 | 0 | 0 | 0 | 0
2021-12-03 17:30 | 1.4905 | 1.3024 | 0.32669 | 1.2837 | 0 | 0 | 0 | 0
2021-12-03 17:45 | 1.5109 | 1.2566 | 0.35527 | 1.1912 | 0 | 0 | 0 | 0
2021-12-03 18:00 | 1.6334 | 1.2809 | 0.35527 | 1.2261 | 0 | 0 | 0 | 0
2021-12-03 18:15 | 1.8274 | 1.2566 | 0.25625 | 1.1134 | 0 | 0 | 0 | 0
2021-12-03 18:30 | 0.99231 | 1.2693 | 0.26748 | 1.0149 | 0 | 0 | 0 | 0
2021-12-03 18:45 | 0.53087 | 1.1842 | 0.35017 | 1.0097 | 0 | 0 | 0 | 0
2021-12-03 19:00 | 0.5227 | 1.2094 | 0.41244 | 1.0585 | 0 | 0 | 0 | 0
2021-12-03 19:15 | 1.317 | 1.4877 | 0.30423 | 1.4748 | 0 | 0 | 0 | 0
2021-12-03 19:30 | 4.3685 | 1.8728 | 0.31954 | 1.7538 | 0 | 0 | 0 | 0
2021-12-03 19:45 | 3.5527 | 1.8958 | 0.31035 | 2.2141 | 0 | 0 | 0 | 0
2021-12-03 20:00 | 0.8698 | 1.2535 | 0.29912 | 1.4002 | 0 | 0 | 0 | 0
2021-12-03 20:15 | 0.89022 | 0.93292 | 0.44919 | 1.1835 | 0 | 0 | 0 | 0
2021-12-03 20:30 | 0.8208 | 0.85673 | 0.37671 | 0.8262 | 0 | 0 | 0 | 0
2021-12-03 20:45 | 0.67788 | 0.97062 | 0.29708 | 0.83786 | 0 | 0 | 0 | 0
2021-12-03 21:00 | 0.71054 | 0.95178 | 0.2736 | 0.96023 | 0 | 0 | 0 | 0
2021-12-03 21:15 | 0.49411 | 0.87845 | 0.27973 | 0.74307 | 0 | 0 | 0 | 0
2021-12-03 21:30 | 0.53087 | 0.83383 | 0.35017 | 0.73023 | 0 | 0 | 0 | 0
2021-12-03 21:45 | 0.5227 | 0.92418 | 0.46144 | 0.57024 | 0 | 0 | 0 | 0
2021-12-03 22:00 | 0.48186 | 0.95234 | 0.51045 | 0.88264 | 0 | 0 | 0 | 0
2021-12-03 22:15 | 0.46961 | 0.76031 | 0.39407 | 0.55945 | 0 | 0 | 0 | 0
2021-12-03 22:30 | 0.36446 | 0.60732 | 0.35221 | 0.49834 | 0 | 0 | 0 | 0
2021-12-03 22:45 | 0.342 | 0.62343 | 0.37977 | 0.47399 | 0 | 0 | 0 | 0
2021-12-03 23:00 | 3.2669 | 1.7702 | 3.2975 | 1.7956 | 0 | 0 | 0 | 0
2021-12-03 23:15 | 3.471 | 2.1248 | 3.5119 | 1.773 | 0 | 0 | 0 | 0
2021-12-03 23:30 | 3.5017 | 2.1563 | 3.4098 | 1.696 | 0 | 0 | 0 | 0
2021-12-03 23:45 | 3.4813 | 2.1191 | 3.3894 | 1.7142 | 0 | 0 | 0 | 0
2021-12-04 | 3.4506 | 1.9676 | 3.4404 | 1.7376 | 0 | 0 | 0 | 0
2021-12-04 00:15 | 3.4813 | 1.875 | 3.5323 | 1.7055 | 0 | 0 | 0 | 0
2021-12-04 00:30 | 3.5527 | 1.875 | 3.4302 | 1.6941 | 0 | 0 | 0 | 0
2021-12-04 00:45 | 3.5425 | 1.8532 | 3.4915 | 1.7012 | 0 | 0 | 0 | 0
2021-12-04 01:00 | 3.5017 | 1.8629 | 3.4098 | 1.7392 | 0 | 0 | 0 | 0
2021-12-04 01:15 | 3.4813 | 1.8629 | 3.4302 | 1.6851 | 0 | 0 | 0 | 0
2021-12-04 01:30 | 3.5936 | 1.8532 | 3.471 | 1.6975 | 0 | 0 | 0 | 0
2021-12-04 01:45 | 3.4915 | 1.8083 | 3.3894 | 1.6654 | 0 | 0 | 0 | 0
2021-12-04 02:00 | 3.5323 | 1.7276 | 3.3894 | 1.6705 | 0 | 0 | 0 | 0
2021-12-04 02:15 | 3.5221 | 1.7276 | 3.4813 | 1.6527 | 0 | 0 | 0 | 0
2021-12-04 02:30 | 3.6038 | 1.5901 | 3.5323 | 1.6951 | 0 | 0 | 0 | 0
2021-12-04 02:45 | 3.5221 | 1.6118 | 3.4302 | 1.7072 | 0 | 0 | 0 | 0
2021-12-04 03:00 | 3.4813 | 1.714 | 3.4098 | 1.694 | 0 | 0 | 0 | 0
2021-12-04 03:15 | 3.471 | 1.0444 | 3.4098 | 1.5 | 0 | 0 | 0 | 0
2021-12-04 03:30 | 3.471 | 0.98147 | 3.4098 | 1.3264 | 0 | 0 | 0 | 0
2021-12-04 03:45 | 3.5527 | 0.9675 | 3.4404 | 1.3248 | 0 | 0 | 0 | 0
2021-12-04 04:00 | 3.5221 | 1.0077 | 3.4098 | 1.268 | 0 | 0 | 0 | 0
2021-12-04 04:15 | 3.5221 | 0.79778 | 3.4302 | 1.2542 | 0 | 0 | 0 | 0
2021-12-04 04:30 | 2.2153 | 0.72694 | 3.3894 | 1.2246 | 0 | 0 | 0 | 0
2021-12-04 04:45 | 1.2761 | 0.79318 | 3.4813 | 1.2407 | 0 | 0 | 0 | 0
2021-12-04 05:00 | 0.91881 | 0.72694 | 3.471 | 1.2271 | 0 | 0 | 0 | 0
2021-12-04 05:15 | 0.8208 | 0.74824 | 3.42 | 1.2187 | 0 | 0 | 0 | 0
2021-12-04 05:30 | 0.38284 | 0.74243 | 3.42 | 1.2284 | 0 | 0 | 0 | 0
2021-12-04 05:45 | 0.37365 | 0.73213 | 3.4915 | 1.2232 | 0 | 0 | 0 | 0
2021-12-04 06:00 | 0.35323 | 0.73494 | 3.5119 | 1.2175 | 0 | 0 | 0 | 0
2021-12-04 06:15 | 0.33894 | 0.69902 | 3.3894 | 1.1851 | 0 | 0 | 0 | 0
2021-12-04 06:30 | 0.42061 | 0.8533 | 3.4098 | 1.0619 | 0 | 0 | 0 | 0
2021-12-04 06:45 | 0.42878 | 0.7719 | 3.3485 | 0.94141 | 0 | 0 | 0 | 0
2021-12-04 07:00 | 0.40019 | 0.57181 | 0.51045 | 0.35863 | 0 | 0 | 0 | 0
2021-12-04 07:15 | 0.38182 | 0.58967 | 0.38896 | 0.34696 | 0 | 1e-06 | 0 | 0
2021-12-04 07:30 | 0.57578 | 0.64269 | 0.48595 | 0.40646 | 0 | 1e-06 | 0 | 0
2021-12-04 07:45 | 0.55945 | 0.70696 | 0.35629 | 0.4085 | 0.000439 | 0.018674 | 0.000613 | 0.00861
2021-12-04 08:00 | 2.0214 | 1.1867 | 3.8896 | 1.5049 | 0.002369 | 0.074911 | 0.003212 | 0.040351
2021-12-04 08:15 | 1.3782 | 1.2272 | 4.1841 | 1.4031 | 0.004299 | 0.12319 | 0.005812 | 0.072093
2021-12-04 08:30 | 0.5717 | 0.98857 | 3.6548 | 1.0466 | 0.006228 | 0.15731 | 0.008412 | 0.10383
2021-12-04 08:45 | 0.7718 | 0.97269 | 3.5833 | 1.1831 | 0.009568 | 0.16363 | 0.014091 | 0.12516
2021-12-04 09:00 | 0.73504 | 1.2663 | 2.1337 | 1.1839 | 0.017705 | 0.17125 | 0.029777 | 0.11865
2021-12-04 09:15 | 0.55945 | 1.2172 | 0.57987 | 0.97831 | 0.025841 | 0.20576 | 0.045463 | 0.11214
2021-12-04 09:30 | 0.57987 | 1.1262 | 0.46144 | 1.2726 | 0.033978 | 0.22891 | 0.061149 | 0.10563
2021-12-04 09:45 | 0.66971 | 1.2036 | 0.64521 | 1.1659 | 0.040368 | 0.24757 | 0.07944 | 0.10603
2021-12-04 10:00 | 0.62479 | 1.0519 | 0.76363 | 1.0801 | 0.040801 | 0.22552 | 0.10621 | 0.12554
2021-12-04 10:15 | 0.55537 | 0.81825 | 0.55128 | 1.3444 | 0.041233 | 0.22436 | 0.13299 | 0.14506
2021-12-04 10:30 | 0.59212 | 0.87085 | 0.54312 | 1.2857 | 0.041665 | 0.2186 | 0.15976 | 0.16458
2021-12-04 10:45 | 0.51862 | 0.94284 | 0.55128 | 1.0355 | 0.04335 | 0.22056 | 0.17703 | 0.1726
2021-12-04 11:00 | 0.51453 | 1.22 | 0.38488 | 1.0208 | 0.049312 | 0.24387 | 0.16333 | 0.14968
2021-12-04 11:15 | 0.64929 | 1.3543 | 0.4737 | 1.7326 | 0.055274 | 0.2535 | 0.14963 | 0.12675
2021-12-04 11:30 | 0.78405 | 1.1663 | 0.59212 | 1.5033 | 0.061236 | 0.28184 | 0.13593 | 0.10383
2021-12-04 11:45 | 0.54312 | 1.1541 | 0.38998 | 1.3275 | 0.064423 | 0.29822 | 0.1246 | 0.090568
2021-12-04 12:00 | 0.45736 | 1.1893 | 0.26441 | 1.3326 | 0.058108 | 0.30879 | 0.121 | 0.10163
2021-12-04 12:15 | 0.47778 | 1.2046 | 0.23685 | 1.2335 | 0.051794 | 0.25136 | 0.1174 | 0.1127
2021-12-04 12:30 | 0.4982 | 1.1389 | 0.20826 | 1.3581 | 0.045479 | 0.24526 | 0.1138 | 0.12376
2021-12-04 12:45 | 0.41653 | 1.1896 | 0.29402 | 1.5375 | 0.04192 | 0.23406 | 0.10646 | 0.13131
2021-12-04 13:00 | 0.37365 | 1.4636 | 0.48595 | 1.9195 | 0.047815 | 0.23846 | 0.086891 | 0.12989
2021-12-04 13:15 | 2.9708 | 0.89295 | 0.44103 | 1.0362 | 0.053709 | 0.22542 | 0.06732 | 0.12848
2021-12-04 13:30 | 3.8896 | 0.90049 | 0.53903 | 0.96445 | 0.059604 | 0.19517 | 0.047749 | 0.12706
2021-12-04 13:45 | 3.4915 | 0.77725 | 0.58395 | 1.1982 | 0.066591 | 0.18948 | 0.035538 | 0.1262
2021-12-04 14:00 | 3.665 | 0.73115 | 0.53087 | 1.6366 | 0.077332 | 0.18524 | 0.047475 | 0.12715
2021-12-04 14:15 | 3.3077 | 0.82093 | 0.44919 | 1.8963 | 0.088074 | 0.18469 | 0.059411 | 0.12809
2021-12-04 14:30 | 1.368 | 0.70297 | 0.36854 | 1.5157 | 0.098816 | 0.19422 | 0.071348 | 0.12904
2021-12-04 14:45 | 0.77997 | 0.6522 | 0.35833 | 1.341 | 0.10361 | 0.17423 | 0.075917 | 0.12161
2021-12-04 15:00 | 0.66154 | 0.81848 | 0.41653 | 0.97787 | 0.087915 | 0.1328 | 0.056266 | 0.091907
2021-12-04 15:15 | 0.342 | 0.87352 | 0.53495 | 0.88191 | 0.072221 | 0.11946 | 0.036615 | 0.062201
2021-12-04 15:30 | 0.37569 | 0.78481 | 0.31239 | 0.79965 | 0.056528 | 0.10563 | 0.016964 | 0.032494
2021-12-04 15:45 | 0.31341 | 0.85696 | 0.31444 | 0.79936 | 0.041868 | 0.068821 | 0.00178 | 0.01014
2021-12-04 16:00 | 0.31954 | 0.90369 | 0.37569 | 0.84136 | 0.030779 | 0.051102 | 0.001308 | 0.007433
2021-12-04 16:15 | 0.44103 | 0.81228 | 0.44511 | 0.8453 | 0.01969 | 0.037664 | 0.000835 | 0.004725
2021-12-04 16:30 | 0.43286 | 0.89086 | 0.64929 | 1.2623 | 0.008601 | 0.016519 | 0.000363 | 0.002017
2021-12-04 16:45 | 0.3665 | 1.0755 | 0.70238 | 1.4967 | 0 | 0 | 0 | 0
2021-12-04 17:00 | 0.43286 | 1.0422 | 0.68196 | 1.6574 | 0 | 0 | 0 | 0
2021-12-04 17:15 | 0.39917 | 1.1131 | 1.6232 | 1.5427 | 0 | 0 | 0 | 0
2021-12-04 17:30 | 0.57578 | 1.0548 | 1.4905 | 1.2895 | 0 | 0 | 0 | 0
2021-12-04 17:45 | 0.45736 | 1.0688 | 1.5109 | 1.2 | 0 | 0 | 0 | 0
2021-12-04 18:00 | 0.53087 | 1.0042 | 1.6334 | 1.299 | 0 | 0 | 0 | 0
2021-12-04 18:15 | 0.55537 | 1.0403 | 1.8274 | 1.1878 | 0 | 0 | 0 | 0
2021-12-04 18:30 | 0.60029 | 1.0843 | 0.99231 | 1.0622 | 0 | 0 | 0 | 0
2021-12-04 18:45 | 0.50636 | 1.2507 | 0.53087 | 1.012 | 0 | 0 | 0 | 0
2021-12-04 19:00 | 0.51453 | 1.2847 | 0.5227 | 1.0544 | 0 | 0 | 0 | 0
2021-12-04 19:15 | 0.60845 | 1.2245 | 1.317 | 1.1685 | 0 | 0 | 0 | 0
2021-12-04 19:30 | 0.63704 | 1.2045 | 4.3685 | 1.7778 | 0 | 0 | 0 | 0
2021-12-04 19:45 | 0.70238 | 1.3655 | 3.5527 | 2.0521 | 0 | 0 | 0 | 0
2021-12-04 20:00 | 0.73096 | 1.0369 | 0.8698 | 1.4101 | 0 | 0 | 0 | 0
2021-12-04 20:15 | 0.84938 | 1.1726 | 0.89022 | 1.265 | 0 | 0 | 0 | 0
2021-12-04 20:30 | 1.0311 | 1.0494 | 0.8208 | 0.89445 | 0 | 0 | 0 | 0
2021-12-04 20:45 | 0.80855 | 0.87289 | 0.67788 | 0.8822 | 0 | 0 | 0 | 0
2021-12-04 21:00 | 1.0127 | 0.84525 | 0.71054 | 1.004 | 0 | 0 | 0 | 0
2021-12-04 21:15 | 0.60437 | 0.78645 | 0.49411 | 0.75532 | 0 | 0 | 0 | 0
2021-12-04 21:30 | 0.64929 | 0.75094 | 0.53087 | 0.74015 | 0 | 0 | 0 | 0
2021-12-04 21:45 | 0.55537 | 0.79904 | 0.5227 | 0.57724 | 0 | 0 | 0 | 0
2021-12-04 22:00 | 0.47778 | 0.778 | 0.48186 | 0.87972 | 0 | 0 | 0 | 0
2021-12-04 22:15 | 0.44103 | 0.77374 | 0.46961 | 0.56529 | 0 | 0 | 0 | 0
2021-12-04 22:30 | 0.4737 | 0.64112 | 0.36446 | 0.48566 | 0 | 0 | 0 | 0
2021-12-04 22:45 | 0.51045 | 0.65446 | 0.342 | 0.46772 | 0 | 0 | 0 | 0
2021-12-04 23:00 | 0.55128 | 0.94535 | 3.2669 | 1.7927 | 0 | 0 | 0 | 0
2021-12-04 23:15 | 0.6207 | 0.75611 | 3.471 | 1.7745 | 0 | 0 | 0 | 0
2021-12-04 23:30 | 0.75546 | 0.75611 | 3.5017 | 1.7033 | 0 | 0 | 0 | 0
2021-12-04 23:45 | 0.69013 | 0.77426 | 3.4813 | 1.6982 | 0 | 0 | 0 | 0
2021-12-05 | 0.64929 | 0.94677 | 3.4506 | 1.704 | 0 | 0 | 0 | 0
2021-12-05 00:15 | 0.72688 | 0.95726 | 3.4813 | 1.7113 | 0 | 0 | 0 | 0
2021-12-05 00:30 | 0.37671 | 0.92863 | 3.5527 | 1.6999 | 0 | 0 | 0 | 0
2021-12-05 00:45 | 0.3614 | 0.92863 | 3.5425 | 1.7056 | 0 | 0 | 0 | 0
2021-12-05 01:00 | 0.34098 | 0.94677 | 3.5017 | 1.7217 | 0 | 0 | 0 | 0
2021-12-05 01:15 | 0.31444 | 0.92863 | 3.4813 | 1.6749 | 0 | 0 | 0 | 0
2021-12-05 01:30 | 0.37263 | 0.92863 | 3.5936 | 1.7062 | 0 | 0 | 0 | 0
2021-12-05 01:45 | 0.44103 | 0.92863 | 3.4915 | 1.6581 | 0 | 0 | 0 | 0
2021-12-05 02:00 | 0.43694 | 0.91257 | 3.5323 | 1.6646 | 0 | 0 | 0 | 0
2021-12-05 02:15 | 0.43286 | 0.91257 | 3.5221 | 1.6527 | 0 | 0 | 0 | 0
2021-12-05 02:30 | 0.27564 | 0.91257 | 3.6038 | 1.7039 | 0 | 0 | 0 | 0
2021-12-05 02:45 | 0.29708 | 0.91257 | 3.5221 | 1.7072 | 0 | 0 | 0 | 0
2021-12-05 03:00 | 0.38488 | 0.91257 | 3.4813 | 1.6881 | 0 | 0 | 0 | 0
2021-12-05 03:15 | 0.37058 | 0.91257 | 3.471 | 1.6604 | 0 | 0 | 0 | 0
2021-12-05 03:30 | 0.33792 | 0.91257 | 3.471 | 1.6502 | 0 | 0 | 0 | 0
2021-12-05 03:45 | 0.3369 | 0.91257 | 3.5527 | 1.6865 | 0 | 0 | 0 | 0
2021-12-05 04:00 | 0.37671 | 0.91257 | 3.5221 | 1.6772 | 0 | 0 | 0 | 0
2021-12-05 04:15 | 0.30831 | 0.86086 | 3.5221 | 1.6938 | 0 | 0 | 0 | 0
2021-12-05 04:30 | 0.32056 | 0.98441 | 2.2153 | 1.4869 | 0 | 0 | 0 | 0
2021-12-05 04:45 | 0.37773 | 0.98441 | 1.2761 | 1.3629 | 0 | 0 | 0 | 0
2021-12-05 05:00 | 0.38284 | 1.0621 | 0.91881 | 1.3037 | 0 | 0 | 0 | 0
2021-12-05 05:15 | 0.33383 | 1.1063 | 0.8208 | 1.2776 | 0 | 0 | 0 | 0
2021-12-05 05:30 | 0.31137 | 0.99656 | 0.38284 | 1.2354 | 0 | 0 | 0 | 0
2021-12-05 05:45 | 0.35731 | 0.85823 | 0.37365 | 1.2227 | 0 | 0 | 0 | 0
2021-12-05 06:00 | 0.30729 | 0.85823 | 0.35323 | 1.2108 | 0 | 0 | 0 | 0
2021-12-05 06:15 | 0.32873 | 0.90571 | 0.33894 | 1.1882 | 0 | 0 | 0 | 0
2021-12-05 06:30 | 0.43286 | 0.90479 | 0.42061 | 1.0601 | 0 | 0 | 0 | 0
2021-12-05 06:45 | 0.33894 | 0.82873 | 0.42878 | 0.94374 | 0 | 0 | 0 | 0
2021-12-05 07:00 | 0.28993 | 0.60238 | 0.40019 | 0.36417 | 0 | 0 | 0 | 0
2021-12-05 07:15 | 0.31035 | 0.62024 | 0.38182 | 0.35585 | 0 | 0 | 0 | 0
2021-12-05 07:30 | 0.45736 | 0.6735 | 0.57578 | 0.4228 | 0 | 0 | 0 | 0
2021-12-05 07:45 | 0.32158 | 0.74531 | 0.55945 | 0.42951 | 0.011651 | 0.013218 | 0.000439 | 0.006425
2021-12-05 08:00 | 0.31648 | 1.3583 | 2.0214 | 1.6347 | 0.064801 | 0.045038 | 0.002369 | 0.030555
2021-12-05 08:15 | 0.32158 | 1.3922 | 1.3782 | 1.4424 | 0.11795 | 0.087456 | 0.004299 | 0.054686
2021-12-05 08:30 | 0.38182 | 1.1683 | 0.5717 | 1.0489 | 0.1711 | 0.11712 | 0.006228 | 0.078816
2021-12-05 08:45 | 1.6947 | 1.2864 | 0.7718 | 1.2052 | 0.20924 | 0.13922 | 0.009568 | 0.095844
2021-12-05 09:00 | 2.1847 | 1.2854 | 0.73504 | 1.1723 | 0.19378 | 0.1495 | 0.017705 | 0.093535
2021-12-05 09:15 | 1.1128 | 1.1743 | 0.55945 | 0.94273 | 0.17831 | 0.17113 | 0.025841 | 0.091227
2021-12-05 09:30 | 0.87797 | 1.4188 | 0.57987 | 1.2557 | 0.16285 | 0.16723 | 0.033978 | 0.088919
2021-12-05 09:45 | 0.82488 | 1.3102 | 0.66971 | 1.1589 | 0.15576 | 0.17177 | 0.040368 | 0.088397
2021-12-05 10:00 | 0.93106 | 1.3102 | 0.62479 | 1.0807 | 0.17861 | 0.18962 | 0.040801 | 0.093879
2021-12-05 10:15 | 0.93106 | 1.5594 | 0.55537 | 1.3374 | 0.20146 | 0.21726 | 0.041233 | 0.099361
2021-12-05 10:30 | 1.6028 | 1.4894 | 0.59212 | 1.2828 | 0.22431 | 0.2211 | 0.041665 | 0.10484
2021-12-05 10:45 | 3.1035 | 1.2954 | 0.51862 | 1.0314 | 0.23323 | 0.22308 | 0.04335 | 0.10799
2021-12-05 11:00 | 2.4297 | 1.2954 | 0.51453 | 0.99216 | 0.19227 | 0.20937 | 0.049312 | 0.10344
2021-12-05 11:15 | 0.48186 | 1.5572 | 0.64929 | 1.4155 | 0.1513 | 0.20944 | 0.055274 | 0.098891
2021-12-05 11:30 | 2.5012 | 1.524 | 0.78405 | 1.2945 | 0.11033 | 0.20147 | 0.061236 | 0.09434
2021-12-05 11:45 | 2.2256 | 1.2833 | 0.54312 | 0.97044 | 0.093287 | 0.19765 | 0.064423 | 0.090526
2021-12-05 12:00 | 0.44919 | 1.286 | 0.45736 | 0.95454 | 0.16213 | 0.21166 | 0.058108 | 0.08812
2021-12-05 12:15 | 2.6543 | 1.2407 | 0.47778 | 1.1049 | 0.23098 | 0.19663 | 0.051794 | 0.085714
2021-12-05 12:30 | 3.6956 | 1.4044 | 0.4982 | 1.2939 | 0.29982 | 0.19711 | 0.045479 | 0.083307
2021-12-05 12:45 | 3.614 | 1.3999 | 0.41653 | 1.3257 | 0.33747 | 0.19576 | 0.04192 | 0.080443
2021-12-05 13:00 | 3.665 | 1.5677 | 0.37365 | 1.3744 | 0.26286 | 0.20058 | 0.047815 | 0.07669
2021-12-05 13:15 | 5.2756 | 1.5315 | 2.9708 | 1.4048 | 0.18826 | 0.19227 | 0.053709 | 0.072937
2021-12-05 13:30 | 6.4549 | 1.5315 | 3.8896 | 1.4694 | 0.11366 | 0.20838 | 0.059604 | 0.069184
2021-12-05 13:45 | 3.8896 | 1.6879 | 3.4915 | 1.6565 | 0.06897 | 0.20034 | 0.066591 | 0.066093
2021-12-05 14:00 | 3.5119 | 1.9061 | 3.665 | 2.1173 | 0.1321 | 0.20189 | 0.077332 | 0.065203
2021-12-05 14:15 | 3.0831 | 1.8409 | 3.3077 | 2.3151 | 0.19524 | 0.198 | 0.088074 | 0.064312
2021-12-05 14:30 | 0.35017 | 1.7449 | 1.368 | 1.6528 | 0.25837 | 0.20389 | 0.098816 | 0.063422
2021-12-05 14:45 | 0.40632 | 1.5519 | 0.77997 | 1.4021 | 0.29966 | 0.19563 | 0.10361 | 0.05991
2021-12-05 15:00 | 0.30525 | 1.2409 | 0.66154 | 1.0226 | 0.26204 | 0.13583 | 0.087915 | 0.047944
2021-12-05 15:15 | 0.31137 | 1.2213 | 0.342 | 0.87374 | 0.22442 | 0.1038 | 0.072221 | 0.035977
2021-12-05 15:30 | 0.18989 | 1.1219 | 0.37569 | 0.80753 | 0.1868 | 0.081434 | 0.056528 | 0.024011
2021-12-05 15:45 | 0.27054 | 1.1199 | 0.31341 | 0.78769 | 0.14881 | 0.062918 | 0.041868 | 0.014062
2021-12-05 16:00 | 0.18274 | 1.1408 | 0.31954 | 0.81934 | 0.10948 | 0.046806 | 0.030779 | 0.010324
2021-12-05 16:15 | 0.1807 | 1.1849 | 0.44103 | 0.8488 | 0.070154 | 0.025079 | 0.01969 | 0.006586
2021-12-05 16:30 | 0.23787 | 1.2504 | 0.43286 | 1.2518 | 0.030827 | 0.012431 | 0.008601 | 0.002848
2021-12-05 16:45 | 0.26237 | 1.3355 | 0.3665 | 1.4598 | 0 | 0 | 0 | 0
2021-12-05 17:00 | 0.25829 | 1.2887 | 0.43286 | 1.6002 | 0 | 0 | 0 | 0
2021-12-05 17:15 | 0.24706 | 1.305 | 0.39917 | 1.5221 | 0 | 0 | 0 | 0
2021-12-05 17:30 | 0.2685 | 1.305 | 0.57578 | 1.296 | 0 | 0 | 0 | 0
2021-12-05 17:45 | 0.28381 | 1.1337 | 0.45736 | 1.1895 | 0 | 0 | 0 | 0
2021-12-05 18:00 | 0.28585 | 1.305 | 0.53087 | 1.2873 | 0 | 0 | 0 | 0
2021-12-05 18:15 | 0.29198 | 1.115 | 0.55537 | 1.1848 | 0 | 0 | 0 | 0
2021-12-05 18:30 | 0.40019 | 1.115 | 0.60029 | 1.0598 | 0 | 0 | 0 | 0
2021-12-05 18:45 | 0.30729 | 1.038 | 0.50636 | 0.99216 | 0 | 0 | 0 | 0
2021-12-05 19:00 | 1.7151 | 0.9553 | 0.51453 | 1.0288 | 0 | 0 | 0 | 0
2021-12-05 19:15 | 5.4548 | 0.99196 | 0.60845 | 1.1498 | 0 | 0 | 0 | 0
2021-12-05 19:30 | 5.4125 | 1.3487 | 0.63704 | 1.7573 | 0 | 0 | 0 | 0
2021-12-05 19:45 | 5.3336 | 1.6068 | 0.70238 | 2.0474 | 0 | 0 | 0 | 0
2021-12-05 20:00 | 2.1745 | 1.4458 | 0.73096 | 1.3944 | 0 | 0 | 0 | 0
2021-12-05 20:15 | 2.5318 | 1.2393 | 0.84938 | 1.2592 | 0 | 0 | 0 | 0
2021-12-05 20:30 | 2.1439 | 0.97444 | 1.0311 | 0.94141 | 0 | 0 | 0 | 0
2021-12-05 20:45 | 1.8989 | 0.95197 | 0.80855 | 0.92595 | 0 | 0 | 0 | 0
2021-12-05 21:00 | 0.67788 | 1.0545 | 1.0127 | 1.0839 | 0 | 0 | 0 | 0
2021-12-05 21:15 | 0.69421 | 0.8204 | 0.60437 | 0.76699 | 0 | 0 | 0 | 0
2021-12-05 21:30 | 0.91881 | 0.77091 | 0.64929 | 0.75532 | 0 | 0 | 0 | 0
2021-12-05 21:45 | 0.82488 | 0.83325 | 0.55537 | 0.58949 | 0 | 0 | 0 | 0
2021-12-05 22:00 | 0.65337 | 0.86175 | 0.47778 | 0.88555 | 0 | 0 | 0 | 0
2021-12-05 22:15 | 0.6207 | 0.74275 | 0.44103 | 0.57754 | 0 | 0 | 0 | 0
2021-12-05 22:30 | 0.51453 | 0.58476 | 0.4737 | 0.48449 | 0 | 0 | 0 | 0
2021-12-05 22:45 | 0.51453 | 0.58476 | 0.51045 | 0.49513 | 0 | 0 | 0 | 0
2021-12-05 23:00 | 3.3792 | 1.0569 | 0.55128 | 1.8203 | 0 | 0 | 0 | 0
2021-12-05 23:15 | 3.614 | 1.1403 | 0.6207 | 1.8131 | 0 | 0 | 0 | 0
2021-12-05 23:30 | 3.614 | 0.84162 | 0.75546 | 1.7753 | 0 | 0 | 0 | 0
2021-12-05 23:45 | 3.6344 | 0.77067 | 0.69013 | 1.7507 | 0 | 0 | 0 | 0
2021-12-06 | 3.6446 | 1.0284 | 0.64929 | 1.7538 | 0 | 0 | 0 | 0
2021-12-06 00:15 | 3.4915 | 1.0812 | 0.72688 | 1.7698 | 0 | 0 | 0 | 0
2021-12-06 00:30 | 3.5017 | 1.0248 | 0.37671 | 1.709 | 0 | 0 | 0 | 0
2021-12-06 00:45 | 3.5323 | 1.0248 | 0.3614 | 1.717 | 0 | 0 | 0 | 0
2021-12-06 01:00 | 3.5221 | 0.97197 | 0.34098 | 1.7155 | 0 | 0 | 0 | 0
2021-12-06 01:15 | 3.5731 | 1.0248 | 0.31444 | 1.6781 | 0 | 0 | 0 | 0
2021-12-06 01:30 | 3.5425 | 1.0248 | 0.37263 | 1.7148 | 0 | 0 | 0 | 0
2021-12-06 01:45 | 3.42 | 1.0248 | 0.44103 | 1.6808 | 0 | 0 | 0 | 0
2021-12-06 02:00 | 3.3894 | 0.9741 | 0.43694 | 1.6867 | 0 | 0 | 0 | 0
2021-12-06 02:15 | 3.4506 | 0.9481 | 0.43286 | 1.6749 | 0 | 0 | 0 | 0
2021-12-06 02:30 | 3.4608 | 1.0219 | 0.27564 | 1.6994 | 0 | 0 | 0 | 0
2021-12-06 02:45 | 3.5527 | 0.96908 | 0.29708 | 1.712 | 0 | 0 | 0 | 0
2021-12-06 03:00 | 3.471 | 1.0219 | 0.38488 | 1.6925 | 0 | 0 | 0 | 0
2021-12-06 03:15 | 3.4302 | 0.99588 | 0.37058 | 1.66 | 0 | 0 | 0 | 0
2021-12-06 03:30 | 3.4506 | 0.9481 | 0.33792 | 1.6591 | 0 | 0 | 0 | 0
2021-12-06 03:45 | 3.4506 | 0.96908 | 0.3369 | 1.6889 | 0 | 0 | 0 | 0
2021-12-06 04:00 | 3.5323 | 0.93333 | 0.37671 | 1.6897 | 0 | 0 | 0 | 0
2021-12-06 04:15 | 3.5731 | 0.98445 | 0.30831 | 1.6932 | 0 | 0 | 0 | 0
2021-12-06 04:30 | 3.471 | 0.78217 | 0.32056 | 1.4848 | 0 | 0 | 0 | 0
2021-12-06 04:45 | 3.4506 | 0.87153 | 0.37773 | 1.3746 | 0 | 0 | 0 | 0
2021-12-06 05:00 | 3.4506 | 0.87153 | 0.38284 | 1.3102 | 0 | 0 | 0 | 0
2021-12-06 05:15 | 3.6038 | 0.90616 | 0.33383 | 1.2841 | 0 | 0 | 0 | 0
2021-12-06 05:30 | 3.5119 | 0.70845 | 0.31137 | 1.2423 | 0 | 0 | 0 | 0
2021-12-06 05:45 | 3.4915 | 0.65963 | 0.35731 | 1.2251 | 0 | 0 | 0 | 0
2021-12-06 06:00 | 3.4915 | 0.70376 | 0.30729 | 1.2118 | 0 | 0 | 0 | 0
2021-12-06 06:15 | 3.5936 | 0.76257 | 0.32873 | 1.1891 | 0 | 0 | 0 | 0
2021-12-06 06:30 | 3.614 | 0.69097 | 0.43286 | 1.0709 | 0 | 0 | 0 | 0
2021-12-06 06:45 | 3.4813 | 0.78138 | 0.33894 | 0.94652 | 0 | 0 | 0 | 0
2021-12-06 07:00 | 0.5472 | 0.56468 | 0.28993 | 0.36869 | 0 | 0 | 0 | 0
2021-12-06 07:15 | 0.29606 | 0.56744 | 0.31035 | 0.35002 | 0 | 0 | 0 | 0
2021-12-06 07:30 | 0.40325 | 0.60487 | 0.45736 | 0.43913 | 0 | 0 | 0 | 0
2021-12-06 07:45 | 0.38386 | 0.6517 | 0.32158 | 0.43417 | 0.011396 | 0.013257 | 0.011651 | 0.007514
2021-12-06 08:00 | 3.2669 | 1.1383 | 0.31648 | 1.6286 | 0.065409 | 0.06275 | 0.064801 | 0.037157
2021-12-06 08:15 | 3.471 | 1.1896 | 0.32158 | 1.4385 | 0.11942 | 0.11505 | 0.11795 | 0.0668
2021-12-06 08:30 | 3.5629 | 1.0199 | 0.38182 | 1.0439 | 0.17343 | 0.14617 | 0.1711 | 0.096443
2021-12-06 08:45 | 3.5323 | 1.3514 | 1.6947 | 1.3773 | 0.20908 | 0.16448 | 0.20924 | 0.11622
2021-12-06 09:00 | 3.42 | 1.2058 | 2.1847 | 1.1431 | 0.17587 | 0.18125 | 0.19378 | 0.10741
2021-12-06 09:15 | 3.5833 | 1.1896 | 1.1128 | 0.85522 | 0.14267 | 0.21082 | 0.17831 | 0.098586
2021-12-06 09:30 | 4.4891 | 1.2857 | 0.87797 | 1.3053 | 0.10946 | 0.24407 | 0.16285 | 0.089768
2021-12-06 09:45 | 3.91 | 1.1473 | 0.82488 | 1.1874 | 0.089127 | 0.25887 | 0.15576 | 0.086596
2021-12-06 10:00 | 3.8896 | 1.1473 | 0.93106 | 1.1239 | 0.11712 | 0.26642 | 0.17861 | 0.1007
2021-12-06 10:15 | 3.91 | 1.1581 | 0.93106 | 1.0708 | 0.14511 | 0.26547 | 0.20146 | 0.11479
2021-12-06 10:30 | 3.9611 | 1.1829 | 1.6028 | 1.1662 | 0.17311 | 0.25213 | 0.22431 | 0.12889
2021-12-06 10:45 | 3.9407 | 1.3693 | 3.1035 | 1.3878 | 0.20826 | 0.25438 | 0.23323 | 0.13727
2021-12-06 11:00 | 3.7365 | 1.3608 | 2.4297 | 1.2558 | 0.27039 | 0.25473 | 0.19227 | 0.12713
2021-12-06 11:15 | 3.5017 | 1.3553 | 0.48186 | 1.3951 | 0.33252 | 0.27124 | 0.1513 | 0.11699
2021-12-06 11:30 | 3.5221 | 1.3842 | 2.5012 | 1.5824 | 0.39465 | 0.28191 | 0.11033 | 0.10686
2021-12-06 11:45 | 5.628 | 1.1399 | 2.2256 | 1.2044 | 0.43796 | 0.282 | 0.093287 | 0.10082
2021-12-06 12:00 | 4.1357 | 1.1283 | 0.44919 | 0.92829 | 0.41032 | 0.28221 | 0.16213 | 0.10831
2021-12-06 12:15 | 4.6305 | 1.4102 | 2.6543 | 1.3943 | 0.38267 | 0.26935 | 0.23098 | 0.1158
2021-12-06 12:30 | 4.7976 | 1.5329 | 3.6956 | 1.7606 | 0.35503 | 0.25271 | 0.29982 | 0.1233
2021-12-06 12:45 | 4.3833 | 1.4302 | 3.614 | 1.7743 | 0.34357 | 0.25097 | 0.33747 | 0.12587
2021-12-06 13:00 | 3.1648 | 1.2818 | 3.665 | 1.8274 | 0.39324 | 0.26461 | 0.26286 | 0.1115
2021-12-06 13:15 | 2.1847 | 1.3719 | 5.2756 | 2.1128 | 0.44292 | 0.25304 | 0.18826 | 0.097134
2021-12-06 13:30 | 0.80855 | 1.3936 | 6.4549 | 2.3534 | 0.49259 | 0.25004 | 0.11366 | 0.082767
2021-12-06 13:45 | 0.28993 | 1.446 | 3.8896 | 1.7921 | 0.52946 | 0.25626 | 0.06897 | 0.073372
2021-12-06 14:00 | 0.3665 | 1.7435 | 3.5119 | 1.8951 | 0.51781 | 0.24071 | 0.1321 | 0.081679
2021-12-06 14:15 | 0.35833 | 1.8292 | 3.0831 | 2.0132 | 0.50616 | 0.2429 | 0.19524 | 0.089986
2021-12-06 14:30 | 0.28585 | 1.2205 | 0.35017 | 0.94943 | 0.49451 | 0.25375 | 0.25837 | 0.098293
2021-12-06 14:45 | 0.23991 | 1.1846 | 0.40632 | 0.8682 | 0.46072 | 0.24348 | 0.29966 | 0.1008
2021-12-06 15:00 | 0.24093 | 1.267 | 0.30525 | 0.90437 | 0.34294 | 0.17841 | 0.26204 | 0.08341
2021-12-06 15:15 | 0.24297 | 1.2335 | 0.31137 | 0.88045 | 0.22516 | 0.12764 | 0.22442 | 0.066023
2021-12-06 15:30 | 0.24502 | 1.1069 | 0.18989 | 0.78886 | 0.10738 | 0.074949 | 0.1868 | 0.048637
2021-12-06 15:45 | 0.24399 | 1.1165 | 0.27054 | 0.79265 | 0.013394 | 0.068503 | 0.14881 | 0.033371
2021-12-06 16:00 | 0.30729 | 1.1234 | 0.18274 | 0.80519 | 0.009862 | 0.052174 | 0.10948 | 0.024538
2021-12-06 16:15 | 0.43694 | 1.1428 | 0.1807 | 0.82809 | 0.00633 | 0.030732 | 0.070154 | 0.015705
2021-12-06 16:30 | 0.33077 | 1.0039 | 0.23787 | 1.2416 | 0.002798 | 0.014161 | 0.030827 | 0.006871
2021-12-06 16:45 | 0.29402 | 1.2711 | 0.26237 | 1.4636 | 0 | 0 | 0 | 0
2021-12-06 17:00 | 0.2736 | 1.3099 | 0.25829 | 1.5934 | 0 | 0 | 0 | 0
2021-12-06 17:15 | 0.26645 | 1.3217 | 0.24706 | 1.5168 | 0 | 0 | 0 | 0
2021-12-06 17:30 | 1.3782 | 1.3206 | 0.2685 | 1.296 | 0 | 0 | 0 | 0
2021-12-06 17:45 | 5.3804 | 1.2195 | 0.28381 | 1.1851 | 0 | 0 | 0 | 0
2021-12-06 18:00 | 5.4377 | 1.2772 | 0.28585 | 1.2803 | 0 | 0 | 0 | 0
2021-12-06 18:15 | 6.4455 | 1.2088 | 0.29198 | 1.1773 | 0 | 0 | 0 | 0
2021-12-06 18:30 | 6.5602 | 1.2415 | 0.40019 | 1.0611 | 0 | 0 | 0 | 0
2021-12-06 18:45 | 3.8794 | 1.1564 | 0.30729 | 0.98356 | 0 | 0 | 0 | 0
2021-12-06 19:00 | 3.7875 | 1.1991 | 1.7151 | 1.2242 | 0 | 0 | 0 | 0
2021-12-06 19:15 | 3.8386 | 1.5896 | 5.4548 | 1.8731 | 0 | 0 | 0 | 0
2021-12-06 19:30 | 3.7161 | 1.817 | 5.4125 | 2.4448 | 0 | 0 | 0 | 0
2021-12-06 19:45 | 4.2613 | 1.7834 | 5.3336 | 2.6271 | 0 | 0 | 0 | 0
2021-12-06 20:00 | 3.7365 | 1.152 | 2.1745 | 1.4688 | 0 | 0 | 0 | 0
2021-12-06 20:15 | 1.4497 | 1.3491 | 2.5318 | 1.4021 | 0 | 0 | 0 | 0
2021-12-06 20:30 | 1.2659 | 1.1225 | 2.1439 | 1.1398 | 0 | 0 | 0 | 0
2021-12-06 20:45 | 1.8376 | 1.2314 | 1.8989 | 1.1173 | 0 | 0 | 0 | 0
2021-12-06 21:00 | 0.89022 | 1.2004 | 0.67788 | 1.1008 | 0 | 0 | 0 | 0
2021-12-06 21:15 | 0.51862 | 0.97646 | 0.69421 | 0.78915 | 0 | 0 | 0 | 0
2021-12-06 21:30 | 0.55128 | 0.95681 | 0.91881 | 0.82357 | 0 | 0 | 0 | 0
2021-12-06 21:45 | 0.59212 | 0.93088 | 0.82488 | 0.64375 | 0 | 0 | 0 | 0
2021-12-06 22:00 | 0.53495 | 0.88581 | 0.65337 | 0.91239 | 0 | 0 | 0 | 0
2021-12-06 22:15 | 0.56354 | 0.79736 | 0.6207 | 0.60029 | 0 | 0 | 0 | 0
2021-12-06 22:30 | 0.55945 | 0.66481 | 0.51453 | 0.49207 | 0 | 0 | 0 | 0
2021-12-06 22:45 | 0.342 | 0.66481 | 0.51453 | 0.50389 | 0 | 0 | 0 | 0
2021-12-06 23:00 | 3.2567 | 1.8537 | 3.3792 | 2.2388 | 0 | 0 | 0 | 0
2021-12-06 23:15 | 3.5017 | 1.8444 | 3.614 | 2.2713 | 0 | 0 | 0 | 0
2021-12-06 23:30 | 3.5017 | 1.8464 | 3.614 | 2.2496 | 0 | 0 | 0 | 0
2021-12-06 23:45 | 3.4813 | 1.8506 | 3.6344 | 2.225 | 0 | 0 | 0 | 0
2021-12-07 | 3.226 | 1.4199 | 3.6446 | 2.2339 | 0 | 0 | 0 | 0
2021-12-07 00:15 | 1.8478 | 1.4471 | 3.4915 | 2.2397 | 0 | 0 | 0 | 0
2021-12-07 00:30 | 1.0413 | 1.4199 | 3.5017 | 2.1697 | 0 | 0 | 0 | 0
2021-12-07 00:45 | 1.0086 | 1.4199 | 3.5323 | 2.1792 | 0 | 0 | 0 | 0
2021-12-07 01:00 | 0.64929 | 1.3815 | 3.5221 | 2.1631 | 0 | 0 | 0 | 0
2021-12-07 01:15 | 0.34608 | 1.3414 | 3.5731 | 2.1531 | 0 | 0 | 0 | 0
2021-12-07 01:30 | 0.43694 | 1.4199 | 3.5425 | 2.1713 | 0 | 0 | 0 | 0
2021-12-07 01:45 | 0.36752 | 1.2892 | 3.42 | 2.1277 | 0 | 0 | 0 | 0
2021-12-07 02:00 | 0.30014 | 1.2734 | 3.3894 | 2.1219 | 0 | 0 | 0 | 0
2021-12-07 02:15 | 0.31852 | 1.2734 | 3.4506 | 2.1309 | 0 | 0 | 0 | 0
2021-12-07 02:30 | 0.31137 | 1.0967 | 3.4608 | 2.1475 | 0 | 0 | 0 | 0
2021-12-07 02:45 | 0.44103 | 1.0967 | 3.5527 | 2.1688 | 0 | 0 | 0 | 0
2021-12-07 03:00 | 0.41244 | 1.1752 | 3.471 | 2.135 | 0 | 0 | 0 | 0
2021-12-07 03:15 | 0.32669 | 1.1752 | 3.4302 | 2.1102 | 0 | 0 | 0 | 0
2021-12-07 03:30 | 0.31035 | 1.1232 | 3.4506 | 2.1013 | 0 | 0 | 0 | 0
2021-12-07 03:45 | 0.33383 | 0.98165 | 3.4506 | 2.1413 | 0 | 0 | 0 | 0
2021-12-07 04:00 | 0.32465 | 1.02 | 3.5323 | 2.1468 | 0 | 0 | 0 | 0
2021-12-07 04:15 | 0.34506 | 0.94042 | 3.5731 | 2.1554 | 0 | 0 | 0 | 0
2021-12-07 04:30 | 0.44511 | 0.80604 | 3.471 | 1.9359 | 0 | 0 | 0 | 0
2021-12-07 04:45 | 0.31852 | 0.85209 | 3.4506 | 1.8248 | 0 | 0 | 0 | 0
2021-12-07 05:00 | 0.32158 | 0.83901 | 3.4506 | 1.7647 | 0 | 0 | 0 | 0
2021-12-07 05:15 | 0.30627 | 0.80064 | 3.6038 | 1.7606 | 0 | 0 | 0 | 0
2021-12-07 05:30 | 0.39407 | 0.8202 | 3.5119 | 1.7043 | 0 | 0 | 0 | 0
2021-12-07 05:45 | 0.40019 | 0.83901 | 3.4915 | 1.6875 | 0 | 0 | 0 | 0
2021-12-07 06:00 | 0.32975 | 0.79296 | 3.4915 | 1.6741 | 0 | 0 | 0 | 0
2021-12-07 06:15 | 0.3614 | 0.76987 | 3.5936 | 1.6661 | 0 | 0 | 0 | 0
2021-12-07 06:30 | 0.32158 | 1.0263 | 3.614 | 1.5439 | 0 | 0 | 0 | 0
2021-12-07 06:45 | 0.32056 | 0.77078 | 3.4813 | 1.4001 | 0 | 0 | 0 | 0
2021-12-07 07:00 | 0.45328 | 0.7572 | 0.5472 | 0.40763 | 0 | 0 | 0 | 0
2021-12-07 07:15 | 0.43694 | 0.77036 | 0.29606 | 0.356 | 0 | 0 | 0 | 0
2021-12-07 07:30 | 0.35119 | 0.71984 | 0.40325 | 0.45284 | 0 | 0 | 0 | 0
2021-12-07 07:45 | 0.38794 | 0.72049 | 0.38386 | 0.45094 | 0.021105 | 0.015049 | 0.011396 | 0.004017
2021-12-07 08:00 | 1.6334 | 0.71161 | 3.2669 | 2.0529 | 0.12519 | 0.076028 | 0.065409 | 0.022293
2021-12-07 08:15 | 0.64929 | 0.95241 | 3.471 | 1.8935 | 0.22928 | 0.16089 | 0.11942 | 0.040568
2021-12-07 08:30 | 0.66154 | 0.99136 | 3.5629 | 1.4847 | 0.33337 | 0.21318 | 0.17343 | 0.058844
2021-12-07 08:45 | 0.61662 | 1.0308 | 3.5323 | 1.6457 | 0.39975 | 0.26099 | 0.20908 | 0.072193
2021-12-07 09:00 | 0.6207 | 0.95024 | 3.42 | 1.5144 | 0.31755 | 0.27315 | 0.17587 | 0.067736
2021-12-07 09:15 | 0.64112 | 0.95024 | 3.5833 | 1.282 | 0.23534 | 0.27884 | 0.14267 | 0.06328
2021-12-07 09:30 | 1.562 | 0.91422 | 4.4891 | 1.8264 | 0.15314 | 0.3045 | 0.10946 | 0.058824
2021-12-07 09:45 | 2.0418 | 0.92442 | 3.91 | 1.6305 | 0.090486 | 0.29849 | 0.089127 | 0.060722
2021-12-07 10:00 | 0.69421 | 0.92442 | 3.8896 | 1.5646 | 0.10501 | 0.30838 | 0.11712 | 0.083701
2021-12-07 10:15 | 0.74321 | 0.946 | 3.91 | 1.522 | 0.11954 | 0.28882 | 0.14511 | 0.10668
2021-12-07 10:30 | 0.97189 | 0.946 | 3.9611 | 1.6159 | 0.13407 | 0.29261 | 0.17311 | 0.12966
2021-12-07 10:45 | 0.66154 | 0.9258 | 3.9407 | 1.8207 | 0.14147 | 0.29814 | 0.20826 | 0.14733
2021-12-07 11:00 | 0.4982 | 1.0526 | 3.7365 | 1.7021 | 0.12063 | 0.29532 | 0.27039 | 0.1487
2021-12-07 11:15 | 0.55945 | 0.82029 | 3.5017 | 1.6183 | 0.099801 | 0.30771 | 0.33252 | 0.15007
2021-12-07 11:30 | 0.51862 | 0.837 | 3.5221 | 1.9718 | 0.078968 | 0.29269 | 0.39465 | 0.15143
2021-12-07 11:45 | 0.64112 | 0.88214 | 5.628 | 1.9191 | 0.061006 | 0.27739 | 0.43796 | 0.15325
2021-12-07 12:00 | 0.55537 | 0.91218 | 4.1357 | 1.4123 | 0.054435 | 0.30799 | 0.41032 | 0.15584
2021-12-07 12:15 | 0.49411 | 1.0706 | 4.6305 | 1.8895 | 0.047863 | 0.30809 | 0.38267 | 0.15842
2021-12-07 12:30 | 0.44919 | 1.0199 | 4.7976 | 2.1732 | 0.041291 | 0.29587 | 0.35503 | 0.161
2021-12-07 12:45 | 0.4982 | 1.1137 | 4.3833 | 2.1905 | 0.036696 | 0.29383 | 0.34357 | 0.16138
2021-12-07 13:00 | 0.46961 | 1.2071 | 3.1648 | 2.2171 | 0.039961 | 0.2872 | 0.39324 | 0.15467
2021-12-07 13:15 | 0.38896 | 1.0117 | 2.1847 | 2.359 | 0.043226 | 0.2884 | 0.44292 | 0.14796
2021-12-07 13:30 | 0.27973 | 0.81947 | 0.80855 | 2.2793 | 0.046491 | 0.28476 | 0.49259 | 0.14124
2021-12-07 13:45 | 0.65337 | 0.83306 | 0.28993 | 1.7939 | 0.062454 | 0.23954 | 0.52946 | 0.13751
2021-12-07 14:00 | 0.48186 | 0.78982 | 0.3665 | 1.7753 | 0.12899 | 0.27856 | 0.51781 | 0.14412
2021-12-07 14:15 | 0.45328 | 0.91743 | 0.35833 | 1.6385 | 0.19553 | 0.274 | 0.50616 | 0.15072
2021-12-07 14:30 | 0.39611 | 0.96592 | 0.28585 | 0.92435 | 0.26206 | 0.26358 | 0.49451 | 0.15733
2021-12-07 14:45 | 0.38998 | 0.95451 | 0.23991 | 0.85318 | 0.30259 | 0.25291 | 0.46072 | 0.15575
2021-12-07 15:00 | 0.37773 | 0.9553 | 0.24093 | 0.88964 | 0.23932 | 0.1995 | 0.34294 | 0.12445
2021-12-07 15:15 | 0.35425 | 0.96412 | 0.24297 | 0.88074 | 0.17605 | 0.16346 | 0.22516 | 0.093144
2021-12-07 15:30 | 0.46961 | 0.92449 | 0.24502 | 0.78536 | 0.11278 | 0.11806 | 0.10738 | 0.061841
2021-12-07 15:45 | 0.43694 | 0.93305 | 0.24399 | 0.78011 | 0.059061 | 0.076979 | 0.013394 | 0.035284
2021-12-07 16:00 | 0.37263 | 0.93986 | 0.30729 | 0.81059 | 0.04352 | 0.056339 | 0.009862 | 0.025947
2021-12-07 16:15 | 0.35527 | 0.91084 | 0.43694 | 0.85303 | 0.027979 | 0.033877 | 0.00633 | 0.016609
2021-12-07 16:30 | 0.44103 | 0.92051 | 0.33077 | 0.87316 | 0.012438 | 0.015077 | 0.002798 | 0.007271
2021-12-07 16:45 | 0.5962 | 1.0877 | 0.29402 | 0.85682 | 0 | 0 | 0 | 0
2021-12-07 17:00 | 0.67788 | 1.0178 | 0.2736 | 0.83845 | 0 | 0 | 0 | 0
2021-12-07 17:15 | 0.60029 | 1.1176 | 0.26645 | 0.75546 | 0 | 0 | 0 | 0
2021-12-07 17:30 | 0.43286 | 1.1139 | 1.3782 | 0.89562 | 0 | 0 | 0 | 0
2021-12-07 17:45 | 0.55537 | 1.0044 | 5.3804 | 1.3748 | 0 | 0 | 0 | 0
2021-12-07 18:00 | 0.61254 | 1.0591 | 5.4377 | 1.4264 | 0 | 0 | 0 | 0
2021-12-07 18:15 | 0.63296 | 1.0379 | 6.4455 | 1.5087 | 0 | 0 | 0 | 0
2021-12-07 18:30 | 0.7473 | 1.0852 | 6.5602 | 1.431 | 0 | 0 | 0 | 0
2021-12-07 18:45 | 3.3077 | 1.0209 | 3.8794 | 0.97481 | 0 | 0 | 0 | 0
2021-12-07 19:00 | 3.8794 | 1.1275 | 3.7875 | 1.1921 | 0 | 0 | 0 | 0
2021-12-07 19:15 | 3.9202 | 1.1218 | 3.8386 | 1.8585 | 0 | 0 | 0 | 0
2021-12-07 19:30 | 3.8386 | 0.9925 | 3.7161 | 2.3918 | 0 | 0 | 0 | 0
2021-12-07 19:45 | 2.4195 | 1.2723 | 4.2613 | 2.4386 | 0 | 0 | 0 | 0
2021-12-07 20:00 | 1.858 | 1.2116 | 3.7365 | 1.603 | 0 | 0 | 0 | 0
2021-12-07 20:15 | 1.368 | 1.2947 | 1.4497 | 1.268 | 0 | 0 | 0 | 0
2021-12-07 20:30 | 0.72688 | 0.88485 | 1.2659 | 1.0143 | 0 | 0 | 0 | 0
2021-12-07 20:45 | 0.42061 | 1.0395 | 1.8376 | 1.075 | 0 | 0 | 0 | 0
2021-12-07 21:00 | 3.1239 | 1.0041 | 0.89022 | 0.95381 | 0 | 0 | 0 | 0
2021-12-07 21:15 | 1.0617 | 1.0201 | 0.51862 | 0.75532 | 0 | 0 | 0 | 0
2021-12-07 21:30 | 0.91472 | 0.92457 | 0.55128 | 0.79965 | 0 | 0 | 0 | 0
2021-12-07 21:45 | 0.56354 | 0.96471 | 0.59212 | 0.63733 | 0 | 0 | 0 | 0
2021-12-07 22:00 | 0.53903 | 0.9237 | 0.53495 | 0.90422 | 0 | 0 | 0 | 0
2021-12-07 22:15 | 0.5717 | 0.96815 | 0.56354 | 0.59504 | 0 | 0 | 0 | 0
2021-12-07 22:30 | 0.5962 | 0.72724 | 0.55945 | 0.47282 | 0 | 0 | 0 | 0
2021-12-07 22:45 | 0.62887 | 0.74571 | 0.342 | 0.44132 | 0 | 0 | 0 | 0
2021-12-07 23:00 | 1.2353 | 0.87061 | 3.2567 | 2.2228 | 0 | 0 | 0 | 0
2021-12-07 23:15 | 0.76771 | 0.86764 | 3.5017 | 2.2611 | 0 | 0 | 0 | 0
2021-12-07 23:30 | 0.59212 | 0.86688 | 3.5017 | 2.2307 | 0 | 0 | 0 | 0
2021-12-07 23:45 | 0.37467 | 0.92595 | 3.4813 | 2.2046 | 0 | 0 | 0 | 0
2021-12-08 | 0.29606 | 1.1647 | 3.226 | 2.1712 | 0 | 0 | 0 | 0
2021-12-08 00:15 | 0.30627 | 1.0987 | 1.8478 | 1.9845 | 0 | 0 | 0 | 0
2021-12-08 00:30 | 0.31954 | 1.0987 | 1.0413 | 1.8036 | 0 | 0 | 0 | 0
2021-12-08 00:45 | 0.33996 | 1.0987 | 1.0086 | 1.807 | 0 | 0 | 0 | 0
2021-12-08 01:00 | 0.32771 | 1.1176 | 0.64929 | 1.7396 | 0 | 0 | 0 | 0
2021-12-08 01:15 | 0.28585 | 1.1112 | 0.34608 | 1.6833 | 0 | 0 | 0 | 0
2021-12-08 01:30 | 0.24093 | 1.1112 | 0.43694 | 1.7233 | 0 | 0 | 0 | 0
2021-12-08 01:45 | 0.26748 | 1.1112 | 0.36752 | 1.6756 | 0 | 0 | 0 | 0
2021-12-08 02:00 | 0.25625 | 1.0772 | 0.30014 | 1.6718 | 0 | 0 | 0 | 0
2021-12-08 02:15 | 0.38386 | 1.0772 | 0.31852 | 1.6835 | 0 | 0 | 0 | 0
2021-12-08 02:30 | 0.41653 | 1.0772 | 0.31137 | 1.6918 | 0 | 0 | 0 | 0
2021-12-08 02:45 | 0.30933 | 1.086 | 0.44103 | 1.7199 | 0 | 0 | 0 | 0
2021-12-08 03:00 | 0.26748 | 1.0772 | 0.41244 | 1.6835 | 0 | 0 | 0 | 0
2021-12-08 03:15 | 0.26543 | 1.0772 | 0.32669 | 1.6552 | 0 | 0 | 0 | 0
2021-12-08 03:30 | 0.28177 | 1.0772 | 0.31035 | 1.6527 | 0 | 0 | 0 | 0
2021-12-08 03:45 | 0.30218 | 1.0772 | 0.33383 | 1.6887 | 0 | 0 | 0 | 0
2021-12-08 04:00 | 0.2736 | 1.0772 | 0.32465 | 1.6959 | 0 | 0 | 0 | 0
2021-12-08 04:15 | 0.34915 | 1.0625 | 0.34506 | 1.6943 | 0 | 0 | 0 | 0
2021-12-08 04:30 | 0.29198 | 1.0802 | 0.44511 | 1.5022 | 0 | 0 | 0 | 0
2021-12-08 04:45 | 0.27666 | 1.0802 | 0.31852 | 1.3657 | 0 | 0 | 0 | 0
2021-12-08 05:00 | 0.2736 | 1.0802 | 0.32158 | 1.3089 | 0 | 0 | 0 | 0
2021-12-08 05:15 | 0.31648 | 1.0914 | 0.30627 | 1.3027 | 0 | 0 | 0 | 0
2021-12-08 05:30 | 0.34302 | 1.1584 | 0.39407 | 1.2647 | 0 | 0 | 0 | 0
2021-12-08 05:45 | 0.25931 | 1.1203 | 0.40019 | 1.2488 | 0 | 0 | 0 | 0
2021-12-08 06:00 | 0.24093 | 1.0001 | 0.32975 | 1.2239 | 0 | 0 | 0 | 0
2021-12-08 06:15 | 0.28483 | 1.0188 | 0.3614 | 1.2277 | 0 | 0 | 0 | 0
2021-12-08 06:30 | 0.42061 | 1.1842 | 0.32158 | 1.2792 | 0 | 0 | 0 | 0
2021-12-08 06:45 | 0.30627 | 1.0188 | 0.32056 | 1.2125 | 0 | 0 | 0 | 0
2021-12-08 07:00 | 0.27054 | 0.62521 | 0.45328 | 0.41171 | 0 | 0 | 0 | 0
2021-12-08 07:15 | 0.27462 | 0.59879 | 0.43694 | 0.35775 | 0 | 0 | 0 | 0
2021-12-08 07:30 | 0.36038 | 0.65923 | 0.35119 | 0.44496 | 0 | 0 | 0 | 0
2021-12-08 07:45 | 0.77997 | 0.70499 | 0.38794 | 0.43519 | 0.000913 | 0.01722 | 0.021105 | 0.006986
2021-12-08 08:00 | 1.368 | 1.433 | 1.6334 | 1.8954 | 0.005605 | 0.077314 | 0.12519 | 0.039954
2021-12-08 08:15 | 0.60437 | 1.4455 | 0.64929 | 1.769 | 0.010297 | 0.15772 | 0.22928 | 0.072921
2021-12-08 08:30 | 0.71871 | 1.3739 | 0.66154 | 1.4584 | 0.014989 | 0.2103 | 0.33337 | 0.10589
2021-12-08 08:45 | 0.83713 | 1.3357 | 0.61662 | 1.6113 | 0.020873 | 0.25174 | 0.39975 | 0.12859
2021-12-08 09:00 | 0.69829 | 1.3483 | 0.6207 | 1.522 | 0.031699 | 0.25416 | 0.31755 | 0.11237
2021-12-08 09:15 | 0.4982 | 1.353 | 0.64112 | 1.3006 | 0.042526 | 0.26676 | 0.23534 | 0.096163
2021-12-08 09:30 | 0.41244 | 1.9209 | 1.562 | 1.9743 | 0.053352 | 0.27936 | 0.15314 | 0.079951
2021-12-08 09:45 | 0.44511 | 1.8402 | 2.0418 | 1.8487 | 0.065305 | 0.26948 | 0.090486 | 0.071507
2021-12-08 10:00 | 0.48595 | 1.5331 | 0.69421 | 1.5897 | 0.081941 | 0.28491 | 0.10501 | 0.091237
2021-12-08 10:15 | 0.53495 | 1.6328 | 0.74321 | 1.5605 | 0.098577 | 0.28955 | 0.11954 | 0.11097
2021-12-08 10:30 | 0.62887 | 1.6618 | 0.97189 | 1.6836 | 0.11521 | 0.29431 | 0.13407 | 0.1307
2021-12-08 10:45 | 0.49003 | 1.9071 | 0.66154 | 1.8382 | 0.13094 | 0.29786 | 0.14147 | 0.14648
2021-12-08 11:00 | 0.53087 | 1.8613 | 0.4982 | 1.6776 | 0.14287 | 0.31442 | 0.12063 | 0.14872
2021-12-08 11:15 | 2.5216 | 1.6162 | 0.55945 | 1.6188 | 0.1548 | 0.31561 | 0.099801 | 0.15097
2021-12-08 11:30 | 1.562 | 1.56 | 0.51862 | 1.9625 | 0.16673 | 0.31433 | 0.078968 | 0.15321
2021-12-08 11:45 | 0.62479 | 1.789 | 0.64112 | 1.9261 | 0.18194 | 0.29699 | 0.061006 | 0.15471
2021-12-08 12:00 | 0.73913 | 1.7705 | 0.55537 | 1.4048 | 0.21084 | 0.30777 | 0.054435 | 0.15399
2021-12-08 12:15 | 0.62887 | 1.8584 | 0.49411 | 1.7909 | 0.23973 | 0.29103 | 0.047863 | 0.15327
2021-12-08 12:30 | 0.54312 | 1.758 | 0.44919 | 1.9457 | 0.26863 | 0.28991 | 0.041291 | 0.15255
2021-12-08 12:45 | 1.6743 | 1.8274 | 0.4982 | 1.9773 | 0.28885 | 0.2838 | 0.036696 | 0.15148
2021-12-08 13:00 | 3.0831 | 1.7029 | 0.46961 | 2.0975 | 0.27277 | 0.27861 | 0.039961 | 0.14893
2021-12-08 13:15 | 0.54312 | 1.4314 | 0.38896 | 2.2337 | 0.2567 | 0.2692 | 0.043226 | 0.14638
2021-12-08 13:30 | 0.49003 | 1.3707 | 0.27973 | 2.2569 | 0.24062 | 0.26409 | 0.046491 | 0.14383
2021-12-08 13:45 | 0.48186 | 1.3095 | 0.65337 | 1.8259 | 0.22272 | 0.27324 | 0.062454 | 0.14515
2021-12-08 14:00 | 0.82488 | 1.3913 | 0.48186 | 1.78 | 0.19717 | 0.28715 | 0.12899 | 0.16138
2021-12-08 14:15 | 0.40325 | 1.4501 | 0.45328 | 1.6251 | 0.17162 | 0.25784 | 0.19553 | 0.17761
2021-12-08 14:30 | 0.43286 | 1.2082 | 0.39611 | 0.91793 | 0.14606 | 0.26289 | 0.26206 | 0.19384
2021-12-08 14:45 | 0.44103 | 1.2082 | 0.38998 | 0.84764 | 0.12081 | 0.2513 | 0.30259 | 0.19819
2021-12-08 15:00 | 0.44103 | 1.2086 | 0.37773 | 0.87885 | 0.096793 | 0.19152 | 0.23932 | 0.15806
2021-12-08 15:15 | 0.35731 | 1.1899 | 0.35425 | 0.86076 | 0.07278 | 0.15777 | 0.17605 | 0.11793
2021-12-08 15:30 | 0.40427 | 1.2725 | 0.46961 | 0.79119 | 0.048767 | 0.10632 | 0.11278 | 0.077797
2021-12-08 15:45 | 0.44103 | 1.2842 | 0.43694 | 0.77311 | 0.027952 | 0.05937 | 0.059061 | 0.043722
2021-12-08 16:00 | 0.48186 | 1.2818 | 0.37263 | 0.7804 | 0.020613 | 0.042715 | 0.04352 | 0.032164
2021-12-08 16:15 | 0.68604 | 1.2612 | 0.35527 | 0.83086 | 0.013274 | 0.02824 | 0.027979 | 0.020606
2021-12-08 16:30 | 0.33792 | 1.2325 | 0.44103 | 0.87316 | 0.005934 | 0.014143 | 0.012438 | 0.009048
2021-12-08 16:45 | 0.34915 | 1.2442 | 0.5962 | 0.87491 | 0 | 0 | 0 | 0
2021-12-08 17:00 | 0.44103 | 1.2442 | 0.67788 | 0.85186 | 0 | 0 | 0 | 0
2021-12-08 17:15 | 0.53903 | 0.94008 | 0.60029 | 0.77238 | 0 | 0 | 0 | 0
2021-12-08 17:30 | 0.55537 | 1.0607 | 0.43286 | 0.86937 | 0 | 0 | 0 | 0
2021-12-08 17:45 | 0.51453 | 1.4825 | 0.55537 | 1.3823 | 0 | 0 | 0 | 0
2021-12-08 18:00 | 0.47778 | 1.4895 | 0.61254 | 1.4416 | 0 | 0 | 0 | 0
2021-12-08 18:15 | 0.60437 | 1.4233 | 0.63296 | 1.5227 | 0 | 0 | 0 | 0
2021-12-08 18:30 | 0.68196 | 1.5217 | 0.7473 | 1.4543 | 0 | 0 | 0 | 0
2021-12-08 18:45 | 0.66154 | 1.3306 | 3.3077 | 1.3517 | 0 | 0 | 0 | 0
2021-12-08 19:00 | 3.1444 | 1.5319 | 3.8794 | 1.653 | 0 | 0 | 0 | 0
2021-12-08 19:15 | 4.231 | 1.6804 | 3.9202 | 2.3508 | 0 | 0 | 0 | 0
2021-12-08 19:30 | 3.7263 | 1.6832 | 3.8386 | 2.8771 | 0 | 0 | 0 | 0
2021-12-08 19:45 | 3.7569 | 1.8542 | 2.4195 | 2.6121 | 0 | 0 | 0 | 0
2021-12-08 20:00 | 0.95964 | 1.2743 | 1.858 | 1.6467 | 0 | 0 | 0 | 0
2021-12-08 20:15 | 0.69013 | 1.1616 | 1.368 | 1.233 | 0 | 0 | 0 | 0
2021-12-08 20:30 | 1.2455 | 0.98409 | 0.72688 | 1.0313 | 0 | 0 | 0 | 0
2021-12-08 20:45 | 1.368 | 1.1673 | 0.42061 | 1.0441 | 0 | 0 | 0 | 0
2021-12-08 21:00 | 0.65746 | 1.0325 | 3.1239 | 1.0296 | 0 | 0 | 0 | 0
2021-12-08 21:15 | 0.47778 | 0.90766 | 1.0617 | 0.57447 | 0 | 0 | 0 | 0
2021-12-08 21:30 | 0.51862 | 0.84682 | 0.91472 | 0.62114 | 0 | 0 | 0 | 0
2021-12-08 21:45 | 0.41244 | 0.87348 | 0.56354 | 0.5647 | 0 | 0 | 0 | 0
2021-12-08 22:00 | 0.41244 | 0.73578 | 0.53903 | 0.52912 | 0 | 0 | 0 | 0
2021-12-08 22:15 | 0.41244 | 0.6347 | 0.5717 | 0.52357 | 0 | 0 | 0 | 0
2021-12-08 22:30 | 0.38284 | 0.60204 | 0.5962 | 0.49207 | 0 | 0 | 0 | 0
2021-12-08 22:45 | 0.34098 | 0.60204 | 0.62887 | 0.46115 | 0 | 0 | 0 | 0
2021-12-08 23:00 | 3.2464 | 1.5754 | 1.2353 | 2.3466 | 0 | 0 | 0 | 0
2021-12-08 23:15 | 3.4915 | 1.4278 | 0.76771 | 2.3209 | 0 | 0 | 0 | 0
2021-12-08 23:30 | 3.614 | 1.1441 | 0.59212 | 2.2629 | 0 | 0 | 0 | 0
2021-12-08 23:45 | 3.5936 | 1.226 | 0.37467 | 2.1962 | 0 | 0 | 0 | 0
2021-12-09 | 3.5119 | 1.3001 | 0.29606 | 2.1481 | 0 | 0 | 0 | 0
2021-12-09 00:15 | 3.4915 | 1.098 | 0.30627 | 1.9747 | 0 | 0 | 0 | 0
2021-12-09 00:30 | 3.5221 | 1.3229 | 0.31954 | 1.7977 | 0 | 0 | 0 | 0
2021-12-09 00:45 | 3.5221 | 1.3229 | 0.33996 | 1.803 | 0 | 0 | 0 | 0
2021-12-09 01:00 | 3.5221 | 1.1344 | 0.32771 | 1.7211 | 0 | 0 | 0 | 0
2021-12-09 01:15 | 3.5017 | 1.1047 | 0.28585 | 1.674 | 0 | 0 | 0 | 0
2021-12-09 01:30 | 3.5017 | 1.1017 | 0.24093 | 1.7125 | 0 | 0 | 0 | 0
2021-12-09 01:45 | 3.42 | 1.1017 | 0.26748 | 1.6671 | 0 | 0 | 0 | 0
2021-12-09 02:00 | 3.4506 | 1.0092 | 0.25625 | 1.6531 | 0 | 0 | 0 | 0
2021-12-09 02:15 | 3.4608 | 0.9684 | 0.38386 | 1.6964 | 0 | 0 | 0 | 0
2021-12-09 02:30 | 3.5833 | 0.9944 | 0.41653 | 1.7065 | 0 | 0 | 0 | 0
2021-12-09 02:45 | 3.5527 | 1.0983 | 0.30933 | 1.7078 | 0 | 0 | 0 | 0
2021-12-09 03:00 | 3.4608 | 1.0798 | 0.26748 | 1.6747 | 0 | 0 | 0 | 0
2021-12-09 03:15 | 3.4813 | 1.0471 | 0.26543 | 1.6477 | 0 | 0 | 0 | 0
2021-12-09 03:30 | 3.471 | 0.98316 | 0.28177 | 1.6448 | 0 | 0 | 0 | 0
2021-12-09 03:45 | 3.5119 | 1.0731 | 0.30218 | 1.6759 | 0 | 0 | 0 | 0
2021-12-09 04:00 | 2.736 | 0.99646 | 0.2736 | 1.6903 | 0 | 0 | 0 | 0
2021-12-09 04:15 | 1.5313 | 1.068 | 0.34915 | 1.6994 | 0 | 0 | 0 | 0
2021-12-09 04:30 | 0.28993 | 0.95218 | 0.29198 | 1.4879 | 0 | 0 | 0 | 0
2021-12-09 04:45 | 0.4982 | 0.91741 | 0.27666 | 1.3571 | 0 | 0 | 0 | 0
2021-12-09 05:00 | 0.39509 | 0.91741 | 0.2736 | 1.3044 | 0 | 0 | 0 | 0
2021-12-09 05:15 | 0.44919 | 0.97901 | 0.31648 | 1.3035 | 0 | 0 | 0 | 0
2021-12-09 05:30 | 0.32975 | 1.0453 | 0.34302 | 1.2537 | 0 | 0 | 0 | 0
2021-12-09 05:45 | 0.30321 | 1.0217 | 0.25931 | 1.2375 | 0 | 0 | 0 | 0
2021-12-09 06:00 | 0.30831 | 0.94594 | 0.24093 | 1.2122 | 0 | 0 | 0 | 0
2021-12-09 06:15 | 0.30423 | 0.98611 | 0.28483 | 1.2242 | 0 | 0 | 0 | 0
2021-12-09 06:30 | 0.35323 | 0.99771 | 0.42061 | 1.2853 | 0 | 0 | 0 | 0
2021-12-09 06:45 | 0.37467 | 0.9661 | 0.30627 | 1.2146 | 0 | 0 | 0 | 0
2021-12-09 07:00 | 0.32873 | 0.60882 | 0.27054 | 0.39932 | 0 | 0 | 0 | 0
2021-12-09 07:15 | 0.29504 | 0.58995 | 0.27462 | 0.33865 | 0 | 0 | 0 | 0
2021-12-09 07:30 | 0.38386 | 0.65402 | 0.36038 | 0.43986 | 0 | 0 | 0 | 0
2021-12-09 07:45 | 0.82897 | 0.70791 | 0.77997 | 0.46261 | 0.017421 | 0.01532 | 0.000913 | 0.006929
2021-12-09 08:00 | 1.1026 | 1.8138 | 1.368 | 1.9572 | 0.11092 | 0.067684 | 0.005605 | 0.039825
2021-12-09 08:15 | 0.89839 | 1.3727 | 0.60437 | 1.7051 | 0.20442 | 0.12434 | 0.010297 | 0.072721
2021-12-09 08:30 | 0.86164 | 1.2356 | 0.71871 | 1.4917 | 0.29791 | 0.16914 | 0.014989 | 0.10562
2021-12-09 08:45 | 0.91064 | 1.0097 | 0.83713 | 1.634 | 0.35992 | 0.19455 | 0.020873 | 0.12871
2021-12-09 09:00 | 0.58804 | 1.2354 | 0.69829 | 1.5179 | 0.28414 | 0.17569 | 0.031699 | 0.11448
2021-12-09 09:15 | 0.60845 | 1.1918 | 0.4982 | 1.1253 | 0.20835 | 0.151 | 0.042526 | 0.10025
2021-12-09 09:30 | 0.67379 | 1.3824 | 0.41244 | 1.5067 | 0.13256 | 0.17668 | 0.053352 | 0.086023
2021-12-09 09:45 | 0.65746 | 1.2775 | 0.44511 | 1.4077 | 0.070505 | 0.15548 | 0.065305 | 0.079336
2021-12-09 10:00 | 0.69829 | 1.2166 | 0.48595 | 1.153 | 0.0687 | 0.15631 | 0.081941 | 0.10033
2021-12-09 10:15 | 0.75138 | 1.1851 | 0.53495 | 1.1192 | 0.066895 | 0.18462 | 0.098577 | 0.12133
2021-12-09 10:30 | 0.68196 | 1.2113 | 0.62887 | 1.2586 | 0.06509 | 0.1944 | 0.11521 | 0.14233
2021-12-09 10:45 | 0.58395 | 1.1933 | 0.49003 | 1.3948 | 0.067032 | 0.20964 | 0.13094 | 0.15942
2021-12-09 11:00 | 0.86572 | 1.2113 | 0.53087 | 1.2445 | 0.085445 | 0.19074 | 0.14287 | 0.16289
2021-12-09 11:15 | 0.54312 | 1.3118 | 2.5216 | 1.457 | 0.10386 | 0.19026 | 0.1548 | 0.16636
2021-12-09 11:30 | 0.49411 | 1.3495 | 1.562 | 1.6751 | 0.12227 | 0.16207 | 0.16673 | 0.16984
2021-12-09 11:45 | 0.5472 | 1.2519 | 0.62479 | 1.5195 | 0.1362 | 0.15144 | 0.18194 | 0.17297
2021-12-09 12:00 | 0.47778 | 1.2064 | 0.73913 | 1.0159 | 0.13038 | 0.14084 | 0.21084 | 0.17568
2021-12-09 12:15 | 0.42878 | 1.2519 | 0.62887 | 1.382 | 0.12456 | 0.17108 | 0.23973 | 0.17839
2021-12-09 12:30 | 0.37671 | 1.281 | 0.54312 | 1.5202 | 0.11874 | 0.1594 | 0.26863 | 0.1811
2021-12-09 12:45 | 0.30218 | 1.3079 | 1.6743 | 1.7206 | 0.11163 | 0.14641 | 0.28885 | 0.1818
2021-12-09 13:00 | 0.3369 | 1.7809 | 3.0831 | 2.0435 | 0.098867 | 0.13895 | 0.27277 | 0.17457
2021-12-09 13:15 | 0.30116 | 1.2518 | 0.54312 | 1.7212 | 0.0861 | 0.13963 | 0.2567 | 0.16735
2021-12-09 13:30 | 0.27156 | 1.2613 | 0.49003 | 1.815 | 0.073334 | 0.14738 | 0.24062 | 0.16013
2021-12-09 13:45 | 0.27156 | 1.2316 | 0.48186 | 1.3902 | 0.064274 | 0.18114 | 0.22272 | 0.15805
2021-12-09 14:00 | 0.38488 | 1.2316 | 0.82488 | 1.3961 | 0.071621 | 0.21318 | 0.19717 | 0.17437
2021-12-09 14:15 | 0.42061 | 1.1769 | 0.40325 | 1.1825 | 0.078968 | 0.21026 | 0.17162 | 0.19068
2021-12-09 14:30 | 0.29402 | 0.97746 | 0.43286 | 0.48828 | 0.086314 | 0.21954 | 0.14606 | 0.207
2021-12-09 14:45 | 0.27768 | 0.90914 | 0.44103 | 0.40603 | 0.094132 | 0.21065 | 0.12081 | 0.21086
2021-12-09 15:00 | 0.27462 | 0.87811 | 0.44103 | 0.38327 | 0.10404 | 0.16002 | 0.096793 | 0.16852
2021-12-09 15:15 | 0.27666 | 0.84457 | 0.35731 | 0.35615 | 0.11395 | 0.10748 | 0.07278 | 0.12618
2021-12-09 15:30 | 0.36242 | 0.83546 | 0.40427 | 0.33267 | 0.12385 | 0.077411 | 0.048767 | 0.083846
2021-12-09 15:45 | 0.30627 | 0.84514 | 0.44103 | 0.32421 | 0.12588 | 0.052475 | 0.027952 | 0.047715
2021-12-09 16:00 | 0.30933 | 0.85433 | 0.48186 | 0.33004 | 0.092903 | 0.042614 | 0.020613 | 0.035109
2021-12-09 16:15 | 0.31444 | 0.93396 | 0.68604 | 0.40238 | 0.059921 | 0.028623 | 0.013274 | 0.022502
2021-12-09 16:30 | 0.42469 | 0.87347 | 0.33792 | 0.39494 | 0.026939 | 0.014179 | 0.005934 | 0.009896
2021-12-09 16:45 | 0.35323 | 0.94919 | 0.34915 | 0.4085 | 0 | 0 | 0 | 0
2021-12-09 17:00 | 0.30116 | 0.96354 | 0.44103 | 0.43359 | 0 | 0 | 0 | 0
2021-12-09 17:15 | 0.24399 | 1.038 | 0.53903 | 0.56354 | 0 | 0 | 0 | 0
2021-12-09 17:30 | 0.26748 | 1.0984 | 0.55537 | 0.71827 | 0 | 0 | 0 | 0
2021-12-09 17:45 | 0.37773 | 1.1194 | 0.51453 | 1.294 | 0 | 0 | 0 | 0
2021-12-09 18:00 | 0.37058 | 1.1521 | 0.47778 | 1.3333 | 0 | 0 | 0 | 0
2021-12-09 18:15 | 0.28789 | 1.1334 | 0.60437 | 1.5163 | 0 | 0 | 0 | 0
2021-12-09 18:30 | 0.2981 | 1.1322 | 0.68196 | 1.4643 | 0 | 0 | 0 | 0
2021-12-09 18:45 | 0.37773 | 1.2051 | 0.66154 | 1.3633 | 0 | 0 | 0 | 0
2021-12-09 19:00 | 2.8279 | 1.1105 | 3.1444 | 1.9966 | 0 | 0 | 0 | 0
2021-12-09 19:15 | 2.9606 | 1.432 | 4.231 | 2.8106 | 0 | 0 | 0 | 0
2021-12-09 19:30 | 2.8075 | 1.5238 | 3.7263 | 3.1455 | 0 | 0 | 0 | 0
2021-12-09 19:45 | 2.8177 | 1.2548 | 3.7569 | 2.9053 | 0 | 0 | 0 | 0
2021-12-09 20:00 | 0.51862 | 1.0093 | 0.95964 | 1.5184 | 0 | 0 | 0 | 0
2021-12-09 20:15 | 0.3471 | 1.0233 | 0.69013 | 1.1755 | 0 | 0 | 0 | 0
2021-12-09 20:30 | 0.44511 | 0.90687 | 1.2455 | 1.0873 | 0 | 0 | 0 | 0
2021-12-09 20:45 | 0.32669 | 0.8996 | 1.368 | 1.0441 | 0 | 0 | 0 | 0
2021-12-09 21:00 | 0.2981 | 0.99557 | 0.65746 | 1.0495 | 0 | 0 | 0 | 0
2021-12-09 21:15 | 0.34506 | 0.88537 | 0.47778 | 0.59008 | 0 | 0 | 0 | 0
2021-12-09 21:30 | 0.41653 | 0.88205 | 0.51862 | 0.63339 | 0 | 0 | 0 | 0
2021-12-09 21:45 | 0.31444 | 0.76557 | 0.41244 | 0.56178 | 0 | 0 | 0 | 0
2021-12-09 22:00 | 0.30831 | 0.75361 | 0.41244 | 0.5157 | 0 | 0 | 0 | 0
2021-12-09 22:15 | 0.34608 | 0.66505 | 0.41244 | 0.49616 | 0 | 0 | 0 | 0
2021-12-09 22:30 | 0.35221 | 0.66505 | 0.38284 | 0.46334 | 0 | 0 | 0 | 0
2021-12-09 22:45 | 0.53903 | 0.64827 | 0.34098 | 0.43694 | 0 | 0 | 0 | 0
2021-12-09 23:00 | 3.3077 | 2.1041 | 3.2464 | 2.6047 | 0 | 0 | 0 | 0
2021-12-09 23:15 | 3.5527 | 2.4616 | 3.4915 | 2.7112 | 0 | 0 | 0 | 0
2021-12-09 23:30 | 3.5527 | 2.4616 | 3.614 | 2.7127 | 0 | 0 | 0 | 0
2021-12-09 23:45 | 3.5323 | 2.4616 | 3.5936 | 2.6635 | 0 | 0 | 0 | 0
2021-12-10 | 3.4915 | 2.3864 | 3.5119 | 2.6027 | 0 | 0 | 0 | 0
2021-12-10 00:15 | 3.471 | 2.4164 | 3.4915 | 2.4111 | 0 | 0 | 0 | 0
2021-12-10 00:30 | 3.5731 | 2.4531 | 3.5221 | 2.2492 | 0 | 0 | 0 | 0
2021-12-10 00:45 | 3.471 | 2.4858 | 3.5221 | 2.2569 | 0 | 0 | 0 | 0
2021-12-10 01:00 | 3.4506 | 2.4858 | 3.5221 | 2.1819 | 0 | 0 | 0 | 0
2021-12-10 01:15 | 3.4608 | 2.4773 | 3.5017 | 2.1332 | 0 | 0 | 0 | 0
2021-12-10 01:30 | 3.5323 | 2.4358 | 3.5017 | 2.1656 | 0 | 0 | 0 | 0
2021-12-10 01:45 | 3.471 | 2.3512 | 3.42 | 2.1138 | 0 | 0 | 0 | 0
2021-12-10 02:00 | 3.4404 | 2.3334 | 3.4506 | 2.1079 | 0 | 0 | 0 | 0
2021-12-10 02:15 | 3.4506 | 2.3331 | 3.4608 | 2.15 | 0 | 0 | 0 | 0
2021-12-10 02:30 | 3.5323 | 2.4046 | 3.5833 | 2.1691 | 0 | 0 | 0 | 0
2021-12-10 02:45 | 3.4813 | 2.3847 | 3.5527 | 2.1579 | 0 | 0 | 0 | 0
2021-12-10 03:00 | 3.3996 | 2.4049 | 3.4608 | 2.1268 | 0 | 0 | 0 | 0
2021-12-10 03:15 | 3.42 | 2.4049 | 3.4813 | 2.1079 | 0 | 0 | 0 | 0
2021-12-10 03:30 | 3.5527 | 2.3762 | 3.471 | 2.1046 | 0 | 0 | 0 | 0
2021-12-10 03:45 | 3.4608 | 2.3263 | 3.5119 | 2.1327 | 0 | 0 | 0 | 0
2021-12-10 04:00 | 3.42 | 2.2668 | 2.736 | 2.025 | 0 | 0 | 0 | 0
2021-12-10 04:15 | 3.4098 | 2.3725 | 1.5313 | 1.8656 | 0 | 0 | 0 | 0
2021-12-10 04:30 | 3.4098 | 2.4416 | 0.28993 | 1.489 | 0 | 0 | 0 | 0
2021-12-10 04:45 | 3.6242 | 2.4416 | 0.4982 | 1.3827 | 0 | 0 | 0 | 0
2021-12-10 05:00 | 3.5527 | 2.376 | 0.39509 | 1.3162 | 0 | 0 | 0 | 0
2021-12-10 05:15 | 3.4915 | 2.4001 | 0.44919 | 1.3215 | 0 | 0 | 0 | 0
2021-12-10 05:30 | 3.4404 | 2.2841 | 0.32975 | 1.2418 | 0 | 0 | 0 | 0
2021-12-10 05:45 | 3.4506 | 2.2708 | 0.30321 | 1.2395 | 0 | 0 | 0 | 0
2021-12-10 06:00 | 3.5119 | 2.2405 | 0.30831 | 1.2204 | 0 | 0 | 0 | 0
2021-12-10 06:15 | 3.4915 | 2.2169 | 0.30423 | 1.2287 | 0 | 0 | 0 | 0
2021-12-10 06:30 | 3.4098 | 2.237 | 0.35323 | 1.2818 | 0 | 0 | 0 | 0
2021-12-10 06:45 | 3.3485 | 2.1927 | 0.37467 | 1.2284 | 0 | 0 | 0 | 0
2021-12-10 07:00 | 0.6207 | 0.62765 | 0.32873 | 0.40004 | 0 | 0 | 0 | 0
2021-12-10 07:15 | 0.2736 | 0.63521 | 0.29504 | 0.34054 | 0 | 0 | 0 | 0
2021-12-10 07:30 | 0.3369 | 0.66594 | 0.38386 | 0.43111 | 0 | 0 | 0 | 0
2021-12-10 07:45 | 0.65337 | 0.72751 | 0.82897 | 0.51687 | 0.001738 | 0.019564 | 0.017421 | 0.009077
2021-12-10 08:00 | 3.9304 | 1.9964 | 1.1026 | 1.9426 | 0.011497 | 0.092101 | 0.11092 | 0.05393
2021-12-10 08:15 | 3.6446 | 1.9823 | 0.89839 | 1.6439 | 0.021256 | 0.16591 | 0.20442 | 0.098783
2021-12-10 08:30 | 3.6854 | 2.2058 | 0.86164 | 1.4876 | 0.031016 | 0.20955 | 0.29791 | 0.14364
2021-12-10 08:45 | 3.7365 | 1.8706 | 0.91064 | 1.7066 | 0.042028 | 0.2398 | 0.35992 | 0.17464
2021-12-10 09:00 | 1.2455 | 1.5475 | 0.58804 | 1.4829 | 0.058836 | 0.21854 | 0.28414 | 0.15007
2021-12-10 09:15 | 0.73504 | 1.2467 | 0.60845 | 1.0833 | 0.075645 | 0.18362 | 0.20835 | 0.1255
2021-12-10 09:30 | 0.48595 | 1.502 | 0.67379 | 1.2938 | 0.092454 | 0.22376 | 0.13256 | 0.10093
2021-12-10 09:45 | 0.46144 | 1.4522 | 0.65746 | 1.3135 | 0.10622 | 0.18754 | 0.070505 | 0.084428
2021-12-10 10:00 | 1.0046 | 1.2683 | 0.69829 | 1.1554 | 0.10586 | 0.17744 | 0.0687 | 0.099771
2021-12-10 10:15 | 3.0729 | 1.2588 | 0.75138 | 1.1396 | 0.10551 | 0.20888 | 0.066895 | 0.11511
2021-12-10 10:30 | 0.76363 | 1.4256 | 0.68196 | 1.2831 | 0.10515 | 0.24065 | 0.06509 | 0.13046
2021-12-10 10:45 | 0.64112 | 1.4426 | 0.58395 | 1.4071 | 0.10338 | 0.2594 | 0.067032 | 0.14305
2021-12-10 11:00 | 0.58395 | 1.441 | 0.86572 | 1.2801 | 0.095032 | 0.23816 | 0.085445 | 0.14632
2021-12-10 11:15 | 0.50228 | 1.3084 | 0.54312 | 1.2472 | 0.086683 | 0.23744 | 0.10386 | 0.1496
2021-12-10 11:30 | 0.51045 | 1.4136 | 0.49411 | 1.4249 | 0.078334 | 0.21098 | 0.12227 | 0.15288
2021-12-10 11:45 | 0.93514 | 1.441 | 0.5472 | 1.5143 | 0.07284 | 0.22542 | 0.1362 | 0.15706
2021-12-10 12:00 | 3.1852 | 1.2375 | 0.47778 | 1.0113 | 0.080647 | 0.21119 | 0.13038 | 0.16389
2021-12-10 12:15 | 2.3072 | 1.441 | 0.42878 | 1.3645 | 0.088453 | 0.23081 | 0.12456 | 0.17071
2021-12-10 12:30 | 0.47778 | 1.421 | 0.37671 | 1.5098 | 0.09626 | 0.2108 | 0.11874 | 0.17754
2021-12-10 12:45 | 2.103 | 1.4412 | 0.30218 | 1.5975 | 0.10016 | 0.18922 | 0.11163 | 0.18094
2021-12-10 13:00 | 2.4093 | 1.4447 | 0.3369 | 1.6541 | 0.085828 | 0.1998 | 0.098867 | 0.17177
2021-12-10 13:15 | 0.39611 | 1.4531 | 0.30116 | 1.7293 | 0.071494 | 0.21058 | 0.0861 | 0.1626
2021-12-10 13:30 | 1.0617 | 1.6128 | 0.27156 | 1.8191 | 0.05716 | 0.23419 | 0.073334 | 0.15344
2021-12-10 13:45 | 0.76363 | 1.4373 | 0.27156 | 1.3803 | 0.044388 | 0.24389 | 0.064274 | 0.15
2021-12-10 14:00 | 0.3665 | 1.4105 | 0.38488 | 1.3951 | 0.038923 | 0.27699 | 0.071621 | 0.1675
2021-12-10 14:15 | 0.46961 | 1.2639 | 0.42061 | 1.2108 | 0.033459 | 0.28594 | 0.078968 | 0.185
2021-12-10 14:30 | 0.40019 | 1.0172 | 0.29402 | 0.49936 | 0.027994 | 0.29856 | 0.086314 | 0.2025
2021-12-10 14:45 | 0.4737 | 1.0127 | 0.27768 | 0.41332 | 0.022458 | 0.28647 | 0.094132 | 0.20821
2021-12-10 15:00 | 0.51862 | 0.96582 | 0.27462 | 0.38823 | 0.016586 | 0.19362 | 0.10404 | 0.1699
2021-12-10 15:15 | 0.39202 | 0.93606 | 0.27666 | 0.34565 | 0.010714 | 0.13682 | 0.11395 | 0.1316
2021-12-10 15:30 | 0.36854 | 0.92363 | 0.36242 | 0.33704 | 0.004842 | 0.10975 | 0.12385 | 0.093297
2021-12-10 15:45 | 0.37773 | 0.90204 | 0.30627 | 0.33237 | 0 | 0.073366 | 0.12588 | 0.059821
2021-12-10 16:00 | 0.36242 | 0.94251 | 0.30933 | 0.33558 | 0 | 0.052114 | 0.092903 | 0.044067
2021-12-10 16:15 | 0.55945 | 0.92401 | 0.31444 | 0.4085 | 0 | 0.0338 | 0.059921 | 0.028312
2021-12-10 16:30 | 0.39304 | 0.8385 | 0.42469 | 0.40777 | 0 | 0.016587 | 0.026939 | 0.012557
2021-12-10 16:45 | 0.33587 | 0.84275 | 0.35323 | 0.41769 | 0 | 0 | 0 | 0
2021-12-10 17:00 | 0.52678 | 0.84568 | 0.30116 | 0.43811 | 0 | 0 | 0 | 0
2021-12-10 17:15 | 1.0311 | 1.0312 | 0.24399 | 0.55989 | 0 | 0 | 0 | 0
2021-12-10 17:30 | 1.613 | 1.1292 | 0.26748 | 0.70981 | 0 | 0 | 0 | 0
2021-12-10 17:45 | 1.2863 | 1.4368 | 0.37773 | 1.2972 | 0 | 0 | 0 | 0
2021-12-10 18:00 | 1.419 | 1.4796 | 0.37058 | 1.3355 | 0 | 0 | 0 | 0
2021-12-10 18:15 | 1.8887 | 1.5089 | 0.28789 | 1.5208 | 0 | 0 | 0 | 0
2021-12-10 18:30 | 2.0826 | 1.5089 | 0.2981 | 1.4686 | 0 | 0 | 0 | 0
2021-12-10 18:45 | 0.69829 | 1.2277 | 0.37773 | 1.3673 | 0 | 0 | 0 | 0
2021-12-10 19:00 | 0.69829 | 1.3225 | 2.8279 | 2.3416 | 0 | 0 | 0 | 0
2021-12-10 19:15 | 4.0427 | 1.8951 | 2.9606 | 3.1901 | 0 | 0 | 0 | 0
2021-12-10 19:30 | 4.0632 | 2.3924 | 2.8075 | 3.5009 | 0 | 0 | 0 | 0
2021-12-10 19:45 | 3.8488 | 2.4361 | 2.8177 | 3.2634 | 0 | 0 | 0 | 0
2021-12-10 20:00 | 0.67379 | 1.4753 | 0.51862 | 1.5497 | 0 | 0 | 0 | 0
2021-12-10 20:15 | 0.60437 | 1.2249 | 0.3471 | 1.1609 | 0 | 0 | 0 | 0
2021-12-10 20:30 | 0.82488 | 1.1084 | 0.44511 | 1.097 | 0 | 0 | 0 | 0
2021-12-10 20:45 | 0.82488 | 1.0753 | 0.32669 | 1.0483 | 0 | 0 | 0 | 0
2021-12-10 21:00 | 0.65746 | 1.2155 | 0.2981 | 1.053 | 0 | 0 | 0 | 0
2021-12-10 21:15 | 0.6207 | 0.82777 | 0.34506 | 0.59941 | 0 | 0 | 0 | 0
2021-12-10 21:30 | 1.0311 | 0.82471 | 0.41653 | 0.64287 | 0 | 0 | 0 | 0
2021-12-10 21:45 | 0.84938 | 0.64352 | 0.31444 | 0.54078 | 0 | 0 | 0 | 0
2021-12-10 22:00 | 0.64112 | 0.64489 | 0.30831 | 0.48682 | 0 | 0 | 0 | 0
2021-12-10 22:15 | 0.56762 | 0.61365 | 0.34608 | 0.4893 | 0 | 0 | 0 | 0
2021-12-10 22:30 | 0.44103 | 0.63504 | 0.35221 | 0.46334 | 0 | 0 | 0 | 0
2021-12-10 22:45 | 0.38998 | 0.63504 | 0.53903 | 0.4597 | 0 | 0 | 0 | 0
2021-12-10 23:00 | 3.3281 | 2.1527 | 3.3077 | 2.6062 | 0 | 0 | 0 | 0
2021-12-10 23:15 | 3.6446 | 2.4708 | 3.5527 | 2.717 | 0 | 0 | 0 | 0
2021-12-10 23:30 | 3.6038 | 2.4708 | 3.5527 | 2.7331 | 0 | 0 | 0 | 0
2021-12-10 23:45 | 3.5017 | 2.4708 | 3.5323 | 2.6839 | 0 | 0 | 0 | 0
2021-12-11 | 3.4915 | 2.4136 | 3.4915 | 2.61 | 0 | 0 | 0 | 0
2021-12-11 00:15 | 3.5833 | 2.2637 | 3.471 | 2.4023 | 0 | 0 | 0 | 0
2021-12-11 00:30 | 3.6038 | 2.2629 | 3.5731 | 2.2696 | 0 | 0 | 0 | 0
2021-12-11 00:45 | 3.5527 | 2.2629 | 3.471 | 2.254 | 0 | 0 | 0 | 0
2021-12-11 01:00 | 3.4302 | 2.2629 | 3.4506 | 2.1878 | 0 | 0 | 0 | 0
2021-12-11 01:15 | 3.4302 | 2.2656 | 3.4608 | 2.1376 | 0 | 0 | 0 | 0
2021-12-11 01:30 | 3.5425 | 2.2838 | 3.5323 | 2.1744 | 0 | 0 | 0 | 0
2021-12-11 01:45 | 3.4404 | 2.2352 | 3.471 | 2.1255 | 0 | 0 | 0 | 0
2021-12-11 02:00 | 3.4506 | 2.1273 | 3.4404 | 2.1152 | 0 | 0 | 0 | 0
2021-12-11 02:15 | 3.4813 | 2.0916 | 3.4506 | 2.1456 | 0 | 0 | 0 | 0
2021-12-11 02:30 | 3.5527 | 1.9396 | 3.5323 | 2.1691 | 0 | 0 | 0 | 0
2021-12-11 02:45 | 3.5629 | 1.9577 | 3.4813 | 2.1652 | 0 | 0 | 0 | 0
2021-12-11 03:00 | 3.8079 | 1.9752 | 3.3996 | 2.1254 | 0 | 0 | 0 | 0
2021-12-11 03:15 | 3.5833 | 1.9752 | 3.42 | 2.1093 | 0 | 0 | 0 | 0
2021-12-11 03:30 | 3.5119 | 2.0504 | 3.5527 | 2.1251 | 0 | 0 | 0 | 0
2021-12-11 03:45 | 3.5323 | 1.9775 | 3.4608 | 2.1356 | 0 | 0 | 0 | 0
2021-12-11 04:00 | 2.8483 | 1.8556 | 3.42 | 2.0265 | 0 | 0 | 0 | 0
2021-12-11 04:15 | 1.2965 | 1.7696 | 3.4098 | 1.8627 | 0 | 0 | 0 | 0
2021-12-11 04:30 | 1.0209 | 1.1326 | 3.4098 | 1.492 | 0 | 0 | 0 | 0
2021-12-11 04:45 | 0.6207 | 1.4179 | 3.6242 | 1.4031 | 0 | 0 | 0 | 0
2021-12-11 05:00 | 0.34404 | 1.2827 | 3.5527 | 1.3279 | 0 | 0 | 0 | 0
2021-12-11 05:15 | 0.37263 | 1.2575 | 3.4915 | 1.3317 | 0 | 0 | 0 | 0
2021-12-11 05:30 | 0.41653 | 0.87187 | 3.4404 | 1.2448 | 0 | 0 | 0 | 0
2021-12-11 05:45 | 0.34608 | 0.82619 | 3.4506 | 1.2337 | 0 | 0 | 0 | 0
2021-12-11 06:00 | 0.37569 | 0.76827 | 3.5119 | 1.2204 | 0 | 0 | 0 | 0
2021-12-11 06:15 | 0.40223 | 0.82454 | 3.4915 | 1.2433 | 0 | 0 | 0 | 0
2021-12-11 06:30 | 0.32873 | 0.99398 | 3.4098 | 1.2818 | 0 | 0 | 0 | 0
2021-12-11 06:45 | 0.35935 | 0.86427 | 3.3485 | 1.2284 | 0 | 0 | 0 | 0
2021-12-11 07:00 | 0.46553 | 0.62239 | 0.6207 | 0.4158 | 0 | 0 | 0 | 0
2021-12-11 07:15 | 0.33383 | 0.64204 | 0.2736 | 0.32406 | 0 | 0 | 0 | 0
2021-12-11 07:30 | 0.36956 | 0.64871 | 0.3369 | 0.40982 | 0 | 0 | 0 | 0
2021-12-11 07:45 | 0.37875 | 0.76875 | 0.65337 | 0.55931 | 0.007858 | 0.012094 | 0.001738 | 0.009237
2021-12-11 08:00 | 2.001 | 1.4829 | 3.9304 | 1.9485 | 0.054111 | 0.053288 | 0.011497 | 0.055113
2021-12-11 08:15 | 0.6207 | 1.4221 | 3.6446 | 1.5668 | 0.10036 | 0.084408 | 0.021256 | 0.10099
2021-12-11 08:30 | 0.48186 | 1.1698 | 3.6854 | 1.492 | 0.14662 | 0.13103 | 0.031016 | 0.14686
2021-12-11 08:45 | 0.47778 | 1.449 | 3.7365 | 1.7285 | 0.17921 | 0.15523 | 0.042028 | 0.17864
2021-12-11 09:00 | 0.65746 | 1.3874 | 1.2455 | 1.356 | 0.14491 | 0.14135 | 0.058836 | 0.15422
2021-12-11 09:15 | 0.90656 | 0.98474 | 0.73504 | 1.1055 | 0.11061 | 0.13583 | 0.075645 | 0.12981
2021-12-11 09:30 | 0.75138 | 1.2044 | 0.48595 | 1.2973 | 0.076308 | 0.11552 | 0.092454 | 0.1054
2021-12-11 09:45 | 0.67379 | 1.282 | 0.46144 | 1.2872 | 0.052519 | 0.11134 | 0.10622 | 0.088253
2021-12-11 10:00 | 0.60029 | 1.0708 | 1.0046 | 1.1898 | 0.080352 | 0.11229 | 0.10586 | 0.099721
2021-12-11 10:15 | 0.61254 | 1.0919 | 3.0729 | 1.4998 | 0.10818 | 0.13917 | 0.10551 | 0.11119
2021-12-11 10:30 | 0.60437 | 1.093 | 0.76363 | 1.3146 | 0.13602 | 0.16303 | 0.10515 | 0.12266
2021-12-11 10:45 | 0.5962 | 1.0919 | 0.64112 | 1.4199 | 0.15455 | 0.18557 | 0.10338 | 0.13252
2021-12-11 11:00 | 0.69013 | 1.1241 | 0.58395 | 1.3085 | 0.12731 | 0.13664 | 0.095032 | 0.13656
2021-12-11 11:15 | 0.69421 | 1.3387 | 0.50228 | 1.2513 | 0.10007 | 0.1286 | 0.086683 | 0.14061
2021-12-11 11:30 | 0.61254 | 1.3511 | 0.51045 | 1.4132 | 0.072838 | 0.13526 | 0.078334 | 0.14465
2021-12-11 11:45 | 0.77588 | 1.1359 | 0.93514 | 1.5921 | 0.050369 | 0.15833 | 0.07284 | 0.14967
2021-12-11 12:00 | 0.69013 | 1.1094 | 3.1852 | 1.4285 | 0.051431 | 0.1634 | 0.080647 | 0.15812
2021-12-11 12:15 | 0.68196 | 1.1682 | 2.3072 | 1.6602 | 0.052494 | 0.16398 | 0.088453 | 0.16658
2021-12-11 12:30 | 0.65746 | 1.1682 | 0.47778 | 1.5483 | 0.053556 | 0.16044 | 0.09626 | 0.17503
2021-12-11 12:45 | 0.60029 | 1.0626 | 2.103 | 1.8559 | 0.053707 | 0.15574 | 0.10016 | 0.18004
2021-12-11 13:00 | 0.5717 | 1.0207 | 2.4093 | 1.9289 | 0.04935 | 0.14746 | 0.085828 | 0.17162
2021-12-11 13:15 | 0.5227 | 1.2764 | 0.39611 | 1.7229 | 0.044993 | 0.14893 | 0.071494 | 0.1632
2021-12-11 13:30 | 0.44511 | 1.4131 | 1.0617 | 1.8937 | 0.040636 | 0.14195 | 0.05716 | 0.15478
2021-12-11 13:45 | 0.53087 | 1.6268 | 0.76363 | 1.4059 | 0.036783 | 0.17936 | 0.044388 | 0.15127
2021-12-11 14:00 | 0.97189 | 1.6205 | 0.3665 | 1.3716 | 0.035428 | 0.16184 | 0.038923 | 0.16628
2021-12-11 14:15 | 1.4497 | 1.1376 | 0.46961 | 1.2137 | 0.034073 | 0.16707 | 0.033459 | 0.18129
2021-12-11 14:30 | 0.70646 | 1.1832 | 0.40019 | 0.50389 | 0.032718 | 0.17444 | 0.027994 | 0.19631
2021-12-11 14:45 | 0.5227 | 1.2789 | 0.4737 | 0.4298 | 0.030331 | 0.16772 | 0.022458 | 0.20057
2021-12-11 15:00 | 0.5227 | 1.2408 | 0.51862 | 0.40282 | 0.022811 | 0.13847 | 0.016586 | 0.16423
2021-12-11 15:15 | 0.50636 | 1.1521 | 0.39202 | 0.32523 | 0.015292 | 0.092235 | 0.010714 | 0.1279
2021-12-11 15:30 | 0.55945 | 1.3003 | 0.36854 | 0.34506 | 0.007773 | 0.070669 | 0.004842 | 0.091565
2021-12-11 15:45 | 0.49411 | 1.0651 | 0.37773 | 0.34142 | 0.001447 | 0.071593 | 0 | 0.059567
2021-12-11 16:00 | 0.4737 | 1.3314 | 0.36242 | 0.33369 | 0.001069 | 0.053203 | 0 | 0.04388
2021-12-11 16:15 | 0.5472 | 1.0885 | 0.55945 | 0.42484 | 0.000692 | 0.032422 | 0 | 0.028193
2021-12-11 16:30 | 0.60437 | 0.959 | 0.39304 | 0.37117 | 0.000315 | 0.01354 | 0 | 0.012505
2021-12-11 16:45 | 0.60437 | 0.96666 | 0.33587 | 0.36534 | 0 | 0 | 0 | 0
2021-12-11 17:00 | 0.51862 | 1.0112 | 0.52678 | 0.41594 | 0 | 0 | 0 | 0
2021-12-11 17:15 | 0.4737 | 1.1052 | 1.0311 | 0.4753 | 0 | 0 | 0 | 0
2021-12-11 17:30 | 0.46144 | 1.0571 | 1.613 | 0.72732 | 0 | 0 | 0 | 0
2021-12-11 17:45 | 0.5962 | 1.126 | 1.2863 | 1.2651 | 0 | 0 | 0 | 0
2021-12-11 18:00 | 0.60845 | 1.2877 | 1.419 | 1.3049 | 0 | 0 | 0 | 0
2021-12-11 18:15 | 0.56354 | 1.228 | 1.8887 | 1.5295 | 0 | 0 | 0 | 0
2021-12-11 18:30 | 0.60845 | 1.228 | 2.0826 | 1.6244 | 0 | 0 | 0 | 0
2021-12-11 18:45 | 0.61662 | 1.1964 | 0.69829 | 1.3912 | 0 | 0 | 0 | 0
2021-12-11 19:00 | 2.9606 | 1.4174 | 0.69829 | 2.3667 | 0 | 0 | 0 | 0
2021-12-11 19:15 | 3.8896 | 1.5718 | 4.0427 | 3.5795 | 0 | 0 | 0 | 0
2021-12-11 19:30 | 3.8182 | 1.8555 | 4.0632 | 3.4573 | 0 | 0 | 0 | 0
2021-12-11 19:45 | 3.859 | 2.0105 | 3.8488 | 3.3057 | 0 | 0 | 0 | 0
2021-12-11 20:00 | 1.7968 | 1.6113 | 0.67379 | 1.5217 | 0 | 0 | 0 | 0
2021-12-11 20:15 | 0.91064 | 1.1815 | 0.60437 | 1.1201 | 0 | 0 | 0 | 0
2021-12-11 20:30 | 0.75955 | 1.3553 | 0.82488 | 1.0976 | 0 | 0 | 0 | 0
2021-12-11 20:45 | 1.1128 | 1.0228 | 0.82488 | 1.0693 | 0 | 0 | 0 | 0
2021-12-11 21:00 | 0.67379 | 1.066 | 0.65746 | 1.0454 | 0 | 0 | 0 | 0
2021-12-11 21:15 | 0.62887 | 0.82312 | 0.6207 | 0.6175 | 0 | 0 | 0 | 0
2021-12-11 21:30 | 0.63704 | 0.97309 | 1.0311 | 0.71434 | 0 | 0 | 0 | 0
2021-12-11 21:45 | 0.95147 | 0.76875 | 0.84938 | 0.58745 | 0 | 0 | 0 | 0
2021-12-11 22:00 | 0.92289 | 0.81748 | 0.64112 | 0.50957 | 0 | 0 | 0 | 0
2021-12-11 22:15 | 0.55945 | 0.768 | 0.56762 | 0.5033 | 0 | 0 | 0 | 0
2021-12-11 22:30 | 0.47778 | 0.76272 | 0.44103 | 0.47428 | 0 | 0 | 0 | 0
2021-12-11 22:45 | 0.47778 | 0.76272 | 0.38998 | 0.46655 | 0 | 0 | 0 | 0
2021-12-11 23:00 | 3.3894 | 1.2911 | 3.3281 | 2.615 | 0 | 0 | 0 | 0
2021-12-11 23:15 | 3.6956 | 1.4256 | 3.6446 | 2.7418 | 0 | 0 | 0 | 0
2021-12-11 23:30 | 3.7263 | 1.5934 | 3.6038 | 2.7477 | 0 | 0 | 0 | 0
2021-12-11 23:45 | 3.6446 | 1.5614 | 3.5017 | 2.6869 | 0 | 0 | 0 | 0
2021-12-12 | 3.614 | 1.2357 | 3.4915 | 2.6158 | 0 | 0 | 0 | 0
2021-12-12 00:15 | 3.6344 | 1.2891 | 3.5833 | 2.4169 | 0 | 0 | 0 | 0
2021-12-12 00:30 | 3.6344 | 0.91865 | 3.6038 | 2.2769 | 0 | 0 | 0 | 0
2021-12-12 00:45 | 3.4915 | 0.91865 | 3.5527 | 2.2555 | 0 | 0 | 0 | 0
2021-12-12 01:00 | 3.3996 | 0.91865 | 3.4302 | 2.1776 | 0 | 0 | 0 | 0
2021-12-12 01:15 | 3.42 | 0.91865 | 3.4302 | 2.1303 | 0 | 0 | 0 | 0
2021-12-12 01:30 | 3.4302 | 0.91865 | 3.5425 | 2.1671 | 0 | 0 | 0 | 0
2021-12-12 01:45 | 1.8887 | 0.83884 | 3.4404 | 2.1182 | 0 | 0 | 0 | 0
2021-12-12 02:00 | 1.123 | 0.83884 | 3.4506 | 2.1035 | 0 | 0 | 0 | 0
2021-12-12 02:15 | 0.84938 | 0.83884 | 3.4813 | 2.1398 | 0 | 0 | 0 | 0
2021-12-12 02:30 | 0.69829 | 0.98172 | 3.5527 | 2.1618 | 0 | 0 | 0 | 0
2021-12-12 02:45 | 0.27156 | 0.98172 | 3.5629 | 2.171 | 0 | 0 | 0 | 0
2021-12-12 03:00 | 0.68196 | 0.92406 | 3.8079 | 2.172 | 0 | 0 | 0 | 0
2021-12-12 03:15 | 0.45328 | 0.86525 | 3.5833 | 2.1254 | 0 | 0 | 0 | 0
2021-12-12 03:30 | 0.38692 | 0.86525 | 3.5119 | 2.1309 | 0 | 0 | 0 | 0
2021-12-12 03:45 | 0.38079 | 0.89673 | 3.5323 | 2.1327 | 0 | 0 | 0 | 0
2021-12-12 04:00 | 0.38386 | 1.0072 | 2.8483 | 1.9302 | 0 | 0 | 0 | 0
2021-12-12 04:15 | 0.36752 | 1.0484 | 1.2965 | 1.5448 | 0 | 0 | 0 | 0
2021-12-12 04:30 | 0.30831 | 0.99562 | 1.0209 | 1.3213 | 0 | 0 | 0 | 0
2021-12-12 04:45 | 0.30831 | 1.0017 | 0.6207 | 1.3095 | 0 | 0 | 0 | 0
2021-12-12 05:00 | 0.391 | 0.97716 | 0.34404 | 1.2458 | 0 | 0 | 0 | 0
2021-12-12 05:15 | 0.31546 | 1.1722 | 0.37263 | 1.2677 | 0 | 0 | 0 | 0
2021-12-12 05:30 | 0.30116 | 1.1109 | 0.41653 | 1.2496 | 0 | 0 | 0 | 0
2021-12-12 05:45 | 0.3226 | 0.99073 | 0.34608 | 1.2297 | 0 | 0 | 0 | 0
2021-12-12 06:00 | 0.40836 | 0.96287 | 0.37569 | 1.2236 | 0 | 0 | 0 | 0
2021-12-12 06:15 | 0.29708 | 1.1319 | 0.40223 | 1.2523 | 0 | 0 | 0 | 0
2021-12-12 06:30 | 0.29708 | 1.1819 | 0.32873 | 1.2687 | 0 | 0 | 0 | 0
2021-12-12 06:45 | 0.29606 | 0.98682 | 0.35935 | 1.2185 | 0 | 0 | 0 | 0
2021-12-12 07:00 | 0.391 | 0.64767 | 0.46553 | 0.42513 | 0 | 0 | 0 | 0
2021-12-12 07:15 | 0.24093 | 0.65165 | 0.33383 | 0.31721 | 0 | 0 | 0 | 0
2021-12-12 07:30 | 0.31239 | 0.69565 | 0.36956 | 0.38036 | 0 | 0 | 0 | 0
2021-12-12 07:45 | 0.30423 | 0.86792 | 0.37875 | 0.53349 | 0.002305 | 0.016461 | 0.007858 | 0.010297
2021-12-12 08:00 | 1.4088 | 1.5848 | 2.001 | 1.9455 | 0.016564 | 0.06988 | 0.054111 | 0.062505
2021-12-12 08:15 | 1.6743 | 1.5326 | 0.6207 | 1.4586 | 0.030823 | 0.12151 | 0.10036 | 0.11471
2021-12-12 08:30 | 1.7457 | 1.5205 | 0.48186 | 1.4791 | 0.045081 | 0.17512 | 0.14662 | 0.16692
2021-12-12 08:45 | 2.5012 | 1.5382 | 0.47778 | 1.6865 | 0.05716 | 0.18426 | 0.17921 | 0.20287
2021-12-12 09:00 | 2.2664 | 1.4693 | 0.65746 | 1.345 | 0.057902 | 0.19916 | 0.14491 | 0.1724
2021-12-12 09:15 | 2.491 | 1.2531 | 0.90656 | 1.1551 | 0.058645 | 0.17244 | 0.11061 | 0.14192
2021-12-12 09:30 | 1.4599 | 1.3101 | 0.75138 | 1.3218 | 0.059387 | 0.14905 | 0.076308 | 0.11145
2021-12-12 09:45 | 2.8585 | 1.5027 | 0.67379 | 1.2878 | 0.061111 | 0.11536 | 0.052519 | 0.089989
2021-12-12 10:00 | 1.6028 | 1.2403 | 0.60029 | 1.1863 | 0.067948 | 0.11553 | 0.080352 | 0.10537
2021-12-12 10:15 | 0.75138 | 1.6052 | 0.61254 | 1.508 | 0.074784 | 0.10032 | 0.10818 | 0.12075
2021-12-12 10:30 | 0.8698 | 1.553 | 0.60437 | 1.3164 | 0.081621 | 0.11483 | 0.13602 | 0.13614
2021-12-12 10:45 | 0.47778 | 1.4334 | 0.5962 | 1.431 | 0.089846 | 0.1194 | 0.15455 | 0.14841
2021-12-12 11:00 | 0.44103 | 1.64 | 0.69013 | 1.3336 | 0.10533 | 0.13894 | 0.12731 | 0.14771
2021-12-12 11:15 | 0.3226 | 1.3862 | 0.69421 | 1.2577 | 0.1208 | 0.15548 | 0.10007 | 0.14701
2021-12-12 11:30 | 0.27666 | 1.4862 | 0.61254 | 1.3887 | 0.13628 | 0.19297 | 0.072838 | 0.1463
2021-12-12 11:45 | 0.27564 | 1.5834 | 0.77588 | 1.6254 | 0.14644 | 0.19125 | 0.050369 | 0.14766
2021-12-12 12:00 | 0.2491 | 1.4809 | 0.69013 | 1.4618 | 0.12872 | 0.17994 | 0.051431 | 0.15717
2021-12-12 12:15 | 0.36956 | 1.4852 | 0.68196 | 1.6894 | 0.111 | 0.16573 | 0.052494 | 0.16668
2021-12-12 12:30 | 0.40632 | 1.5096 | 0.65746 | 1.5711 | 0.093284 | 0.14646 | 0.053556 | 0.17619
2021-12-12 12:45 | 0.38488 | 1.4962 | 0.60029 | 1.8822 | 0.076626 | 0.14266 | 0.053707 | 0.18173
2021-12-12 13:00 | 0.38284 | 1.4719 | 0.5717 | 1.9572 | 0.065534 | 0.1643 | 0.04935 | 0.17184
2021-12-12 13:15 | 1.0924 | 1.4554 | 0.5227 | 1.3732 | 0.054443 | 0.18639 | 0.044993 | 0.16196
2021-12-12 13:30 | 2.981 | 1.4222 | 0.44511 | 1.4017 | 0.043351 | 0.1974 | 0.040636 | 0.15207
2021-12-12 13:45 | 1.5926 | 1.2143 | 0.53087 | 0.98298 | 0.034215 | 0.17194 | 0.036783 | 0.14701
2021-12-12 14:00 | 0.70646 | 1.17 | 0.97189 | 0.98691 | 0.035375 | 0.16816 | 0.035428 | 0.16029
2021-12-12 14:15 | 0.77997 | 1.2142 | 1.4497 | 0.94827 | 0.036535 | 0.16404 | 0.034073 | 0.17358
2021-12-12 14:30 | 0.64521 | 1.0829 | 0.70646 | 0.40938 | 0.037695 | 0.15558 | 0.032718 | 0.18686
2021-12-12 14:45 | 0.53495 | 1.0604 | 0.5227 | 0.39304 | 0.03713 | 0.14469 | 0.030331 | 0.1901
2021-12-12 15:00 | 0.42061 | 1.0294 | 0.5227 | 0.38298 | 0.027464 | 0.11799 | 0.022811 | 0.15493
2021-12-12 15:15 | 0.33281 | 0.9526 | 0.50636 | 0.34871 | 0.017797 | 0.080405 | 0.015292 | 0.11977
2021-12-12 15:30 | 0.3665 | 0.94408 | 0.55945 | 0.37131 | 0.00813 | 0.081731 | 0.007773 | 0.0846
2021-12-12 15:45 | 0.23889 | 0.95622 | 0.49411 | 0.36723 | 0 | 0.05674 | 0.001447 | 0.053792
2021-12-12 16:00 | 0.21745 | 0.96541 | 0.4737 | 0.35571 | 0 | 0.037653 | 0.001069 | 0.039635
2021-12-12 16:15 | 0.41653 | 0.84815 | 0.5472 | 0.44001 | 0 | 0.028533 | 0.000692 | 0.025478
2021-12-12 16:30 | 0.45736 | 0.79849 | 0.60437 | 0.39567 | 0 | 0.011481 | 0.000315 | 0.011321
2021-12-12 16:45 | 0.40427 | 0.83145 | 0.60437 | 0.39932 | 0 | 0 | 0 | 0
2021-12-12 17:00 | 0.35833 | 0.84465 | 0.51862 | 0.42819 | 0 | 0 | 0 | 0
2021-12-12 17:15 | 0.37161 | 0.87769 | 0.4737 | 0.48595 | 0 | 0 | 0 | 0
2021-12-12 17:30 | 0.37058 | 1.1331 | 0.46144 | 0.71098 | 0 | 0 | 0 | 0
2021-12-12 17:45 | 0.41653 | 1.3249 | 0.5962 | 1.2849 | 0 | 0 | 0 | 0
2021-12-12 18:00 | 0.44103 | 1.3249 | 0.60845 | 1.316 | 0 | 0 | 0 | 0
2021-12-12 18:15 | 0.36344 | 1.3186 | 0.56354 | 1.5307 | 0 | 0 | 0 | 0
2021-12-12 18:30 | 0.29708 | 1.4526 | 0.60845 | 1.6256 | 0 | 0 | 0 | 0
2021-12-12 18:45 | 0.29606 | 1.2436 | 0.61662 | 1.4069 | 0 | 0 | 0 | 0
2021-12-12 19:00 | 0.29912 | 1.6415 | 2.9606 | 2.7162 | 0 | 0 | 0 | 0
2021-12-12 19:15 | 0.2981 | 2.172 | 3.8896 | 4.0482 | 0 | 0 | 0 | 0
2021-12-12 19:30 | 0.45328 | 2.172 | 3.8182 | 3.9117 | 0 | 0 | 0 | 0
2021-12-12 19:45 | 0.37977 | 2.3778 | 3.859 | 3.7567 | 0 | 0 | 0 | 0
2021-12-12 20:00 | 0.35119 | 1.598 | 1.7968 | 1.674 | 0 | 0 | 0 | 0
2021-12-12 20:15 | 0.37977 | 1.2311 | 0.91064 | 1.1288 | 0 | 0 | 0 | 0
2021-12-12 20:30 | 0.57987 | 1.0993 | 0.75955 | 1.0588 | 0 | 0 | 0 | 0
2021-12-12 20:45 | 1.6743 | 1.058 | 1.1128 | 1.1128 | 0 | 0 | 0 | 0
2021-12-12 21:00 | 3.0321 | 1.0738 | 0.67379 | 0.99698 | 0 | 0 | 0 | 0
2021-12-12 21:15 | 2.93 | 0.90243 | 0.62887 | 0.621 | 0 | 0 | 0 | 0
2021-12-12 21:30 | 3.6038 | 0.85246 | 0.63704 | 0.71259 | 0 | 0 | 0 | 0
2021-12-12 21:45 | 2.0826 | 0.84847 | 0.95147 | 0.64404 | 0 | 0 | 0 | 0
2021-12-12 22:00 | 0.66971 | 0.97022 | 0.92289 | 0.57316 | 0 | 0 | 0 | 0
2021-12-12 22:15 | 0.64112 | 0.59536 | 0.55945 | 0.52022 | 0 | 0 | 0 | 0
2021-12-12 22:30 | 0.55537 | 0.57948 | 0.47778 | 0.47486 | 0 | 0 | 0 | 0
2021-12-12 22:45 | 0.60437 | 0.58753 | 0.47778 | 0.46188 | 0 | 0 | 0 | 0
2021-12-12 23:00 | 0.63296 | 1.9352 | 3.3894 | 3.0204 | 0 | 0 | 0 | 0
2021-12-12 23:15 | 0.60437 | 2.2654 | 3.6956 | 3.1811 | 0 | 0 | 0 | 0
2021-12-12 23:30 | 0.63704 | 2.2654 | 3.7263 | 3.1721 | 0 | 0 | 0 | 0
2021-12-12 23:45 | 0.53903 | 2.2675 | 3.6446 | 3.1089 | 0 | 0 | 0 | 0
2021-12-13 | 0.53903 | 2.4994 | 3.614 | 3.0394 | 0 | 0 | 0 | 0
2021-12-13 00:15 | 0.50228 | 2.4216 | 3.6344 | 2.8323 | 0 | 0 | 0 | 0
2021-12-13 00:30 | 0.56354 | 2.3091 | 3.6344 | 2.7423 | 0 | 0 | 0 | 0
2021-12-13 00:45 | 0.34506 | 2.3091 | 3.4915 | 2.7026 | 0 | 0 | 0 | 0
2021-12-13 01:00 | 0.2787 | 2.2739 | 3.3996 | 2.6145 | 0 | 0 | 0 | 0
2021-12-13 01:15 | 0.35935 | 2.2671 | 3.42 | 2.574 | 0 | 0 | 0 | 0
2021-12-13 01:30 | 0.28177 | 2.2739 | 3.4302 | 2.6039 | 0 | 0 | 0 | 0
2021-12-13 01:45 | 0.27973 | 2.2227 | 1.8887 | 2.325 | 0 | 0 | 0 | 0
2021-12-13 02:00 | 0.33792 | 2.1892 | 1.123 | 2.2015 | 0 | 0 | 0 | 0
2021-12-13 02:15 | 0.33383 | 2.1892 | 0.84938 | 2.1993 | 0 | 0 | 0 | 0
2021-12-13 02:30 | 0.30627 | 2.1577 | 0.69829 | 2.2222 | 0 | 0 | 0 | 0
2021-12-13 02:45 | 0.29912 | 2.2633 | 0.27156 | 2.1674 | 0 | 0 | 0 | 0
2021-12-13 03:00 | 0.38692 | 2.1892 | 0.68196 | 2.2145 | 0 | 0 | 0 | 0
2021-12-13 03:15 | 0.34302 | 2.1892 | 0.45328 | 2.1372 | 0 | 0 | 0 | 0
2021-12-13 03:30 | 0.32669 | 2.1605 | 0.38692 | 2.1379 | 0 | 0 | 0 | 0
2021-12-13 03:45 | 0.3175 | 2.1493 | 0.38079 | 2.1389 | 0 | 0 | 0 | 0
2021-12-13 04:00 | 0.39509 | 2.1455 | 0.38386 | 1.9312 | 0 | 0 | 0 | 0
2021-12-13 04:15 | 0.26033 | 1.9643 | 0.36752 | 1.5532 | 0 | 0 | 0 | 0
2021-12-13 04:30 | 0.28585 | 2.255 | 0.30831 | 1.3196 | 0 | 0 | 0 | 0
2021-12-13 04:45 | 0.36752 | 2.1211 | 0.30831 | 1.2996 | 0 | 0 | 0 | 0
2021-12-13 05:00 | 0.41653 | 1.9875 | 0.391 | 1.247 | 0 | 0 | 0 | 0
2021-12-13 05:15 | 0.32669 | 2.0032 | 0.31546 | 1.265 | 0 | 0 | 0 | 0
2021-12-13 05:30 | 0.32873 | 2.1019 | 0.30116 | 1.2481 | 0 | 0 | 0 | 0
2021-12-13 05:45 | 0.29096 | 1.867 | 0.3226 | 1.2248 | 0 | 0 | 0 | 0
2021-12-13 06:00 | 0.34098 | 2.1019 | 0.40836 | 1.2381 | 0 | 0 | 0 | 0
2021-12-13 06:15 | 0.43694 | 1.9554 | 0.29708 | 1.2478 | 0 | 0 | 0 | 0
2021-12-13 06:30 | 0.32567 | 1.8154 | 0.29708 | 1.2493 | 0 | 0 | 0 | 0
2021-12-13 06:45 | 0.32873 | 1.835 | 0.29606 | 1.2124 | 0 | 0 | 0 | 0
2021-12-13 07:00 | 0.32465 | 0.60621 | 0.391 | 0.43957 | 0 | 0 | 0 | 0
2021-12-13 07:15 | 0.26135 | 0.66101 | 0.24093 | 0.30729 | 0 | 0 | 0 | 0
2021-12-13 07:30 | 0.43286 | 0.71399 | 0.31239 | 0.35965 | 0 | 0 | 0 | 0
2021-12-13 07:45 | 0.35833 | 0.86765 | 0.30423 | 0.53101 | 0.002559 | 0.014644 | 0.002305 | 0.008962
2021-12-13 08:00 | 0.30627 | 1.6523 | 1.4088 | 2.1016 | 0.019235 | 0.064758 | 0.016564 | 0.055614
2021-12-13 08:15 | 0.30116 | 1.7308 | 1.6743 | 1.6518 | 0.035911 | 0.10502 | 0.030823 | 0.10227
2021-12-13 08:30 | 0.29402 | 1.7308 | 1.7457 | 1.674 | 0.052587 | 0.15644 | 0.045081 | 0.14892
2021-12-13 08:45 | 0.46553 | 1.8757 | 2.5012 | 1.8017 | 0.068295 | 0.19035 | 0.05716 | 0.18115
2021-12-13 09:00 | 1.0924 | 1.6369 | 2.2664 | 1.3566 | 0.078646 | 0.16589 | 0.057902 | 0.15299
2021-12-13 09:15 | 0.90247 | 1.6564 | 2.491 | 1.352 | 0.088998 | 0.14868 | 0.058645 | 0.12483
2021-12-13 09:30 | 0.60845 | 1.7925 | 1.4599 | 1.4049 | 0.09935 | 0.12907 | 0.059387 | 0.096666
2021-12-13 09:45 | 0.51453 | 1.7464 | 2.8585 | 1.5783 | 0.10794 | 0.10752 | 0.061111 | 0.076467
2021-12-13 10:00 | 0.49411 | 1.6267 | 1.6028 | 1.2822 | 0.10676 | 0.086786 | 0.067948 | 0.089562
2021-12-13 10:15 | 1.0515 | 1.6437 | 0.75138 | 1.4823 | 0.10558 | 0.084859 | 0.074784 | 0.10266
2021-12-13 10:30 | 1.7253 | 1.5306 | 0.8698 | 1.2117 | 0.1044 | 0.089031 | 0.081621 | 0.11575
2021-12-13 10:45 | 0.69421 | 1.5476 | 0.47778 | 1.0559 | 0.10293 | 0.092573 | 0.089846 | 0.12793
2021-12-13 11:00 | 1.0617 | 1.4776 | 0.44103 | 1.0495 | 0.099865 | 0.10449 | 0.10533 | 0.13529
2021-12-13 11:15 | 0.89022 | 1.565 | 0.3226 | 1.235 | 0.096798 | 0.12005 | 0.1208 | 0.14265
2021-12-13 11:30 | 0.70646 | 1.5386 | 0.27666 | 1.0709 | 0.093731 | 0.13284 | 0.13628 | 0.15001
2021-12-13 11:45 | 0.60845 | 1.6219 | 0.27564 | 1.3468 | 0.090027 | 0.12607 | 0.14644 | 0.15525
2021-12-13 12:00 | 0.4737 | 1.709 | 0.2491 | 1.4332 | 0.082775 | 0.12634 | 0.12872 | 0.1524
2021-12-13 12:15 | 0.45328 | 1.6177 | 0.36956 | 1.363 | 0.075523 | 0.11948 | 0.111 | 0.14954
2021-12-13 12:30 | 0.40019 | 1.5059 | 0.40632 | 1.1012 | 0.068272 | 0.11662 | 0.093284 | 0.14668
2021-12-13 12:45 | 0.37467 | 1.5977 | 0.38488 | 1.4209 | 0.061421 | 0.11286 | 0.076626 | 0.14446
2021-12-13 13:00 | 0.35119 | 1.514 | 0.38284 | 1.4883 | 0.056811 | 0.11986 | 0.065534 | 0.14365
2021-12-13 13:15 | 0.53903 | 1.2308 | 1.0924 | 0.77559 | 0.052201 | 0.12488 | 0.054443 | 0.14284
2021-12-13 13:30 | 0.5227 | 1.2567 | 2.981 | 0.90539 | 0.047592 | 0.13614 | 0.043351 | 0.14203
2021-12-13 13:45 | 2.3787 | 1.3607 | 1.5926 | 0.65483 | 0.04273 | 0.14237 | 0.034215 | 0.14204
2021-12-13 14:00 | 0.85347 | 1.3084 | 0.70646 | 0.58614 | 0.036453 | 0.13924 | 0.035375 | 0.14647
2021-12-13 14:15 | 0.59212 | 1.2952 | 0.77997 | 0.61925 | 0.030176 | 0.18623 | 0.036535 | 0.15091
2021-12-13 14:30 | 1.5518 | 1.2171 | 0.64521 | 0.45153 | 0.023899 | 0.18194 | 0.037695 | 0.15534
2021-12-13 14:45 | 0.46553 | 1.2171 | 0.53495 | 0.41142 | 0.017869 | 0.14822 | 0.03713 | 0.1526
2021-12-13 15:00 | 0.83305 | 1.234 | 0.42061 | 0.39946 | 0.013227 | 0.098531 | 0.027464 | 0.12142
2021-12-13 15:15 | 0.55537 | 1.1692 | 0.33281 | 0.35177 | 0.008585 | 0.082779 | 0.017797 | 0.090249
2021-12-13 15:30 | 1.2659 | 1.1032 | 0.3665 | 0.39654 | 0.003943 | 0.07304 | 0.00813 | 0.059076
2021-12-13 15:45 | 2.8789 | 1.1129 | 0.23889 | 0.36271 | 0 | 0.068046 | 0 | 0.032534
2021-12-13 16:00 | 0.80038 | 1.1221 | 0.21745 | 0.36067 | 0 | 0.048681 | 0 | 0.023995
2021-12-13 16:15 | 0.83713 | 1.0072 | 0.41653 | 0.4737 | 0 | 0.023361 | 0 | 0.015456
2021-12-13 16:30 | 0.7718 | 1.0121 | 0.45736 | 0.42703 | 0 | 0.007803 | 0 | 0.006918
2021-12-13 16:45 | 0.68196 | 1.1722 | 0.40427 | 0.41959 | 0 | 0 | 0 | 0
2021-12-13 17:00 | 0.61662 | 1.0768 | 0.35833 | 0.44249 | 0 | 0 | 0 | 0
2021-12-13 17:15 | 3.2669 | 1.1255 | 0.37161 | 0.50374 | 0 | 0 | 0 | 0
2021-12-13 17:30 | 1.4803 | 1.1584 | 0.37058 | 0.72557 | 0 | 0 | 0 | 0
2021-12-13 17:45 | 0.49003 | 1.5498 | 0.41653 | 1.3039 | 0 | 0 | 0 | 0
2021-12-13 18:00 | 0.67788 | 1.5976 | 0.44103 | 1.3382 | 0 | 0 | 0 | 0
2021-12-13 18:15 | 2.9912 | 1.6876 | 0.36344 | 1.5409 | 0 | 0 | 0 | 0
2021-12-13 18:30 | 0.60029 | 1.8457 | 0.29708 | 1.6108 | 0 | 0 | 0 | 0
2021-12-13 18:45 | 0.67788 | 1.5672 | 0.29606 | 1.4053 | 0 | 0 | 0 | 0
2021-12-13 19:00 | 0.69013 | 1.8296 | 0.29912 | 2.5139 | 0 | 0 | 0 | 0
2021-12-13 19:15 | 0.65337 | 2.3171 | 0.2981 | 3.3115 | 0 | 0 | 0 | 0
2021-12-13 19:30 | 0.64112 | 2.243 | 0.45328 | 3.2033 | 0 | 0 | 0 | 0
2021-12-13 19:45 | 0.69421 | 2.3529 | 0.37977 | 3.049 | 0 | 0 | 0 | 0
2021-12-13 20:00 | 0.68604 | 1.4909 | 0.35119 | 1.4135 | 0 | 0 | 0 | 0
2021-12-13 20:15 | 0.58804 | 1.1314 | 0.37977 | 0.82138 | 0 | 0 | 0 | 0
2021-12-13 20:30 | 0.46144 | 1.0401 | 0.57987 | 0.83539 | 0 | 0 | 0 | 0
2021-12-13 20:45 | 0.64929 | 1.153 | 1.6743 | 1.0807 | 0 | 0 | 0 | 0
2021-12-13 21:00 | 2.0214 | 1.3548 | 3.0321 | 1.3333 | 0 | 0 | 0 | 0
2021-12-13 21:15 | 2.4297 | 0.95612 | 2.93 | 0.94039 | 0 | 0 | 0 | 0
2021-12-13 21:30 | 2.5114 | 1.0552 | 3.6038 | 1.0962 | 0 | 0 | 0 | 0
2021-12-13 21:45 | 2.1337 | 0.81334 | 2.0826 | 0.82372 | 0 | 0 | 0 | 0
2021-12-13 22:00 | 1.7355 | 0.89158 | 0.66971 | 0.57549 | 0 | 0 | 0 | 0
2021-12-13 22:15 | 0.60845 | 0.6091 | 0.64112 | 0.52314 | 0 | 0 | 0 | 0
2021-12-13 22:30 | 0.53087 | 0.59099 | 0.55537 | 0.4807 | 0 | 0 | 0 | 0
2021-12-13 22:45 | 0.4737 | 0.64511 | 0.60437 | 0.47472 | 0 | 0 | 0 | 0
2021-12-13 23:00 | 0.47778 | 2.1301 | 0.63296 | 2.6281 | 0 | 0 | 0 | 0
2021-12-13 23:15 | 0.48186 | 2.374 | 0.60437 | 2.7512 | 0 | 0 | 0 | 0
2021-12-13 23:30 | 0.45328 | 2.374 | 0.63704 | 2.7468 | 0 | 0 | 0 | 0
2021-12-13 23:45 | 0.41653 | 2.374 | 0.53903 | 2.6667 | 0 | 0 | 0 | 0
2021-12-14 | 0.40121 | 1.8543 | 0.53903 | 2.5957 | 0 | 0 | 0 | 0
2021-12-14 00:15 | 0.33485 | 1.2775 | 0.50228 | 2.4052 | 0 | 0 | 0 | 0
2021-12-14 00:30 | 0.30014 | 1.2775 | 0.56354 | 2.3225 | 0 | 0 | 0 | 0
2021-12-14 00:45 | 0.3369 | 1.25 | 0.34506 | 2.2473 | 0 | 0 | 0 | 0
2021-12-14 01:00 | 0.29402 | 1.197 | 0.2787 | 2.1512 | 0 | 0 | 0 | 0
2021-12-14 01:15 | 0.28075 | 0.94483 | 0.35935 | 2.1149 | 0 | 0 | 0 | 0
2021-12-14 01:30 | 0.24399 | 1.2437 | 0.28177 | 2.138 | 0 | 0 | 0 | 0
2021-12-14 01:45 | 0.24297 | 0.93947 | 0.27973 | 1.8764 | 0 | 0 | 0 | 0
2021-12-14 02:00 | 0.27462 | 0.98076 | 0.33792 | 1.7656 | 0 | 0 | 0 | 0
2021-12-14 02:15 | 0.39713 | 0.98076 | 0.33383 | 1.754 | 0 | 0 | 0 | 0
2021-12-14 02:30 | 0.42469 | 0.88214 | 0.30627 | 1.7715 | 0 | 0 | 0 | 0
2021-12-14 02:45 | 0.37671 | 1.0423 | 0.29912 | 1.7026 | 0 | 0 | 0 | 0
2021-12-14 03:00 | 0.30729 | 0.97815 | 0.38692 | 1.7739 | 0 | 0 | 0 | 0
2021-12-14 03:15 | 0.26441 | 0.88214 | 0.34302 | 1.6961 | 0 | 0 | 0 | 0
2021-12-14 03:30 | 0.27258 | 0.88214 | 0.32669 | 1.6916 | 0 | 0 | 0 | 0
2021-12-14 03:45 | 0.26135 | 0.88214 | 0.3175 | 1.6913 | 0 | 0 | 0 | 0
2021-12-14 04:00 | 0.30423 | 0.96891 | 0.39509 | 1.4831 | 0 | 0 | 0 | 0
2021-12-14 04:15 | 0.43286 | 0.66239 | 0.26033 | 1.08 | 0 | 0 | 0 | 0
2021-12-14 04:30 | 0.37569 | 0.6567 | 0.28585 | 0.86455 | 0 | 0 | 0 | 0
2021-12-14 04:45 | 0.27564 | 0.59386 | 0.36752 | 0.85916 | 0 | 0 | 0 | 0
2021-12-14 05:00 | 0.28075 | 0.63144 | 0.41653 | 0.81351 | 0 | 0 | 0 | 0
2021-12-14 05:15 | 0.24297 | 0.60845 | 0.32669 | 0.79688 | 0 | 0 | 0 | 0
2021-12-14 05:30 | 0.29504 | 0.62865 | 0.32873 | 0.79338 | 0 | 0 | 0 | 0
2021-12-14 05:45 | 0.42878 | 0.62865 | 0.29096 | 0.76757 | 0 | 0 | 0 | 0
2021-12-14 06:00 | 0.27462 | 0.59072 | 0.34098 | 0.78799 | 0 | 0 | 0 | 0
2021-12-14 06:15 | 0.26237 | 0.66133 | 0.43694 | 0.79688 | 0 | 0 | 0 | 0
2021-12-14 06:30 | 0.24195 | 0.62714 | 0.32567 | 0.77953 | 0 | 0 | 0 | 0
2021-12-14 06:45 | 0.31137 | 0.62734 | 0.32873 | 0.76203 | 0 | 0 | 0 | 0
2021-12-14 07:00 | 0.34915 | 0.59649 | 0.32465 | 0.40777 | 0 | 0 | 0 | 0
2021-12-14 07:15 | 0.29198 | 0.57581 | 0.26135 | 0.30233 | 0 | 0 | 0 | 0
2021-12-14 07:30 | 0.30933 | 0.58288 | 0.43286 | 0.36388 | 0 | 0 | 0 | 0
2021-12-14 07:45 | 0.5717 | 0.72477 | 0.35833 | 0.52737 | 0.001392 | 0.005819 | 0.002559 | 0.0077
2021-12-14 08:00 | 0.70646 | 1.4112 | 0.30627 | 1.6786 | 0.010976 | 0.032888 | 0.019235 | 0.049018
2021-12-14 08:15 | 1.1026 | 1.1307 | 0.30116 | 1.199 | 0.02056 | 0.066955 | 0.035911 | 0.090336
2021-12-14 08:30 | 0.80855 | 1.1144 | 0.29402 | 1.207 | 0.030144 | 0.092502 | 0.052587 | 0.13165
2021-12-14 08:45 | 0.47778 | 1.3096 | 0.46553 | 1.3636 | 0.046981 | 0.12001 | 0.068295 | 0.16104
2021-12-14 09:00 | 0.50636 | 1.1457 | 1.0924 | 1.0241 | 0.10662 | 0.10369 | 0.078646 | 0.1391
2021-12-14 09:15 | 0.4737 | 1.1279 | 0.90247 | 0.96898 | 0.16627 | 0.077895 | 0.088998 | 0.11716
2021-12-14 09:30 | 0.51045 | 1.1474 | 0.60845 | 0.85055 | 0.22591 | 0.054874 | 0.09935 | 0.095222
2021-12-14 09:45 | 0.46144 | 1.1879 | 0.51453 | 1.0932 | 0.27024 | 0.046326 | 0.10794 | 0.079155
2021-12-14 10:00 | 0.40223 | 1.0833 | 0.49411 | 0.79717 | 0.22396 | 0.065297 | 0.10676 | 0.088082
2021-12-14 10:15 | 0.41653 | 1.1609 | 1.0515 | 1.074 | 0.17767 | 0.074946 | 0.10558 | 0.09701
2021-12-14 10:30 | 0.42469 | 1.1251 | 1.7253 | 0.89226 | 0.13139 | 0.083445 | 0.1044 | 0.10594
2021-12-14 10:45 | 0.50636 | 0.9894 | 0.69421 | 0.59212 | 0.098864 | 0.092697 | 0.10293 | 0.11288
2021-12-14 11:00 | 0.47778 | 1.1373 | 1.0617 | 0.66737 | 0.14799 | 0.10537 | 0.099865 | 0.11093
2021-12-14 11:15 | 0.48595 | 1.0931 | 0.89022 | 0.86193 | 0.19713 | 0.1347 | 0.096798 | 0.10898
2021-12-14 11:30 | 0.51862 | 1.0603 | 0.70646 | 0.66869 | 0.24626 | 0.14871 | 0.093731 | 0.10702
2021-12-14 11:45 | 0.61254 | 1.1753 | 0.60845 | 0.62975 | 0.28187 | 0.16 | 0.090027 | 0.10555
2021-12-14 12:00 | 0.5227 | 1.0168 | 0.4737 | 0.91006 | 0.23707 | 0.1499 | 0.082775 | 0.1056
2021-12-14 12:15 | 0.33894 | 1.1368 | 0.45328 | 0.76626 | 0.19227 | 0.13796 | 0.075523 | 0.10566
2021-12-14 12:30 | 0.3471 | 0.98263 | 0.40019 | 0.47297 | 0.14746 | 0.10737 | 0.068272 | 0.10572
2021-12-14 12:45 | 0.32465 | 1.1041 | 0.37467 | 0.84822 | 0.10701 | 0.10368 | 0.061421 | 0.10416
2021-12-14 13:00 | 0.32873 | 1.1427 | 0.35119 | 1.0864 | 0.092528 | 0.12515 | 0.056811 | 0.095589
2021-12-14 13:15 | 0.91881 | 0.99083 | 0.53903 | 0.54049 | 0.078044 | 0.137 | 0.052201 | 0.087022
2021-12-14 13:30 | 0.40734 | 1.0341 | 0.5227 | 0.86455 | 0.06356 | 0.15073 | 0.047592 | 0.078455
2021-12-14 13:45 | 0.32056 | 1.114 | 2.3787 | 0.95322 | 0.050016 | 0.16201 | 0.04273 | 0.072509
2021-12-14 14:00 | 0.33281 | 1.1446 | 0.85347 | 0.65571 | 0.042094 | 0.15845 | 0.036453 | 0.077709
2021-12-14 14:15 | 0.30218 | 1.1263 | 0.59212 | 0.65264 | 0.034172 | 0.15488 | 0.030176 | 0.082908
2021-12-14 14:30 | 0.30116 | 1.0782 | 1.5518 | 0.63237 | 0.02625 | 0.14666 | 0.023899 | 0.088107
2021-12-14 14:45 | 0.36344 | 0.90558 | 0.46553 | 0.44365 | 0.018765 | 0.12492 | 0.017869 | 0.089331
2021-12-14 15:00 | 0.42878 | 0.88439 | 0.83305 | 0.48405 | 0.013901 | 0.090664 | 0.013227 | 0.07432
2021-12-14 15:15 | 0.35935 | 0.85238 | 0.55537 | 0.3964 | 0.009036 | 0.065581 | 0.008585 | 0.05931
2021-12-14 15:30 | 0.32975 | 0.98543 | 1.2659 | 0.54239 | 0.004171 | 0.053973 | 0.003943 | 0.044299
2021-12-14 15:45 | 0.33485 | 1.0322 | 2.8789 | 0.73913 | 0 | 0.011514 | 0 | 0.030621
2021-12-14 16:00 | 0.33179 | 0.86813 | 0.80038 | 0.43111 | 0 | 0.007157 | 0 | 0.022586
2021-12-14 16:15 | 0.30423 | 0.91614 | 0.83713 | 0.53087 | 0 | 0.007533 | 0 | 0.014552
2021-12-14 16:30 | 0.37569 | 0.90852 | 0.7718 | 0.49003 | 0 | 0.001906 | 0 | 0.006518
2021-12-14 16:45 | 0.39815 | 0.93578 | 0.68196 | 0.47501 | 0 | 0 | 0 | 0
2021-12-14 17:00 | 0.30014 | 0.9644 | 0.61662 | 0.49149 | 0 | 0 | 0 | 0
2021-12-14 17:15 | 0.29708 | 1.0128 | 3.2669 | 0.93237 | 0 | 0 | 0 | 0
2021-12-14 17:30 | 0.2981 | 1.0872 | 1.4803 | 0.74015 | 0 | 0 | 0 | 0
2021-12-14 17:45 | 0.39509 | 1.0314 | 0.49003 | 0.60525 | 0 | 0 | 0 | 0
2021-12-14 18:00 | 0.37671 | 1.0595 | 0.67788 | 0.65819 | 0 | 0 | 0 | 0
2021-12-14 18:15 | 0.35731 | 1.1661 | 2.9912 | 1.0474 | 0 | 0 | 0 | 0
2021-12-14 18:30 | 0.41244 | 1.0977 | 0.60029 | 0.7594 | 0 | 0 | 0 | 0
2021-12-14 18:45 | 0.4737 | 1.1495 | 0.67788 | 0.94798 | 0 | 0 | 0 | 0
2021-12-14 19:00 | 0.50228 | 1.8772 | 0.69013 | 2.0714 | 0 | 0 | 0 | 0
2021-12-14 19:15 | 0.64521 | 2.0825 | 0.65337 | 2.8565 | 0 | 0 | 0 | 0
2021-12-14 19:30 | 0.65337 | 2.1532 | 0.64112 | 2.764 | 0 | 0 | 0 | 0
2021-12-14 19:45 | 1.8274 | 1.6172 | 0.69421 | 2.5394 | 0 | 0 | 0 | 0
2021-12-14 20:00 | 1.1638 | 1.0813 | 0.68604 | 0.97773 | 0 | 0 | 0 | 0
2021-12-14 20:15 | 1.2047 | 1.0459 | 0.58804 | 0.69829 | 0 | 0 | 0 | 0
2021-12-14 20:30 | 1.5313 | 0.96449 | 0.46144 | 0.72046 | 0 | 0 | 0 | 0
2021-12-14 20:45 | 0.72688 | 0.83325 | 0.64929 | 0.91093 | 0 | 0 | 0 | 0
2021-12-14 21:00 | 0.69829 | 1.3718 | 2.0214 | 1.4949 | 0 | 0 | 0 | 0
2021-12-14 21:15 | 0.67379 | 1.0915 | 2.4297 | 1.2134 | 0 | 0 | 0 | 0
2021-12-14 21:30 | 0.82897 | 1.2414 | 2.5114 | 1.3762 | 0 | 0 | 0 | 0
2021-12-14 21:45 | 0.88205 | 0.93502 | 2.1337 | 1.0439 | 0 | 0 | 0 | 0
2021-12-14 22:00 | 0.55128 | 0.8566 | 1.7355 | 0.747 | 0 | 0 | 0 | 0
2021-12-14 22:15 | 0.51045 | 0.66186 | 0.60845 | 0.52955 | 0 | 0 | 0 | 0
2021-12-14 22:30 | 0.43286 | 0.59165 | 0.53087 | 0.47661 | 0 | 0 | 0 | 0
2021-12-14 22:45 | 0.36854 | 0.57535 | 0.4737 | 0.49353 | 0 | 0 | 0 | 0
2021-12-14 23:00 | 0.38998 | 1.3713 | 0.47778 | 2.2311 | 0 | 0 | 0 | 0
2021-12-14 23:15 | 0.44919 | 1.2927 | 0.48186 | 2.3198 | 0 | 0 | 0 | 0
2021-12-14 23:30 | 0.4982 | 1.1687 | 0.45328 | 2.3113 | 0 | 0 | 0 | 0
2021-12-14 23:45 | 0.51045 | 0.97466 | 0.41653 | 2.2289 | 0 | 0 | 0 | 0
2021-12-15 | 0.46144 | 0.88664 | 0.40121 | 2.1922 | 0 | 0 | 0 | 0
2021-12-15 00:15 | 0.36548 | 0.88664 | 0.33485 | 2.1891 | 0 | 0 | 0 | 0
2021-12-15 00:30 | 0.34506 | 0.96077 | 0.30014 | 2.2167 | 0 | 0 | 0 | 0
2021-12-15 00:45 | 0.47778 | 0.94467 | 0.3369 | 2.1513 | 0 | 0 | 0 | 0
2021-12-15 01:00 | 0.39611 | 0.8682 | 0.29402 | 2.1004 | 0 | 0 | 0 | 0
2021-12-15 01:15 | 0.28483 | 0.92253 | 0.28075 | 2.1055 | 0 | 0 | 0 | 0
2021-12-15 01:30 | 0.28585 | 0.8942 | 0.24399 | 2.1105 | 0 | 0 | 0 | 0
2021-12-15 01:45 | 0.2787 | 0.83291 | 0.24297 | 1.8586 | 0 | 0 | 0 | 0
2021-12-15 02:00 | 0.28789 | 0.7315 | 0.27462 | 1.7619 | 0 | 0 | 0 | 0
2021-12-15 02:15 | 0.38284 | 0.73465 | 0.39713 | 1.7653 | 0 | 0 | 0 | 0
2021-12-15 02:30 | 0.33077 | 0.85504 | 0.42469 | 1.7877 | 0 | 0 | 0 | 0
2021-12-15 02:45 | 0.34608 | 0.74196 | 0.37671 | 1.6934 | 0 | 0 | 0 | 0
2021-12-15 03:00 | 0.32465 | 0.71083 | 0.30729 | 1.7589 | 0 | 0 | 0 | 0
2021-12-15 03:15 | 0.42061 | 0.73465 | 0.26441 | 1.6872 | 0 | 0 | 0 | 0
2021-12-15 03:30 | 0.32873 | 0.73465 | 0.27258 | 1.6862 | 0 | 0 | 0 | 0
2021-12-15 03:45 | 0.29912 | 0.70196 | 0.26135 | 1.681 | 0 | 0 | 0 | 0
2021-12-15 04:00 | 0.3471 | 0.66383 | 0.30423 | 1.4802 | 0 | 0 | 0 | 0
2021-12-15 04:15 | 0.32771 | 0.62121 | 0.43286 | 1.0925 | 0 | 0 | 0 | 0
2021-12-15 04:30 | 0.33792 | 0.58214 | 0.37569 | 0.85464 | 0 | 0 | 0 | 0
2021-12-15 04:45 | 0.28993 | 0.59986 | 0.27564 | 0.85303 | 0 | 0 | 0 | 0
2021-12-15 05:00 | 0.29198 | 0.59453 | 0.28075 | 0.80768 | 0 | 0 | 0 | 0
2021-12-15 05:15 | 0.4053 | 0.60572 | 0.24297 | 0.78784 | 0 | 0 | 0 | 0
2021-12-15 05:30 | 0.45736 | 0.59333 | 0.29504 | 0.77924 | 0 | 0 | 0 | 0
2021-12-15 05:45 | 0.30525 | 0.588 | 0.42878 | 0.77165 | 0 | 0 | 0 | 0
2021-12-15 06:00 | 0.29708 | 0.588 | 0.27462 | 0.78011 | 0 | 0 | 0 | 0
2021-12-15 06:15 | 0.27768 | 0.60822 | 0.26237 | 0.78274 | 0 | 0 | 0 | 0
2021-12-15 06:30 | 0.37977 | 0.66748 | 0.24195 | 0.76815 | 0 | 0 | 0 | 0
2021-12-15 06:45 | 0.42878 | 0.5905 | 0.31137 | 0.76071 | 0 | 0 | 0 | 0
2021-12-15 07:00 | 0.34608 | 0.4984 | 0.34915 | 0.3929 | 0 | 0 | 0 | 0
2021-12-15 07:15 | 0.33077 | 0.51551 | 0.29198 | 0.28162 | 0 | 0 | 0 | 0
2021-12-15 07:30 | 0.40325 | 0.50851 | 0.30933 | 0.3579 | 0 | 0 | 0 | 0
2021-12-15 07:45 | 0.95964 | 0.68866 | 0.5717 | 0.55362 | 0.00018 | 0.006877 | 0.001392 | 0.004884
2021-12-15 08:00 | 0.91881 | 1.037 | 0.70646 | 1.5462 | 0.001498 | 0.041124 | 0.010976 | 0.032701
2021-12-15 08:15 | 0.98006 | 0.72907 | 1.1026 | 1.2637 | 0.002815 | 0.075783 | 0.02056 | 0.060518
2021-12-15 08:30 | 0.62887 | 1.0444 | 0.80855 | 1.228 | 0.004133 | 0.10186 | 0.030144 | 0.088335
2021-12-15 08:45 | 0.71871 | 1.0449 | 0.47778 | 1.3438 | 0.00694 | 0.10633 | 0.046981 | 0.11064
2021-12-15 09:00 | 0.68604 | 1.089 | 0.50636 | 1.0078 | 0.019159 | 0.11478 | 0.10662 | 0.10897
2021-12-15 09:15 | 0.71871 | 0.88537 | 0.4737 | 0.94506 | 0.031378 | 0.097845 | 0.16627 | 0.10729
2021-12-15 09:30 | 0.5962 | 0.8673 | 0.51045 | 0.70034 | 0.043597 | 0.1176 | 0.22591 | 0.10562
2021-12-15 09:45 | 0.60029 | 0.8534 | 0.46144 | 0.86747 | 0.055267 | 0.14462 | 0.27024 | 0.10483
2021-12-15 10:00 | 0.64112 | 0.86781 | 0.40223 | 0.75546 | 0.063461 | 0.11576 | 0.22396 | 0.10507
2021-12-15 10:15 | 0.72279 | 0.86923 | 0.41653 | 1.0273 | 0.071656 | 0.1031 | 0.17767 | 0.10532
2021-12-15 10:30 | 0.7473 | 0.92357 | 0.42469 | 0.81409 | 0.07985 | 0.11479 | 0.13139 | 0.10555
2021-12-15 10:45 | 0.72279 | 0.82963 | 0.50636 | 0.56995 | 0.084917 | 0.11526 | 0.098864 | 0.10679
2021-12-15 11:00 | 0.53903 | 0.8936 | 0.47778 | 0.66446 | 0.070113 | 0.14131 | 0.14799 | 0.11484
2021-12-15 11:15 | 0.43286 | 1.1193 | 0.48595 | 0.85143 | 0.05531 | 0.17061 | 0.19713 | 0.12288
2021-12-15 11:30 | 0.64521 | 1.1193 | 0.51862 | 0.66869 | 0.040506 | 0.13602 | 0.24626 | 0.13092
2021-12-15 11:45 | 0.44103 | 1.0007 | 0.61254 | 0.62566 | 0.027905 | 0.15223 | 0.28187 | 0.1371
2021-12-15 12:00 | 0.45736 | 1.1526 | 0.5227 | 0.90539 | 0.029345 | 0.13691 | 0.23707 | 0.1317
2021-12-15 12:15 | 0.50636 | 0.92292 | 0.33894 | 0.74409 | 0.030785 | 0.15718 | 0.19227 | 0.12629
2021-12-15 12:30 | 0.5472 | 0.78057 | 0.3471 | 0.45838 | 0.032225 | 0.16096 | 0.14746 | 0.12089
2021-12-15 12:45 | 0.46144 | 1.1526 | 0.32465 | 0.82343 | 0.032861 | 0.13803 | 0.10701 | 0.1142
2021-12-15 13:00 | 0.46961 | 1.031 | 0.32873 | 1.0663 | 0.028359 | 0.11569 | 0.092528 | 0.1031
2021-12-15 13:15 | 0.45328 | 0.96633 | 0.91881 | 0.61618 | 0.023857 | 0.13031 | 0.078044 | 0.091996
2021-12-15 13:30 | 0.75546 | 0.90019 | 0.40734 | 0.88278 | 0.019355 | 0.14045 | 0.06356 | 0.080894
2021-12-15 13:45 | 0.55128 | 0.80526 | 0.32056 | 0.90568 | 0.015595 | 0.14212 | 0.050016 | 0.070732
2021-12-15 14:00 | 0.61662 | 1.0682 | 0.33281 | 0.63441 | 0.016592 | 0.139 | 0.042094 | 0.065295
2021-12-15 14:15 | 0.46144 | 0.843 | 0.30218 | 0.63106 | 0.017589 | 0.13585 | 0.034172 | 0.059857
2021-12-15 14:30 | 0.42878 | 0.88839 | 0.30116 | 0.61881 | 0.018587 | 0.12926 | 0.02625 | 0.054419
2021-12-15 14:45 | 0.43694 | 0.76875 | 0.36344 | 0.43986 | 0.018811 | 0.12043 | 0.018765 | 0.048784
2021-12-15 15:00 | 0.43694 | 0.73451 | 0.42878 | 0.49134 | 0.014067 | 0.10254 | 0.013901 | 0.042117
2021-12-15 15:15 | 0.41653 | 0.69085 | 0.35935 | 0.39713 | 0.009322 | 0.069985 | 0.009036 | 0.03545
2021-12-15 15:30 | 0.32873 | 0.75946 | 0.32975 | 0.52241 | 0.004578 | 0.056099 | 0.004171 | 0.028783
2021-12-15 15:45 | 0.30627 | 0.84872 | 0.33485 | 0.72454 | 0.000454 | 0.052769 | 0 | 0.022183
2021-12-15 16:00 | 0.29198 | 0.78218 | 0.33179 | 0.42528 | 0.000337 | 0.030839 | 0 | 0.016369
2021-12-15 16:15 | 0.39815 | 0.88897 | 0.30423 | 0.52357 | 0.000219 | 0.018811 | 0 | 0.010555
2021-12-15 16:30 | 0.61254 | 0.81358 | 0.37569 | 0.4807 | 0.000102 | 0.006805 | 0 | 0.004741
2021-12-15 16:45 | 0.5227 | 0.84178 | 0.39815 | 0.44671 | 0 | 0 | 0 | 0
2021-12-15 17:00 | 0.46553 | 0.87681 | 0.30014 | 0.43753 | 0 | 0 | 0 | 0
2021-12-15 17:15 | 0.42061 | 0.81105 | 0.29708 | 0.88906 | 0 | 0 | 0 | 0
2021-12-15 17:30 | 0.58804 | 0.87657 | 0.2981 | 0.7209 | 0 | 0 | 0 | 0
2021-12-15 17:45 | 0.73096 | 0.94882 | 0.39509 | 0.58235 | 0 | 0 | 0 | 0
2021-12-15 18:00 | 0.88614 | 0.87354 | 0.37671 | 0.6245 | 0 | 0 | 0 | 0
2021-12-15 18:15 | 0.81263 | 0.78389 | 0.35731 | 1.0081 | 0 | 0 | 0 | 0
2021-12-15 18:30 | 0.71463 | 1.0495 | 0.41244 | 0.71156 | 0 | 0 | 0 | 0
2021-12-15 18:45 | 0.67379 | 0.91327 | 0.4737 | 0.54312 | 0 | 0 | 0 | 0
2021-12-15 19:00 | 1.3067 | 1.1383 | 0.50228 | 1.589 | 0 | 0 | 0 | 0
2021-12-15 19:15 | 3.1954 | 1.4996 | 0.64521 | 2.3887 | 0 | 0 | 0 | 0
2021-12-15 19:30 | 1.1026 | 1.5773 | 0.65337 | 2.309 | 0 | 0 | 0 | 0
2021-12-15 19:45 | 3.6242 | 1.4309 | 1.8274 | 2.4548 | 0 | 0 | 0 | 0
2021-12-15 20:00 | 1.2353 | 1.0174 | 1.1638 | 0.87855 | 0 | 0 | 0 | 0
2021-12-15 20:15 | 0.98006 | 0.9967 | 1.2047 | 0.67496 | 0 | 0 | 0 | 0
2021-12-15 20:30 | 1.0719 | 1.012 | 1.5313 | 0.83539 | 0 | 0 | 0 | 0
2021-12-15 20:45 | 0.8698 | 1.0392 | 0.72688 | 0.95468 | 0 | 0 | 0 | 0
2021-12-15 21:00 | 0.71871 | 1.0531 | 0.69829 | 1.1484 | 0 | 0 | 0 | 0
2021-12-15 21:15 | 0.51453 | 0.87893 | 0.67379 | 1.158 | 0 | 0 | 0 | 0
2021-12-15 21:30 | 0.58804 | 0.80343 | 0.82897 | 1.3639 | 0 | 0 | 0 | 0
2021-12-15 21:45 | 0.87797 | 0.77334 | 0.88205 | 1.0894 | 0 | 0 | 0 | 0
2021-12-15 22:00 | 0.55945 | 0.77665 | 0.55128 | 0.74875 | 0 | 0 | 0 | 0
2021-12-15 22:15 | 0.44511 | 0.62223 | 0.51045 | 0.5208 | 0 | 0 | 0 | 0
2021-12-15 22:30 | 0.54312 | 0.5911 | 0.43286 | 0.45328 | 0 | 0 | 0 | 0
2021-12-15 22:45 | 0.41244 | 0.5911 | 0.36854 | 0.45634 | 0 | 0 | 0 | 0
2021-12-15 23:00 | 3.3179 | 1.4014 | 0.38998 | 2.1103 | 0 | 0 | 0 | 0
2021-12-15 23:15 | 3.4506 | 1.1775 | 0.44919 | 2.2743 | 0 | 0 | 0 | 0
2021-12-15 23:30 | 3.4813 | 1.2164 | 0.4982 | 2.2979 | 0 | 0 | 0 | 0
2021-12-15 23:45 | 3.4506 | 1.1775 | 0.51045 | 2.2483 | 0 | 0 | 0 | 0
2021-12-16 | 3.4404 | 2.2663 | 0.46144 | 2.2158 | 0 | 0 | 0 | 0
2021-12-16 00:15 | 3.4506 | 2.3091 | 0.36548 | 2.1976 | 0 | 0 | 0 | 0
2021-12-16 00:30 | 3.4915 | 2.2562 | 0.34506 | 2.2203 | 0 | 0 | 0 | 0
2021-12-16 00:45 | 3.471 | 2.3091 | 0.47778 | 2.171 | 0 | 0 | 0 | 0
2021-12-16 01:00 | 3.4506 | 2.2158 | 0.39611 | 2.1102 | 0 | 0 | 0 | 0
2021-12-16 01:15 | 3.3792 | 2.2158 | 0.28483 | 2.1054 | 0 | 0 | 0 | 0
2021-12-16 01:30 | 3.3996 | 2.1984 | 0.28585 | 2.1169 | 0 | 0 | 0 | 0
2021-12-16 01:45 | 3.4098 | 2.0128 | 0.2787 | 1.8602 | 0 | 0 | 0 | 0
2021-12-16 02:00 | 3.3587 | 2.0317 | 0.28789 | 1.7664 | 0 | 0 | 0 | 0
2021-12-16 02:15 | 3.471 | 2.0822 | 0.38284 | 1.7651 | 0 | 0 | 0 | 0
2021-12-16 02:30 | 3.3485 | 2.0822 | 0.33077 | 1.7755 | 0 | 0 | 0 | 0
2021-12-16 02:45 | 3.3587 | 2.2104 | 0.34608 | 1.6986 | 0 | 0 | 0 | 0
2021-12-16 03:00 | 3.5017 | 2.0317 | 0.32465 | 1.767 | 0 | 0 | 0 | 0
2021-12-16 03:15 | 3.5425 | 2.1045 | 0.42061 | 1.7094 | 0 | 0 | 0 | 0
2021-12-16 03:30 | 3.3792 | 2.0758 | 0.32873 | 1.6929 | 0 | 0 | 0 | 0
2021-12-16 03:45 | 3.3587 | 1.9812 | 0.29912 | 1.6805 | 0 | 0 | 0 | 0
2021-12-16 04:00 | 3.4098 | 1.6522 | 0.3471 | 1.4907 | 0 | 0 | 0 | 0
2021-12-16 04:15 | 2.052 | 1.3213 | 0.32771 | 1.0894 | 0 | 0 | 0 | 0
2021-12-16 04:30 | 0.94739 | 0.90875 | 0.33792 | 0.8612 | 0 | 0 | 0 | 0
2021-12-16 04:45 | 0.86164 | 0.94404 | 0.28993 | 0.85493 | 0 | 0 | 0 | 0
2021-12-16 05:00 | 0.49411 | 0.88999 | 0.29198 | 0.8103 | 0 | 0 | 0 | 0
2021-12-16 05:15 | 0.26748 | 0.9159 | 0.4053 | 0.80053 | 0 | 0 | 0 | 0
2021-12-16 05:30 | 0.32975 | 0.88938 | 0.45736 | 0.79557 | 0 | 0 | 0 | 0
2021-12-16 05:45 | 0.25318 | 0.88938 | 0.30525 | 0.77821 | 0 | 0 | 0 | 0
2021-12-16 06:00 | 0.23276 | 0.87462 | 0.29708 | 0.78813 | 0 | 0 | 0 | 0
2021-12-16 06:15 | 0.25012 | 0.99051 | 0.27768 | 0.78172 | 0 | 0 | 0 | 0
2021-12-16 06:30 | 0.40836 | 1.0053 | 0.37977 | 0.76232 | 0 | 0 | 0 | 0
2021-12-16 06:45 | 0.3175 | 0.98755 | 0.42878 | 0.77821 | 0 | 0 | 0 | 0
2021-12-16 07:00 | 0.29504 | 0.67888 | 0.34608 | 0.40369 | 0 | 0 | 0 | 0
2021-12-16 07:15 | 0.27564 | 0.65255 | 0.33077 | 0.28964 | 0 | 0 | 0 | 0
2021-12-16 07:30 | 0.33894 | 0.68869 | 0.40325 | 0.36402 | 0 | 0 | 0 | 0
2021-12-16 07:45 | 0.84938 | 0.90723 | 0.95964 | 0.57929 | 0.000907 | 0.009018 | 0.00018 | 0.004779
2021-12-16 08:00 | 1.174 | 1.4118 | 0.91881 | 1.482 | 0.007952 | 0.047903 | 0.001498 | 0.032114
2021-12-16 08:15 | 0.70646 | 1.2833 | 0.98006 | 1.3174 | 0.014996 | 0.08773 | 0.002815 | 0.059449
2021-12-16 08:30 | 0.48186 | 1.1758 | 0.62887 | 1.2152 | 0.02204 | 0.13127 | 0.004133 | 0.086784
2021-12-16 08:45 | 0.60029 | 1.3003 | 0.71871 | 1.3269 | 0.028302 | 0.17963 | 0.00694 | 0.10865
2021-12-16 09:00 | 0.73096 | 1.2775 | 0.68604 | 1.006 | 0.029252 | 0.14667 | 0.019159 | 0.10717
2021-12-16 09:15 | 0.65337 | 1.2775 | 0.71871 | 0.97656 | 0.030202 | 0.11811 | 0.031378 | 0.1057
2021-12-16 09:30 | 0.47778 | 1.1878 | 0.5962 | 0.72659 | 0.031152 | 0.11862 | 0.043597 | 0.10422
2021-12-16 09:45 | 0.55945 | 1.1099 | 0.60029 | 0.88964 | 0.033117 | 0.14528 | 0.055267 | 0.1034
2021-12-16 10:00 | 0.42878 | 1.1517 | 0.64112 | 0.77763 | 0.041991 | 0.11911 | 0.063461 | 0.10243
2021-12-16 10:15 | 0.45328 | 1.2293 | 0.72279 | 1.0541 | 0.050865 | 0.11321 | 0.071656 | 0.10147
2021-12-16 10:30 | 0.46961 | 1.1916 | 0.7473 | 0.83101 | 0.059739 | 0.12581 | 0.07985 | 0.1005
2021-12-16 10:45 | 0.51453 | 1.2558 | 0.72279 | 0.6032 | 0.067283 | 0.1321 | 0.084917 | 0.10022
2021-12-16 11:00 | 0.56762 | 1.2665 | 0.53903 | 0.66562 | 0.065741 | 0.14353 | 0.070113 | 0.10444
2021-12-16 11:15 | 1.8172 | 1.1233 | 0.43286 | 0.55303 | 0.064198 | 0.17373 | 0.05531 | 0.10866
2021-12-16 11:30 | 2.7156 | 1.1233 | 0.64521 | 0.53772 | 0.062656 | 0.20537 | 0.040506 | 0.11289
2021-12-16 11:45 | 0.75955 | 1.2126 | 0.44103 | 0.59941 | 0.062641 | 0.22836 | 0.027905 | 0.11509
2021-12-16 12:00 | 0.64929 | 1.2154 | 0.45736 | 0.86514 | 0.07309 | 0.22053 | 0.029345 | 0.10577
2021-12-16 12:15 | 0.55945 | 1.1873 | 0.50636 | 0.72659 | 0.08354 | 0.20993 | 0.030785 | 0.096441
2021-12-16 12:30 | 0.33996 | 0.97151 | 0.5472 | 0.45897 | 0.093989 | 0.18835 | 0.032225 | 0.087114
2021-12-16 12:45 | 0.46144 | 1.1711 | 0.46144 | 0.65016 | 0.10821 | 0.176 | 0.032861 | 0.077632
2021-12-16 13:00 | 3.0933 | 1.1591 | 0.46961 | 0.6929 | 0.14832 | 0.21281 | 0.028359 | 0.068182
2021-12-16 13:15 | 1.2659 | 1.1993 | 0.45328 | 0.60335 | 0.18843 | 0.23101 | 0.023857 | 0.058733
2021-12-16 13:30 | 0.32362 | 1.2257 | 0.75546 | 0.9207 | 0.22855 | 0.2473 | 0.019355 | 0.049284
2021-12-16 13:45 | 0.22664 | 1.1357 | 0.55128 | 0.9156 | 0.26604 | 0.23695 | 0.015595 | 0.041143
2021-12-16 14:00 | 0.22868 | 1.1397 | 0.61662 | 0.60466 | 0.28542 | 0.23002 | 0.016592 | 0.039498
2021-12-16 14:15 | 0.22664 | 1.1397 | 0.46144 | 0.63937 | 0.3048 | 0.22485 | 0.017589 | 0.037853
2021-12-16 14:30 | 0.23481 | 1.0805 | 0.42878 | 0.61823 | 0.32419 | 0.21094 | 0.018587 | 0.036208
2021-12-16 14:45 | 0.33485 | 0.99404 | 0.43694 | 0.43928 | 0.3339 | 0.19653 | 0.018811 | 0.034214
2021-12-16 15:00 | 0.30014 | 0.98485 | 0.43694 | 0.49076 | 0.2768 | 0.14266 | 0.014067 | 0.030299
2021-12-16 15:15 | 0.23276 | 1.0355 | 0.41653 | 0.40559 | 0.21969 | 0.095657 | 0.009322 | 0.026385
2021-12-16 15:30 | 0.22562 | 0.9588 | 0.32873 | 0.51162 | 0.16259 | 0.079864 | 0.004578 | 0.02247
2021-12-16 15:45 | 0.24297 | 1.189 | 0.30627 | 0.70529 | 0.10913 | 0.034937 | 0.000454 | 0.018255
2021-12-16 16:00 | 0.25318 | 0.98006 | 0.29198 | 0.39815 | 0.080962 | 0.023754 | 0.000337 | 0.013473
2021-12-16 16:15 | 0.30729 | 0.97295 | 0.39815 | 0.48245 | 0.052795 | 0.018348 | 0.000219 | 0.00869
2021-12-16 16:30 | 0.27156 | 0.97057 | 0.61254 | 0.51993 | 0.024627 | 0.005969 | 0.000102 | 0.003908
2021-12-16 16:45 | 0.22562 | 0.97753 | 0.5227 | 0.47151 | 0 | 0 | 0 | 0
2021-12-16 17:00 | 0.22664 | 0.99188 | 0.46553 | 0.44103 | 0 | 0 | 0 | 0
2021-12-16 17:15 | 0.30423 | 1.1554 | 0.42061 | 0.87214 | 0 | 0 | 0 | 0
2021-12-16 17:30 | 0.40121 | 1.0692 | 0.58804 | 0.72557 | 0 | 0 | 0 | 0
2021-12-16 17:45 | 0.28891 | 1.1558 | 0.73096 | 0.61327 | 0 | 0 | 0 | 0
2021-12-16 18:00 | 0.26441 | 1.1558 | 0.88614 | 0.68283 | 0 | 0 | 0 | 0
2021-12-16 18:15 | 0.26033 | 1.0679 | 0.81263 | 1.0378 | 0 | 0 | 0 | 0
2021-12-16 18:30 | 0.29198 | 1.0576 | 0.71463 | 0.71623 | 0 | 0 | 0 | 0
2021-12-16 18:45 | 0.3175 | 0.99815 | 0.67379 | 0.54487 | 0 | 0 | 0 | 0
2021-12-16 19:00 | 0.44103 | 1.3519 | 1.3067 | 1.3264 | 0 | 0 | 0 | 0
2021-12-16 19:15 | 0.34302 | 1.8881 | 3.1954 | 2.2407 | 0 | 0 | 0 | 0
2021-12-16 19:30 | 0.33077 | 1.7389 | 1.1026 | 1.9342 | 0 | 0 | 0 | 0
2021-12-16 19:45 | 0.26135 | 1.9389 | 3.6242 | 2.4359 | 0 | 0 | 0 | 0
2021-12-16 20:00 | 0.32669 | 1.0032 | 1.2353 | 0.91793 | 0 | 0 | 0 | 0
2021-12-16 20:15 | 0.40632 | 0.95431 | 0.98006 | 0.71638 | 0 | 0 | 0 | 0
2021-12-16 20:30 | 0.32056 | 0.86245 | 1.0719 | 0.81059 | 0 | 0 | 0 | 0
2021-12-16 20:45 | 0.34813 | 0.86972 | 0.8698 | 0.88351 | 0 | 0 | 0 | 0
2021-12-16 21:00 | 0.28075 | 1.0028 | 0.71871 | 1.1571 | 0 | 0 | 0 | 0
2021-12-16 21:15 | 0.30729 | 1.0028 | 0.51453 | 1.1632 | 0 | 0 | 0 | 0
2021-12-16 21:30 | 0.40836 | 1.064 | 0.58804 | 1.3738 | 0 | 0 | 0 | 0
2021-12-16 21:45 | 0.61662 | 0.91664 | 0.87797 | 1.1559 | 0 | 0 | 0 | 0
2021-12-16 22:00 | 0.64112 | 0.86265 | 0.55945 | 0.76976 | 0 | 0 | 0 | 0
2021-12-16 22:15 | 0.39713 | 0.65609 | 0.44511 | 0.52547 | 0 | 0 | 0 | 0
2021-12-16 22:30 | 0.4737 | 0.62343 | 0.54312 | 0.47618 | 0 | 0 | 0 | 0
2021-12-16 22:45 | 0.48595 | 0.60204 | 0.41244 | 0.46655 | 0 | 0 | 0 | 0
2021-12-16 23:00 | 3.369 | 2.185 | 3.3179 | 2.1205 | 0 | 0 | 0 | 0
2021-12-16 23:15 | 3.4608 | 2.4217 | 3.4506 | 2.2684 | 0 | 0 | 0 | 0
2021-12-16 23:30 | 3.4506 | 2.4606 | 3.4813 | 2.2789 | 0 | 0 | 0 | 0
2021-12-16 23:45 | 3.4506 | 2.6015 | 3.4506 | 2.2279 | 0 | 0 | 0 | 0
2021-12-17 | 3.471 | 2.5753 | 3.4404 | 2.2056 | 0 | 0 | 0 | 0
2021-12-17 00:15 | 3.5527 | 2.5753 | 3.4506 | 2.1917 | 0 | 0 | 0 | 0
2021-12-17 00:30 | 3.4302 | 2.5589 | 3.4915 | 2.2159 | 0 | 0 | 0 | 0
2021-12-17 00:45 | 3.4506 | 2.5753 | 3.471 | 2.1637 | 0 | 0 | 0 | 0
2021-12-17 01:00 | 3.4098 | 2.5753 | 3.4506 | 2.1 | 0 | 0 | 0 | 0
2021-12-17 01:15 | 3.4302 | 2.4002 | 3.3792 | 2.0879 | 0 | 0 | 0 | 0
2021-12-17 01:30 | 3.42 | 2.4598 | 3.3996 | 2.1023 | 0 | 0 | 0 | 0
2021-12-17 01:45 | 3.3485 | 2.3311 | 3.4098 | 1.8588 | 0 | 0 | 0 | 0
2021-12-17 02:00 | 3.3587 | 2.2289 | 3.3587 | 1.7533 | 0 | 0 | 0 | 0
2021-12-17 02:15 | 3.3485 | 2.3444 | 3.471 | 1.7666 | 0 | 0 | 0 | 0
2021-12-17 02:30 | 3.4915 | 2.328 | 3.3485 | 1.7419 | 0 | 0 | 0 | 0
2021-12-17 02:45 | 3.4915 | 2.4523 | 3.3587 | 1.6709 | 0 | 0 | 0 | 0
2021-12-17 03:00 | 3.4098 | 2.3086 | 3.5017 | 1.7729 | 0 | 0 | 0 | 0
2021-12-17 03:15 | 3.3792 | 2.3444 | 3.5425 | 1.7182 | 0 | 0 | 0 | 0
2021-12-17 03:30 | 3.4608 | 2.4236 | 3.3792 | 1.6798 | 0 | 0 | 0 | 0
2021-12-17 03:45 | 3.4915 | 2.341 | 3.3587 | 1.6587 | 0 | 0 | 0 | 0
2021-12-17 04:00 | 3.42 | 2.4166 | 3.4098 | 1.5869 | 0 | 0 | 0 | 0
2021-12-17 04:15 | 3.4404 | 2.2175 | 2.052 | 1.1638 | 0 | 0 | 0 | 0
2021-12-17 04:30 | 3.4098 | 2.1178 | 0.94739 | 0.95512 | 0 | 0 | 0 | 0
2021-12-17 04:45 | 3.3894 | 2.1355 | 0.86164 | 0.90685 | 0 | 0 | 0 | 0
2021-12-17 05:00 | 3.5119 | 2.0323 | 0.49411 | 0.82445 | 0 | 0 | 0 | 0
2021-12-17 05:15 | 3.3996 | 2.0323 | 0.26748 | 0.77457 | 0 | 0 | 0 | 0
2021-12-17 05:30 | 3.369 | 2.0145 | 0.32975 | 0.79557 | 0 | 0 | 0 | 0
2021-12-17 05:45 | 3.4404 | 2.0145 | 0.25318 | 0.77107 | 0 | 0 | 0 | 0
2021-12-17 06:00 | 3.4915 | 1.9831 | 0.23276 | 0.77734 | 0 | 0 | 0 | 0
2021-12-17 06:15 | 3.369 | 1.9845 | 0.25012 | 0.77399 | 0 | 0 | 0 | 0
2021-12-17 06:30 | 3.3996 | 1.9845 | 0.40836 | 0.77019 | 0 | 0 | 0 | 0
2021-12-17 06:45 | 3.4506 | 1.9667 | 0.3175 | 0.77005 | 0 | 0 | 0 | 0
2021-12-17 07:00 | 0.50228 | 0.62765 | 0.29504 | 0.39888 | 0 | 0 | 0 | 0
2021-12-17 07:15 | 0.27768 | 0.63521 | 0.27564 | 0.28687 | 0 | 0 | 0 | 0
2021-12-17 07:30 | 0.34506 | 0.65962 | 0.33894 | 0.35761 | 0 | 0 | 0 | 0
2021-12-17 07:45 | 0.44511 | 0.94785 | 0.84938 | 0.5822 | 0.00049 | 0.007112 | 0.000907 | 0.00242
2021-12-17 08:00 | 3.2362 | 1.9721 | 1.174 | 1.4923 | 0.004555 | 0.056599 | 0.007952 | 0.017405
2021-12-17 08:15 | 4.053 | 1.9721 | 0.70646 | 1.29 | 0.008619 | 0.10366 | 0.014996 | 0.032389
2021-12-17 08:30 | 3.7365 | 1.9014 | 0.48186 | 1.1609 | 0.012684 | 0.13827 | 0.02204 | 0.047374
2021-12-17 08:45 | 3.6242 | 1.833 | 0.60029 | 1.2825 | 0.017333 | 0.14628 | 0.028302 | 0.061274
2021-12-17 09:00 | 1.6334 | 1.2494 | 0.73096 | 1.0264 | 0.026254 | 0.15614 | 0.029252 | 0.070762
2021-12-17 09:15 | 0.7473 | 1.218 | 0.65337 | 0.98298 | 0.035176 | 0.132 | 0.030202 | 0.080249
2021-12-17 09:30 | 0.5227 | 1.2106 | 0.47778 | 0.69859 | 0.044098 | 0.14525 | 0.031152 | 0.089736
2021-12-17 09:45 | 0.44103 | 1.1703 | 0.55945 | 0.87564 | 0.053646 | 0.17178 | 0.033117 | 0.098059
2021-12-17 10:00 | 0.63296 | 1.2557 | 0.42878 | 0.73913 | 0.067798 | 0.13498 | 0.041991 | 0.098619
2021-12-17 10:15 | 0.45328 | 1.4037 | 0.45328 | 1.0116 | 0.081949 | 0.12535 | 0.050865 | 0.099179
2021-12-17 10:30 | 0.46961 | 1.1519 | 0.46961 | 0.80067 | 0.0961 | 0.13963 | 0.059739 | 0.099739
2021-12-17 10:45 | 0.50636 | 1.1022 | 0.51453 | 0.59329 | 0.11812 | 0.15079 | 0.067283 | 0.10025
2021-12-17 11:00 | 0.60437 | 1.1666 | 0.56762 | 0.62304 | 0.19814 | 0.17601 | 0.065741 | 0.10163
2021-12-17 11:15 | 0.53087 | 1.1944 | 1.8172 | 0.73504 | 0.27816 | 0.20128 | 0.064198 | 0.103
2021-12-17 11:30 | 0.33077 | 1.1944 | 2.7156 | 0.85507 | 0.35817 | 0.16186 | 0.062656 | 0.10437
2021-12-17 11:45 | 0.27973 | 1.3469 | 0.75955 | 0.62975 | 0.4294 | 0.1796 | 0.062641 | 0.10458
2021-12-17 12:00 | 0.33281 | 1.5609 | 0.64929 | 0.88964 | 0.43568 | 0.17744 | 0.07309 | 0.097583
2021-12-17 12:15 | 0.3471 | 1.2365 | 0.55945 | 0.74525 | 0.44197 | 0.19933 | 0.08354 | 0.090581
2021-12-17 12:30 | 0.46553 | 1.0104 | 0.33996 | 0.45371 | 0.44825 | 0.20006 | 0.093989 | 0.083579
2021-12-17 12:45 | 0.38998 | 1.17 | 0.46144 | 0.67292 | 0.45694 | 0.19245 | 0.10821 | 0.077142
2021-12-17 13:00 | 0.37467 | 1.3901 | 3.0933 | 1.0867 | 0.48346 | 0.18908 | 0.14832 | 0.075247
2021-12-17 13:15 | 0.51453 | 1.1701 | 1.2659 | 0.74117 | 0.50998 | 0.20313 | 0.18843 | 0.073352
2021-12-17 13:30 | 0.37365 | 1.2103 | 0.32362 | 0.92814 | 0.5365 | 0.21456 | 0.22855 | 0.071458
2021-12-17 13:45 | 0.44511 | 1.1091 | 0.22664 | 0.90918 | 0.55692 | 0.22589 | 0.26604 | 0.069966
2021-12-17 14:00 | 0.37467 | 1.1228 | 0.22868 | 0.58235 | 0.53192 | 0.24019 | 0.28542 | 0.070041
2021-12-17 14:15 | 0.36854 | 1.1309 | 0.22664 | 0.61166 | 0.50692 | 0.23479 | 0.3048 | 0.070115
2021-12-17 14:30 | 0.40836 | 1.0754 | 0.23481 | 0.60977 | 0.48192 | 0.22939 | 0.32419 | 0.07019
2021-12-17 14:45 | 0.45736 | 1.073 | 0.33485 | 0.44744 | 0.45006 | 0.21371 | 0.3339 | 0.068467
2021-12-17 15:00 | 0.37569 | 1.1043 | 0.30014 | 0.4944 | 0.36701 | 0.17759 | 0.2768 | 0.054979
2021-12-17 15:15 | 0.37058 | 1.2099 | 0.23276 | 0.39932 | 0.28396 | 0.11473 | 0.21969 | 0.041491
2021-12-17 15:30 | 0.45328 | 0.99672 | 0.22562 | 0.49207 | 0.20091 | 0.10168 | 0.16259 | 0.028003
2021-12-17 15:45 | 0.44919 | 1.1053 | 0.24297 | 0.69625 | 0.12388 | 0.070257 | 0.10913 | 0.015862
2021-12-17 16:00 | 0.36956 | 1.0518 | 0.25318 | 0.39013 | 0.091973 | 0.053331 | 0.080962 | 0.011767
2021-12-17 16:15 | 0.36344 | 0.8695 | 0.30729 | 0.48142 | 0.060066 | 0.028561 | 0.052795 | 0.007672
2021-12-17 16:30 | 0.40734 | 0.82629 | 0.27156 | 0.49805 | 0.028159 | 0.011887 | 0.024627 | 0.003578
2021-12-17 16:45 | 0.6207 | 0.83621 | 0.22562 | 0.45328 | 0 | 0 | 0 | 0
2021-12-17 17:00 | 0.51453 | 0.88683 | 0.22664 | 0.43038 | 0 | 0 | 0 | 0
2021-12-17 17:15 | 1.5518 | 1.1159 | 0.30423 | 0.88074 | 0 | 0 | 0 | 0
2021-12-17 17:30 | 0.91472 | 1.0839 | 0.40121 | 0.74467 | 0 | 0 | 0 | 0
2021-12-17 17:45 | 1.5926 | 1.1248 | 0.28891 | 0.60058 | 0 | 0 | 0 | 0
2021-12-17 18:00 | 0.91064 | 1.1535 | 0.26441 | 0.66767 | 0 | 0 | 0 | 0
2021-12-17 18:15 | 0.98414 | 1.2647 | 0.26033 | 1.0339 | 0 | 0 | 0 | 0
2021-12-17 18:30 | 0.66971 | 1.1535 | 0.29198 | 0.71536 | 0 | 0 | 0 | 0
2021-12-17 18:45 | 0.55128 | 0.91925 | 0.3175 | 0.53626 | 0 | 0 | 0 | 0
2021-12-17 19:00 | 0.64521 | 1.2287 | 0.44103 | 0.98546 | 0 | 0 | 0 | 0
2021-12-17 19:15 | 0.50636 | 2.2329 | 0.34302 | 1.8668 | 0 | 0 | 0 | 0
2021-12-17 19:30 | 1.2251 | 1.8874 | 0.33077 | 1.5803 | 0 | 0 | 0 | 0
2021-12-17 19:45 | 1.9091 | 2.139 | 0.26135 | 2.0707 | 0 | 0 | 0 | 0
2021-12-17 20:00 | 1.2659 | 1.0912 | 0.32669 | 0.89051 | 0 | 0 | 0 | 0
2021-12-17 20:15 | 0.69421 | 0.96844 | 0.40632 | 0.72484 | 0 | 0 | 0 | 0
2021-12-17 20:30 | 0.52678 | 0.98345 | 0.32056 | 0.7928 | 0 | 0 | 0 | 0
2021-12-17 20:45 | 0.63296 | 0.93854 | 0.34813 | 0.88658 | 0 | 0 | 0 | 0
2021-12-17 21:00 | 0.5962 | 1.1603 | 0.28075 | 1.1546 | 0 | 0 | 0 | 0
2021-12-17 21:15 | 0.60845 | 1.0765 | 0.30729 | 1.1578 | 0 | 0 | 0 | 0
2021-12-17 21:30 | 0.57987 | 1.3719 | 0.40836 | 1.3727 | 0 | 0 | 0 | 0
2021-12-17 21:45 | 0.49411 | 1.0381 | 0.61662 | 1.1991 | 0 | 0 | 0 | 0
2021-12-17 22:00 | 0.4982 | 0.85922 | 0.64112 | 0.8173 | 0 | 0 | 0 | 0
2021-12-17 22:15 | 0.60845 | 0.64352 | 0.39713 | 0.53276 | 0 | 0 | 0 | 0
2021-12-17 22:30 | 0.59212 | 0.61089 | 0.4737 | 0.49353 | 0 | 0 | 0 | 0
2021-12-17 22:45 | 0.58395 | 0.627 | 0.48595 | 0.45897 | 0 | 0 | 0 | 0
2021-12-17 23:00 | 0.45328 | 2.3821 | 3.369 | 2.1293 | 0 | 0 | 0 | 0
2021-12-17 23:15 | 0.37161 | 2.5421 | 3.4608 | 2.2553 | 0 | 0 | 0 | 0
2021-12-17 23:30 | 0.36752 | 2.5421 | 3.4506 | 2.2643 | 0 | 0 | 0 | 0
2021-12-17 23:45 | 0.37875 | 2.5421 | 3.4506 | 2.2162 | 0 | 0 | 0 | 0
2021-12-18 | 0.44919 | 1.6443 | 3.471 | 2.2027 | 0 | 0 | 0 | 0
2021-12-18 00:15 | 0.48595 | 1.53 | 3.5527 | 2.2034 | 0 | 0 | 0 | 0
2021-12-18 00:30 | 0.44511 | 1.53 | 3.4302 | 2.1955 | 0 | 0 | 0 | 0
2021-12-18 00:45 | 0.34302 | 1.5789 | 3.4506 | 2.1608 | 0 | 0 | 0 | 0
2021-12-18 01:00 | 0.34506 | 1.5194 | 3.4098 | 2.0941 | 0 | 0 | 0 | 0
2021-12-18 01:15 | 0.34915 | 1.555 | 3.4302 | 2.0835 | 0 | 0 | 0 | 0
2021-12-18 01:30 | 0.35629 | 1.7484 | 3.42 | 2.0863 | 0 | 0 | 0 | 0
2021-12-18 01:45 | 0.31239 | 1.7179 | 3.3485 | 1.8413 | 0 | 0 | 0 | 0
2021-12-18 02:00 | 0.31648 | 1.4171 | 3.3587 | 1.7416 | 0 | 0 | 0 | 0
2021-12-18 02:15 | 0.41244 | 1.3815 | 3.3485 | 1.752 | 0 | 0 | 0 | 0
2021-12-18 02:30 | 0.37263 | 1.2491 | 3.4915 | 1.7361 | 0 | 0 | 0 | 0
2021-12-18 02:45 | 0.36956 | 1.1887 | 3.4915 | 1.6724 | 0 | 0 | 0 | 0
2021-12-18 03:00 | 0.34915 | 1.3437 | 3.4098 | 1.7743 | 0 | 0 | 0 | 0
2021-12-18 03:15 | 0.41244 | 1.3821 | 3.3792 | 1.7123 | 0 | 0 | 0 | 0
2021-12-18 03:30 | 0.31035 | 1.2639 | 3.4608 | 1.6667 | 0 | 0 | 0 | 0
2021-12-18 03:45 | 0.30831 | 1.4556 | 3.4915 | 1.663 | 0 | 0 | 0 | 0
2021-12-18 04:00 | 0.35527 | 1.1901 | 3.42 | 1.5869 | 0 | 0 | 0 | 0
2021-12-18 04:15 | 0.41653 | 1.3287 | 3.4404 | 1.1682 | 0 | 0 | 0 | 0
2021-12-18 04:30 | 0.40836 | 1.1928 | 3.4098 | 0.95512 | 0 | 0 | 0 | 0
2021-12-18 04:45 | 0.35935 | 0.94869 | 3.3894 | 0.8733 | 0 | 0 | 0 | 0
2021-12-18 05:00 | 0.29912 | 0.90161 | 3.5119 | 0.81861 | 0 | 0 | 0 | 0
2021-12-18 05:15 | 0.29912 | 0.90681 | 3.3996 | 0.76144 | 0 | 0 | 0 | 0
2021-12-18 05:30 | 0.41653 | 0.85935 | 3.369 | 0.78536 | 0 | 0 | 0 | 0
2021-12-18 05:45 | 0.32465 | 0.86433 | 3.4404 | 0.76961 | 0 | 0 | 0 | 0
2021-12-18 06:00 | 0.31444 | 0.88909 | 3.4915 | 0.77442 | 0 | 0 | 0 | 0
2021-12-18 06:15 | 0.39202 | 0.94505 | 3.369 | 0.75648 | 0 | 0 | 0 | 0
2021-12-18 06:30 | 0.43694 | 0.87277 | 3.3996 | 0.76873 | 0 | 0 | 0 | 0
2021-12-18 06:45 | 0.3175 | 0.85505 | 3.4506 | 0.78463 | 0 | 0 | 0 | 0
2021-12-18 07:00 | 0.35119 | 0.64009 | 0.50228 | 0.38196 | 0 | 0 | 0 | 0
2021-12-18 07:15 | 0.43694 | 0.61883 | 0.27768 | 0.28746 | 0 | 0 | 0 | 0
2021-12-18 07:30 | 0.52678 | 0.65806 | 0.34506 | 0.35877 | 0 | 0 | 0 | 0
2021-12-18 07:45 | 0.91064 | 0.79487 | 0.44511 | 0.55245 | 0.00104 | 0.008796 | 0.00049 | 0.002242
2021-12-18 08:00 | 0.94331 | 1.3892 | 3.2362 | 1.3931 | 0.010297 | 0.061145 | 0.004555 | 0.016413
2021-12-18 08:15 | 0.4982 | 1.2666 | 4.053 | 1.3483 | 0.019553 | 0.10171 | 0.008619 | 0.030584
2021-12-18 08:30 | 0.62887 | 1.1962 | 3.7365 | 1.1682 | 0.02881 | 0.13958 | 0.012684 | 0.044755
2021-12-18 08:45 | 0.93514 | 1.2628 | 3.6242 | 1.2665 | 0.038296 | 0.15914 | 0.017333 | 0.057746
2021-12-18 09:00 | 0.77588 | 1.2738 | 1.6334 | 1.0819 | 0.0496 | 0.14545 | 0.026254 | 0.066107
2021-12-18 09:15 | 0.64112 | 1.2287 | 0.7473 | 0.98473 | 0.060904 | 0.11769 | 0.035176 | 0.074468
2021-12-18 09:30 | 1.3272 | 1.2284 | 0.5227 | 0.70383 | 0.072208 | 0.13151 | 0.044098 | 0.082828
2021-12-18 09:45 | 3.6548 | 1.1639 | 0.44103 | 0.87272 | 0.090157 | 0.16575 | 0.053646 | 0.090549
2021-12-18 10:00 | 3.6956 | 1.1083 | 0.63296 | 0.68604 | 0.16097 | 0.13737 | 0.067798 | 0.093181
2021-12-18 10:15 | 3.7059 | 1.1083 | 0.45328 | 0.63733 | 0.23178 | 0.12628 | 0.081949 | 0.095813
2021-12-18 10:30 | 3.7773 | 1.1083 | 0.46961 | 0.75867 | 0.3026 | 0.14816 | 0.0961 | 0.098445
2021-12-18 10:45 | 3.7161 | 1.0756 | 0.50636 | 0.57403 | 0.37029 | 0.15379 | 0.11812 | 0.10236
2021-12-18 11:00 | 3.6038 | 1.2085 | 0.60437 | 0.62596 | 0.4131 | 0.18617 | 0.19814 | 0.11636
2021-12-18 11:15 | 3.6242 | 1.1223 | 0.53087 | 0.73913 | 0.45591 | 0.21497 | 0.27816 | 0.13035
2021-12-18 11:30 | 3.6344 | 1.1098 | 0.33077 | 0.8294 | 0.49871 | 0.20282 | 0.35817 | 0.14435
2021-12-18 11:45 | 3.7263 | 1.1087 | 0.27973 | 0.53612 | 0.53739 | 0.22508 | 0.4294 | 0.15552
2021-12-18 12:00 | 3.6956 | 1.1509 | 0.33281 | 0.48216 | 0.54302 | 0.2316 | 0.43568 | 0.1483
2021-12-18 12:15 | 3.5936 | 1.0427 | 0.3471 | 0.46524 | 0.54865 | 0.24305 | 0.44197 | 0.14108
2021-12-18 12:30 | 3.6344 | 1.1029 | 0.46553 | 0.45197 | 0.55428 | 0.24941 | 0.44825 | 0.13386
2021-12-18 12:45 | 3.6038 | 0.97999 | 0.38998 | 0.42819 | 0.55944 | 0.26034 | 0.45694 | 0.12811
2021-12-18 13:00 | 3.6854 | 1.0779 | 0.37467 | 0.79601 | 0.56081 | 0.2866 | 0.48346 | 0.13205
2021-12-18 13:15 | 3.6956 | 1.1523 | 0.51453 | 0.75809 | 0.56219 | 0.31326 | 0.50998 | 0.13599
2021-12-18 13:30 | 3.5936 | 1.0668 | 0.37365 | 0.82984 | 0.56356 | 0.34473 | 0.5365 | 0.13994
2021-12-18 13:45 | 3.7161 | 1.1414 | 0.44511 | 0.86368 | 0.56195 | 0.35287 | 0.55692 | 0.14319
2021-12-18 14:00 | 3.8488 | 1.028 | 0.37467 | 0.58352 | 0.53627 | 0.33703 | 0.53192 | 0.14047
2021-12-18 14:15 | 3.665 | 0.99511 | 0.36854 | 0.59722 | 0.51059 | 0.31386 | 0.50692 | 0.13775
2021-12-18 14:30 | 3.6854 | 1.0268 | 0.40836 | 0.61093 | 0.48491 | 0.30618 | 0.48192 | 0.13504
2021-12-18 14:45 | 3.7875 | 1.1539 | 0.45736 | 0.44511 | 0.45243 | 0.28526 | 0.45006 | 0.12955
2021-12-18 15:00 | 3.6752 | 1.2246 | 0.37569 | 0.47399 | 0.3648 | 0.23111 | 0.36701 | 0.10504
2021-12-18 15:15 | 1.6334 | 1.4094 | 0.37058 | 0.39625 | 0.27717 | 0.17089 | 0.28396 | 0.080526
2021-12-18 15:30 | 0.41653 | 1.1086 | 0.45328 | 0.50418 | 0.18954 | 0.12526 | 0.20091 | 0.056012
2021-12-18 15:45 | 0.35833 | 1.1464 | 0.44919 | 0.70646 | 0.10847 | 0.081057 | 0.12388 | 0.033559
2021-12-18 16:00 | 0.28993 | 1.1338 | 0.36956 | 0.39115 | 0.080587 | 0.054695 | 0.091973 | 0.024906
2021-12-18 16:15 | 1.5824 | 0.85227 | 0.36344 | 0.45342 | 0.052709 | 0.034283 | 0.060066 | 0.016253
2021-12-18 16:30 | 3.5936 | 0.84172 | 0.40734 | 0.50009 | 0.024832 | 0.016403 | 0.028159 | 0.0076
2021-12-18 16:45 | 3.665 | 0.87799 | 0.6207 | 0.49397 | 0 | 0 | 0 | 0
2021-12-18 17:00 | 3.665 | 0.87799 | 0.51453 | 0.42863 | 0 | 0 | 0 | 0
2021-12-18 17:15 | 3.6752 | 1.0865 | 1.5518 | 0.95512 | 0 | 0 | 0 | 0
2021-12-18 17:30 | 0.66971 | 0.97156 | 0.91472 | 0.64492 | 0 | 0 | 0 | 0
2021-12-18 17:45 | 0.40734 | 1.0414 | 1.5926 | 0.64433 | 0 | 0 | 0 | 0
2021-12-18 18:00 | 0.47778 | 1.0133 | 0.91064 | 0.59504 | 0 | 0 | 0 | 0
2021-12-18 18:15 | 0.53903 | 1.0275 | 0.98414 | 0.90466 | 0 | 0 | 0 | 0
2021-12-18 18:30 | 0.73913 | 0.83873 | 0.66971 | 0.51351 | 0 | 0 | 0 | 0
2021-12-18 18:45 | 0.73913 | 0.88995 | 0.55128 | 0.51526 | 0 | 0 | 0 | 0
2021-12-18 19:00 | 0.80855 | 1.1878 | 0.64521 | 0.97787 | 0 | 0 | 0 | 0
2021-12-18 19:15 | 0.7718 | 1.2014 | 0.50636 | 1.3616 | 0 | 0 | 0 | 0
2021-12-18 19:30 | 0.93106 | 1.2023 | 1.2251 | 1.1749 | 0 | 0 | 0 | 0
2021-12-18 19:45 | 0.96781 | 1.3952 | 1.9091 | 1.7936 | 0 | 0 | 0 | 0
2021-12-18 20:00 | 1.3374 | 1.1888 | 1.2659 | 0.9751 | 0 | 0 | 0 | 0
2021-12-18 20:15 | 1.1638 | 1.1019 | 0.69421 | 0.73767 | 0 | 0 | 0 | 0
2021-12-18 20:30 | 1.3884 | 0.89223 | 0.52678 | 0.75021 | 0 | 0 | 0 | 0
2021-12-18 20:45 | 0.65337 | 0.90766 | 0.63296 | 0.85916 | 0 | 0 | 0 | 0
2021-12-18 21:00 | 0.69013 | 1.0815 | 0.5962 | 1.1459 | 0 | 0 | 0 | 0
2021-12-18 21:15 | 0.73913 | 1.0445 | 0.60845 | 1.1561 | 0 | 0 | 0 | 0
2021-12-18 21:30 | 0.65746 | 1.0772 | 0.57987 | 1.3082 | 0 | 0 | 0 | 0
2021-12-18 21:45 | 0.5717 | 1.0759 | 0.49411 | 1.1484 | 0 | 0 | 0 | 0
2021-12-18 22:00 | 0.4982 | 0.91681 | 0.4982 | 0.79688 | 0 | 0 | 0 | 0
2021-12-18 22:15 | 0.43286 | 0.64472 | 0.60845 | 0.5386 | 0 | 0 | 0 | 0
2021-12-18 22:30 | 0.43694 | 0.63074 | 0.59212 | 0.51511 | 0 | 0 | 0 | 0
2021-12-18 22:45 | 0.43286 | 0.60681 | 0.58395 | 0.48668 | 0 | 0 | 0 | 0
2021-12-18 23:00 | 0.53903 | 1.4289 | 0.45328 | 1.7186 | 0 | 0 | 0 | 0
2021-12-18 23:15 | 0.57578 | 1.6281 | 0.37161 | 1.7877 | 0 | 0 | 0 | 0
2021-12-18 23:30 | 0.53087 | 1.6281 | 0.36752 | 1.802 | 0 | 0 | 0 | 0
2021-12-18 23:45 | 0.48186 | 1.555 | 0.37875 | 1.7701 | 0 | 0 | 0 | 0
2021-12-19 | 0.48595 | 1.6811 | 0.44919 | 1.768 | 0 | 0 | 0 | 0
2021-12-19 00:15 | 0.51453 | 1.6014 | 0.48595 | 1.7609 | 0 | 0 | 0 | 0
2021-12-19 00:30 | 0.41244 | 1.6014 | 0.44511 | 1.7443 | 0 | 0 | 0 | 0
2021-12-19 00:45 | 0.42469 | 1.6195 | 0.34302 | 1.7023 | 0 | 0 | 0 | 0
2021-12-19 01:00 | 0.32975 | 1.5997 | 0.34506 | 1.6534 | 0 | 0 | 0 | 0
2021-12-19 01:15 | 0.34098 | 1.6014 | 0.34915 | 1.6434 | 0 | 0 | 0 | 0
2021-12-19 01:30 | 0.39815 | 1.6014 | 0.35629 | 1.6311 | 0 | 0 | 0 | 0
2021-12-19 01:45 | 0.33792 | 1.1642 | 0.31239 | 1.3944 | 0 | 0 | 0 | 0
2021-12-19 02:00 | 0.28993 | 1.1743 | 0.31648 | 1.2939 | 0 | 0 | 0 | 0
2021-12-19 02:15 | 0.30218 | 1.1005 | 0.41244 | 1.3136 | 0 | 0 | 0 | 0
2021-12-19 02:30 | 1.7968 | 0.99676 | 0.37263 | 1.2818 | 0 | 0 | 0 | 0
2021-12-19 02:45 | 1.8989 | 0.95414 | 0.36956 | 1.2162 | 0 | 0 | 0 | 0
2021-12-19 03:00 | 0.5472 | 1.1461 | 0.34915 | 1.2802 | 0 | 0 | 0 | 0
2021-12-19 03:15 | 0.53495 | 1.0887 | 0.41244 | 1.2593 | 0 | 0 | 0 | 0
2021-12-19 03:30 | 0.40019 | 0.93481 | 0.31035 | 1.2093 | 0 | 0 | 0 | 0
2021-12-19 03:45 | 0.35629 | 0.93481 | 0.30831 | 1.2025 | 0 | 0 | 0 | 0
2021-12-19 04:00 | 0.93922 | 0.95055 | 0.35527 | 1.2308 | 0 | 0 | 0 | 0
2021-12-19 04:15 | 3.1546 | 0.889 | 0.41653 | 1.0425 | 0 | 0 | 0 | 0
2021-12-19 04:30 | 0.75546 | 0.78149 | 0.40836 | 0.86762 | 0 | 0 | 0 | 0
2021-12-19 04:45 | 0.35527 | 0.79921 | 0.35935 | 0.83597 | 0 | 0 | 0 | 0
2021-12-19 05:00 | 0.37671 | 0.76864 | 0.29912 | 0.8122 | 0 | 0 | 0 | 0
2021-12-19 05:15 | 0.34608 | 0.8806 | 0.29912 | 0.75094 | 0 | 0 | 0 | 0
2021-12-19 05:30 | 0.29198 | 0.86287 | 0.41653 | 0.78536 | 0 | 0 | 0 | 0
2021-12-19 05:45 | 0.45328 | 0.86287 | 0.32465 | 0.76655 | 0 | 0 | 0 | 0
2021-12-19 06:00 | 0.40325 | 0.869 | 0.31444 | 0.76567 | 0 | 0 | 0 | 0
2021-12-19 06:15 | 0.3226 | 0.87668 | 0.39202 | 0.75502 | 0 | 0 | 0 | 0
2021-12-19 06:30 | 0.28789 | 0.87668 | 0.43694 | 0.78419 | 0 | 0 | 0 | 0
2021-12-19 06:45 | 0.33587 | 0.85896 | 0.3175 | 0.77865 | 0 | 0 | 0 | 0
2021-12-19 07:00 | 0.36344 | 0.63378 | 0.35119 | 0.36563 | 0 | 0 | 0 | 0
2021-12-19 07:15 | 0.38692 | 0.65165 | 0.43694 | 0.30218 | 0 | 0 | 0 | 0
2021-12-19 07:30 | 0.38386 | 0.68007 | 0.52678 | 0.38123 | 0 | 0 | 0 | 0
2021-12-19 07:45 | 0.3226 | 1.0848 | 0.91064 | 0.62843 | 0.000725 | 0.008699 | 0.00104 | 0.001268
2021-12-19 08:00 | 0.33485 | 1.3221 | 0.94331 | 1.242 | 0.00769 | 0.055996 | 0.010297 | 0.010154
2021-12-19 08:15 | 0.33587 | 1.4517 | 0.4982 | 1.3308 | 0.014654 | 0.099587 | 0.019553 | 0.01904
2021-12-19 08:30 | 0.68196 | 1.2302 | 0.62887 | 1.1892 | 0.021618 | 0.14305 | 0.02881 | 0.027926
2021-12-19 08:45 | 1.2251 | 1.4233 | 0.93514 | 1.3318 | 0.027794 | 0.15642 | 0.038296 | 0.037615
2021-12-19 09:00 | 0.73096 | 1.2685 | 0.77588 | 1.0988 | 0.027162 | 0.14791 | 0.0496 | 0.052491
2021-12-19 09:15 | 0.75546 | 1.2137 | 0.64112 | 0.94681 | 0.026529 | 0.12267 | 0.060904 | 0.067367
2021-12-19 09:30 | 0.59212 | 1.2328 | 1.3272 | 0.78609 | 0.025897 | 0.14476 | 0.072208 | 0.082243
2021-12-19 09:45 | 0.50228 | 1.4887 | 3.6548 | 1.2986 | 0.025681 | 0.18 | 0.090157 | 0.095925
2021-12-19 10:00 | 0.49411 | 1.2656 | 3.6956 | 1.1282 | 0.029079 | 0.1657 | 0.16097 | 0.1047
2021-12-19 10:15 | 0.73096 | 1.1995 | 3.7059 | 1.0792 | 0.032476 | 0.1715 | 0.23178 | 0.11347
2021-12-19 10:30 | 3.1035 | 1.2636 | 3.7773 | 1.2119 | 0.035873 | 0.22299 | 0.3026 | 0.12224
2021-12-19 10:45 | 2.5522 | 1.2833 | 3.7161 | 1.0197 | 0.038959 | 0.25563 | 0.37029 | 0.13318
2021-12-19 11:00 | 0.47778 | 1.2987 | 3.6038 | 1.0422 | 0.039334 | 0.26064 | 0.4131 | 0.15718
2021-12-19 11:15 | 0.38896 | 1.3816 | 3.6242 | 1.1577 | 0.039709 | 0.29308 | 0.45591 | 0.18119
2021-12-19 11:30 | 0.44103 | 1.4249 | 3.6344 | 1.2611 | 0.040084 | 0.32887 | 0.49871 | 0.20519
2021-12-19 11:45 | 0.66154 | 1.2982 | 3.7263 | 0.9576 | 0.040271 | 0.35438 | 0.53739 | 0.2251
2021-12-19 12:00 | 0.38692 | 1.2959 | 3.6956 | 0.91151 | 0.038818 | 0.35568 | 0.54302 | 0.21853
2021-12-19 12:15 | 0.37977 | 1.2959 | 3.5936 | 0.88118 | 0.037366 | 0.35151 | 0.54865 | 0.21196
2021-12-19 12:30 | 0.38692 | 1.3206 | 3.6344 | 0.87724 | 0.035914 | 0.35512 | 0.55428 | 0.2054
2021-12-19 12:45 | 0.40019 | 1.3144 | 3.6038 | 0.85726 | 0.034376 | 0.36455 | 0.55944 | 0.20036
2021-12-19 13:00 | 2.4297 | 1.5134 | 3.6854 | 1.2408 | 0.032086 | 0.35768 | 0.56081 | 0.20512
2021-12-19 13:15 | 2.9504 | 1.3778 | 3.6956 | 1.2114 | 0.029796 | 0.38441 | 0.56219 | 0.20988
2021-12-19 13:30 | 0.58395 | 1.4807 | 3.5936 | 1.2796 | 0.027506 | 0.38535 | 0.56356 | 0.21464
2021-12-19 13:45 | 0.58395 | 1.4508 | 3.7161 | 1.3187 | 0.025023 | 0.37923 | 0.56195 | 0.21821
2021-12-19 14:00 | 0.60845 | 1.1798 | 3.8488 | 0.9945 | 0.020838 | 0.3619 | 0.53627 | 0.21202
2021-12-19 14:15 | 0.77588 | 1.1038 | 3.665 | 0.9137 | 0.016654 | 0.33719 | 0.51059 | 0.20583
2021-12-19 14:30 | 0.56354 | 1.1678 | 3.6854 | 1.0365 | 0.012469 | 0.32657 | 0.48491 | 0.19964
2021-12-19 14:45 | 0.60845 | 1.2846 | 3.7875 | 0.91151 | 0.008489 | 0.30426 | 0.45243 | 0.18985
2021-12-19 15:00 | 0.51453 | 1.216 | 3.6752 | 0.92435 | 0.006311 | 0.24625 | 0.3648 | 0.15389
2021-12-19 15:15 | 0.70646 | 1.2373 | 1.6334 | 0.55726 | 0.004134 | 0.18011 | 0.27717 | 0.11794
2021-12-19 15:30 | 0.76771 | 1.066 | 0.41653 | 0.48376 | 0.001957 | 0.13156 | 0.18954 | 0.08198
2021-12-19 15:45 | 0.37161 | 1.2902 | 0.35833 | 0.68706 | 0 | 0.089303 | 0.10847 | 0.048847
2021-12-19 16:00 | 0.40836 | 1.121 | 0.28993 | 0.3649 | 0 | 0.060145 | 0.080587 | 0.036266
2021-12-19 16:15 | 0.49003 | 1.1031 | 1.5824 | 0.60131 | 0 | 0.033788 | 0.052709 | 0.023684
2021-12-19 16:30 | 0.53087 | 1.2314 | 3.5936 | 0.92712 | 0 | 0.016334 | 0.024832 | 0.011103
2021-12-19 16:45 | 0.40019 | 1.1697 | 3.665 | 0.9312 | 0 | 0 | 0 | 0
2021-12-19 17:00 | 0.4737 | 1.1457 | 3.665 | 0.87812 | 0 | 0 | 0 | 0
2021-12-19 17:15 | 0.36548 | 1.3361 | 3.6752 | 1.4125 | 0 | 0 | 0 | 0
2021-12-19 17:30 | 0.41653 | 1.0649 | 0.66971 | 0.67467 | 0 | 0 | 0 | 0
2021-12-19 17:45 | 0.39917 | 1.1395 | 0.40734 | 0.61735 | 0 | 0 | 0 | 0
2021-12-19 18:00 | 0.57987 | 1.1114 | 0.47778 | 0.57637 | 0 | 0 | 0 | 0
2021-12-19 18:15 | 0.91472 | 1.1224 | 0.53903 | 0.90116 | 0 | 0 | 0 | 0
2021-12-19 18:30 | 2.1439 | 0.87415 | 0.73913 | 0.53218 | 0 | 0 | 0 | 0
2021-12-19 18:45 | 2.246 | 0.87415 | 0.73913 | 0.53276 | 0 | 0 | 0 | 0
2021-12-19 19:00 | 2.246 | 0.95323 | 0.80855 | 0.67044 | 0 | 0 | 0 | 0
2021-12-19 19:15 | 1.7968 | 0.93679 | 0.7718 | 0.91618 | 0 | 0 | 0 | 0
2021-12-19 19:30 | 0.76771 | 0.94324 | 0.93106 | 0.76246 | 0 | 0 | 0 | 0
2021-12-19 19:45 | 0.75546 | 1.1574 | 0.96781 | 1.3805 | 0 | 0 | 0 | 0
2021-12-19 20:00 | 0.74321 | 0.92161 | 1.3374 | 0.90947 | 0 | 0 | 0 | 0
2021-12-19 20:15 | 1.2047 | 0.90034 | 1.1638 | 0.77384 | 0 | 0 | 0 | 0
2021-12-19 20:30 | 1.2047 | 0.80159 | 1.3884 | 0.84005 | 0 | 0 | 0 | 0
2021-12-19 20:45 | 0.89022 | 0.90695 | 0.65337 | 0.79353 | 0 | 0 | 0 | 0
2021-12-19 21:00 | 1.0821 | 1.1404 | 0.69013 | 1.1482 | 0 | 0 | 0 | 0
2021-12-19 21:15 | 0.69013 | 1.1522 | 0.73913 | 1.1718 | 0 | 0 | 0 | 0
2021-12-19 21:30 | 0.76771 | 1.4636 | 0.65746 | 1.3111 | 0 | 0 | 0 | 0
2021-12-19 21:45 | 0.62887 | 1.0339 | 0.5717 | 1.0941 | 0 | 0 | 0 | 0
2021-12-19 22:00 | 0.42878 | 0.87501 | 0.4982 | 0.73621 | 0 | 0 | 0 | 0
2021-12-19 22:15 | 0.42878 | 0.58882 | 0.43286 | 0.52051 | 0 | 0 | 0 | 0
2021-12-19 22:30 | 0.43694 | 0.57948 | 0.43694 | 0.50928 | 0 | 0 | 0 | 0
2021-12-19 22:45 | 0.46553 | 0.57948 | 0.43286 | 0.48026 | 0 | 0 | 0 | 0
2021-12-19 23:00 | 0.55128 | 1.1115 | 0.53903 | 1.3114 | 0 | 0 | 0 | 0
2021-12-19 23:15 | 0.62479 | 1.0592 | 0.57578 | 1.342 | 0 | 0 | 0 | 0
2021-12-19 23:30 | 0.55945 | 1.1557 | 0.53087 | 1.3455 | 0 | 0 | 0 | 0
2021-12-19 23:45 | 0.58395 | 1.0792 | 0.48186 | 1.3183 | 0 | 0 | 0 | 0
2021-12-20 | 0.60437 | 0.98487 | 0.48595 | 1.3212 | 0 | 0 | 0 | 0
2021-12-20 00:15 | 0.49003 | 0.9434 | 0.51453 | 1.3152 | 0 | 0 | 0 | 0
2021-12-20 00:30 | 0.45736 | 0.95728 | 0.41244 | 1.284 | 0 | 0 | 0 | 0
2021-12-20 00:45 | 0.44103 | 0.75989 | 0.42469 | 1.2642 | 0 | 0 | 0 | 0
2021-12-20 01:00 | 0.32465 | 0.57906 | 0.32975 | 1.2149 | 0 | 0 | 0 | 0
2021-12-20 01:15 | 0.32158 | 0.57906 | 0.34098 | 1.2035 | 0 | 0 | 0 | 0
2021-12-20 01:30 | 0.38794 | 0.61324 | 0.39815 | 1.1979 | 0 | 0 | 0 | 0
2021-12-20 01:45 | 0.44103 | 0.51511 | 0.33792 | 1.1729 | 0 | 0 | 0 | 0
2021-12-20 02:00 | 0.33281 | 0.51582 | 0.28993 | 1.1749 | 0 | 0 | 0 | 0
2021-12-20 02:15 | 0.35731 | 0.85913 | 0.30218 | 1.2354 | 0 | 0 | 0 | 0
2021-12-20 02:30 | 0.32669 | 0.92033 | 1.7968 | 1.4387 | 0 | 0 | 0 | 0
2021-12-20 02:45 | 0.32669 | 0.92033 | 1.8989 | 1.4487 | 0 | 0 | 0 | 0
2021-12-20 03:00 | 0.42469 | 0.8784 | 0.5472 | 1.261 | 0 | 0 | 0 | 0
2021-12-20 03:15 | 0.33383 | 0.75427 | 0.53495 | 1.271 | 0 | 0 | 0 | 0
2021-12-20 03:30 | 0.35731 | 0.53209 | 0.40019 | 1.2112 | 0 | 0 | 0 | 0
2021-12-20 03:45 | 0.35119 | 0.51582 | 0.35629 | 1.199 | 0 | 0 | 0 | 0
2021-12-20 04:00 | 0.43286 | 1.0211 | 0.93922 | 1.3101 | 0 | 0 | 0 | 0
2021-12-20 04:15 | 0.35833 | 0.83471 | 3.1546 | 1.4406 | 0 | 0 | 0 | 0
2021-12-20 04:30 | 0.36956 | 0.5761 | 0.75546 | 0.93149 | 0 | 0 | 0 | 0
2021-12-20 04:45 | 0.3226 | 0.47851 | 0.35527 | 0.84268 | 0 | 0 | 0 | 0
2021-12-20 05:00 | 0.36344 | 0.53777 | 0.37671 | 0.81015 | 0 | 0 | 0 | 0
2021-12-20 05:15 | 0.31954 | 0.50781 | 0.34608 | 0.75532 | 0 | 0 | 0 | 0
2021-12-20 05:30 | 0.42469 | 0.50781 | 0.29198 | 0.78405 | 0 | 0 | 0 | 0
2021-12-20 05:45 | 0.72688 | 0.50781 | 0.45328 | 0.78521 | 0 | 0 | 0 | 0
2021-12-20 06:00 | 0.51045 | 0.50781 | 0.40325 | 0.76494 | 0 | 0 | 0 | 0
2021-12-20 06:15 | 0.38182 | 0.58576 | 0.3226 | 0.75867 | 0 | 0 | 0 | 0
2021-12-20 06:30 | 0.42878 | 0.53184 | 0.28789 | 0.78288 | 0 | 0 | 0 | 0
2021-12-20 06:45 | 0.43694 | 0.5265 | 0.33587 | 0.78434 | 0 | 0 | 0 | 0
2021-12-20 07:00 | 0.44103 | 0.50859 | 0.36344 | 0.36169 | 0 | 0 | 0 | 0
2021-12-20 07:15 | 0.42061 | 0.62016 | 0.38692 | 0.32304 | 0 | 0 | 0 | 0
2021-12-20 07:30 | 0.39815 | 0.71884 | 0.38386 | 0.39144 | 0 | 0 | 0 | 0
2021-12-20 07:45 | 0.37161 | 0.86213 | 0.3226 | 0.63106 | 0.001713 | 0.008585 | 0.000725 | 0.001042
2021-12-20 08:00 | 0.35833 | 1.0827 | 0.33485 | 1.0886 | 0.019577 | 0.062521 | 0.00769 | 0.008886
2021-12-20 08:15 | 0.47778 | 1.2006 | 0.33587 | 1.1396 | 0.03744 | 0.1145 | 0.014654 | 0.01673
2021-12-20 08:30 | 0.41244 | 1.1811 | 0.68196 | 1.0372 | 0.055304 | 0.17034 | 0.021618 | 0.024574
2021-12-20 08:45 | 0.31852 | 1.3163 | 1.2251 | 1.1495 | 0.076265 | 0.20955 | 0.027794 | 0.03342
2021-12-20 09:00 | 0.39202 | 1.1251 | 0.73096 | 0.87943 | 0.12655 | 0.15163 | 0.027162 | 0.0481
2021-12-20 09:15 | 0.42878 | 1.1333 | 0.75546 | 0.69888 | 0.17684 | 0.12807 | 0.026529 | 0.062779
2021-12-20 09:30 | 0.48595 | 1.2889 | 0.59212 | 0.66212 | 0.22713 | 0.1208 | 0.025897 | 0.077458
2021-12-20 09:45 | 0.5472 | 1.2535 | 0.50228 | 0.96198 | 0.27385 | 0.14653 | 0.025681 | 0.090864
2021-12-20 10:00 | 0.44103 | 1.2535 | 0.49411 | 0.96985 | 0.28669 | 0.12263 | 0.029079 | 0.099145
2021-12-20 10:15 | 0.46553 | 1.2025 | 0.73096 | 1.0763 | 0.29952 | 0.12498 | 0.032476 | 0.10743
2021-12-20 10:30 | 0.94739 | 1.5046 | 3.1035 | 1.5311 | 0.31236 | 0.16267 | 0.035873 | 0.11571
2021-12-20 10:45 | 0.98006 | 1.5112 | 2.5522 | 1.3161 | 0.32139 | 0.2142 | 0.038959 | 0.12591
2021-12-20 11:00 | 0.44919 | 1.2216 | 0.47778 | 1.0474 | 0.29407 | 0.21725 | 0.039334 | 0.14776
2021-12-20 11:15 | 1.858 | 1.2074 | 0.38896 | 1.1672 | 0.26675 | 0.25058 | 0.039709 | 0.1696
2021-12-20 11:30 | 1.6028 | 1.3642 | 0.44103 | 1.2846 | 0.23944 | 0.25857 | 0.040084 | 0.19145
2021-12-20 11:45 | 1.5824 | 1.3122 | 0.66154 | 1.0127 | 0.21678 | 0.27271 | 0.040271 | 0.20993
2021-12-20 12:00 | 2.7666 | 1.1843 | 0.38692 | 0.9312 | 0.23875 | 0.27911 | 0.038818 | 0.20569
2021-12-20 12:15 | 1.0005 | 1.2985 | 0.37977 | 0.88264 | 0.26072 | 0.27902 | 0.037366 | 0.20144
2021-12-20 12:30 | 0.42061 | 1.2533 | 0.38692 | 0.87447 | 0.2827 | 0.29557 | 0.035914 | 0.1972
2021-12-20 12:45 | 0.39202 | 1.2251 | 0.40019 | 0.85945 | 0.29638 | 0.29833 | 0.034376 | 0.19432
2021-12-20 13:00 | 0.46553 | 1.2846 | 2.4297 | 1.5332 | 0.23036 | 0.29906 | 0.032086 | 0.20034
2021-12-20 13:15 | 0.57987 | 1.3755 | 2.9504 | 1.4768 | 0.16434 | 0.29979 | 0.029796 | 0.20636
2021-12-20 13:30 | 0.7963 | 1.1465 | 0.58395 | 0.93718 | 0.098324 | 0.30052 | 0.027506 | 0.21238
2021-12-20 13:45 | 0.42878 | 1.2184 | 0.58395 | 1.1746 | 0.037997 | 0.30273 | 0.025023 | 0.2169
2021-12-20 14:00 | 0.89022 | 1.2079 | 0.60845 | 0.9805 | 0.032643 | 0.2889 | 0.020838 | 0.20994
2021-12-20 14:15 | 1.3782 | 1.1805 | 0.77588 | 0.91312 | 0.027288 | 0.27507 | 0.016654 | 0.20299
2021-12-20 14:30 | 1.1842 | 1.1111 | 0.56354 | 1.0248 | 0.021934 | 0.2781 | 0.012469 | 0.19603
2021-12-20 14:45 | 1.123 | 1.2978 | 0.60845 | 0.92202 | 0.016681 | 0.2591 | 0.008489 | 0.18576
2021-12-20 15:00 | 1.2659 | 1.0937 | 0.51453 | 0.93777 | 0.012411 | 0.20128 | 0.006311 | 0.15087
2021-12-20 15:15 | 4.1879 | 1.0909 | 0.70646 | 0.61064 | 0.008142 | 0.1508 | 0.004134 | 0.11599
2021-12-20 15:30 | 2.1337 | 1.0806 | 0.76771 | 0.54107 | 0.003872 | 0.11141 | 0.001957 | 0.081098
2021-12-20 15:45 | 1.1944 | 1.1554 | 0.37161 | 0.70602 | 0 | 0.07067 | 0 | 0.048847
2021-12-20 16:00 | 3.8182 | 1.0187 | 0.40836 | 0.39217 | 0 | 0.050712 | 0 | 0.036266
2021-12-20 16:15 | 4.1677 | 0.92126 | 0.49003 | 0.61181 | 0 | 0.029142 | 0 | 0.023684
2021-12-20 16:30 | 1.9397 | 1.0601 | 0.53087 | 0.93762 | 0 | 0.014733 | 0 | 0.011103
2021-12-20 16:45 | 1.9805 | 1.0381 | 0.40019 | 0.93062 | 0 | 0 | 0 | 0
2021-12-20 17:00 | 2.001 | 0.9106 | 0.4737 | 0.8946 | 0 | 0 | 0 | 0
2021-12-20 17:15 | 0.41653 | 1.647 | 0.36548 | 1.4116 | 0 | 0 | 0 | 0
2021-12-20 17:30 | 0.20724 | 0.94788 | 0.41653 | 0.68123 | 0 | 0 | 0 | 0
2021-12-20 17:45 | 0.2103 | 1.008 | 0.39917 | 0.61487 | 0 | 0 | 0 | 0
2021-12-20 18:00 | 0.28483 | 1.0168 | 0.57987 | 0.5962 | 0 | 0 | 0 | 0
2021-12-20 18:15 | 0.37161 | 1.2216 | 0.91472 | 0.97991 | 0 | 0 | 0 | 0
2021-12-20 18:30 | 0.35731 | 0.99633 | 2.1439 | 0.79601 | 0 | 0 | 0 | 0
2021-12-20 18:45 | 0.27973 | 1.0927 | 2.246 | 0.81132 | 0 | 0 | 0 | 0
2021-12-20 19:00 | 0.26952 | 1.1318 | 2.246 | 0.94856 | 0 | 0 | 0 | 0
2021-12-20 19:15 | 0.32465 | 1.224 | 1.7968 | 1.1303 | 0 | 0 | 0 | 0
2021-12-20 19:30 | 2.5114 | 1.0005 | 0.76771 | 0.80738 | 0 | 0 | 0 | 0
2021-12-20 19:45 | 4.7406 | 1.5211 | 0.75546 | 1.4342 | 0 | 0 | 0 | 0
2021-12-20 20:00 | 1.1026 | 1.1269 | 0.74321 | 0.96548 | 0 | 0 | 0 | 0
2021-12-20 20:15 | 0.4982 | 0.8154 | 1.2047 | 0.89168 | 0 | 0 | 0 | 0
2021-12-20 20:30 | 0.52678 | 0.8206 | 1.2047 | 0.92931 | 0 | 0 | 0 | 0
2021-12-20 20:45 | 0.52678 | 0.9275 | 0.89022 | 0.68152 | 0 | 0 | 0 | 0
2021-12-20 21:00 | 0.53087 | 1.0013 | 1.0821 | 0.86966 | 0 | 0 | 0 | 0
2021-12-20 21:15 | 0.53495 | 0.95204 | 0.69013 | 0.85186 | 0 | 0 | 0 | 0
2021-12-20 21:30 | 0.53903 | 1.0414 | 0.76771 | 0.90597 | 0 | 0 | 0 | 0
2021-12-20 21:45 | 0.54312 | 0.95978 | 0.62887 | 0.88643 | 0 | 0 | 0 | 0
2021-12-20 22:00 | 0.5472 | 0.93724 | 0.42878 | 0.70179 | 0 | 0 | 0 | 0
2021-12-20 22:15 | 0.55128 | 0.5763 | 0.42878 | 0.49018 | 0 | 0 | 0 | 0
2021-12-20 22:30 | 0.55537 | 0.58677 | 0.43694 | 0.49236 | 0 | 0 | 0 | 0
2021-12-20 22:45 | 0.55945 | 0.58677 | 0.46553 | 0.46042 | 0 | 0 | 0 | 0
2021-12-20 23:00 | 0.55945 | 1.0826 | 0.55128 | 1.2997 | 0 | 0 | 0 | 0
2021-12-20 23:15 | 0.56354 | 1.0826 | 0.62479 | 1.345 | 0 | 0 | 0 | 0
2021-12-20 23:30 | 0.56762 | 1.0961 | 0.55945 | 1.3345 | 0 | 0 | 0 | 0
2021-12-20 23:45 | 0.5717 | 1.0263 | 0.58395 | 1.3247 | 0 | 0 | 0 | 0
2021-12-21 | 0.57578 | 1.1439 | 0.60437 | 1.3305 | 0 | 0 | 0 | 0
2021-12-21 00:15 | 0.57987 | 1.1351 | 0.49003 | 1.3135 | 0 | 0 | 0 | 0
2021-12-21 00:30 | 0.58395 | 1.1287 | 0.45736 | 1.2688 | 0 | 0 | 0 | 0
2021-12-21 00:45 | 0.58804 | 1.1351 | 0.44103 | 1.2779 | 0 | 0 | 0 | 0
2021-12-21 01:00 | 0.59212 | 1.0426 | 0.32465 | 1.2214 | 0 | 0 | 0 | 0
2021-12-21 01:15 | 0.5962 | 1.0543 | 0.32158 | 1.1981 | 0 | 0 | 0 | 0
2021-12-21 01:30 | 0.5962 | 1.0721 | 0.38794 | 1.2131 | 0 | 0 | 0 | 0
2021-12-21 01:45 | 0.60029 | 1.0543 | 0.44103 | 1.1959 | 0 | 0 | 0 | 0
2021-12-21 02:00 | 0.60437 | 1.0055 | 0.33281 | 1.1742 | 0 | 0 | 0 | 0
2021-12-21 02:15 | 0.60845 | 1.0643 | 0.35731 | 1.2388 | 0 | 0 | 0 | 0
2021-12-21 02:30 | 0.61254 | 1.1565 | 0.32669 | 1.4417 | 0 | 0 | 0 | 0
2021-12-21 02:45 | 0.61662 | 1.1011 | 0.32669 | 1.4526 | 0 | 0 | 0 | 0
2021-12-21 03:00 | 0.6207 | 1.1469 | 0.42469 | 1.2663 | 0 | 0 | 0 | 0
2021-12-21 03:15 | 0.62479 | 1.0947 | 0.33383 | 1.2697 | 0 | 0 | 0 | 0
2021-12-21 03:30 | 0.62887 | 1.0188 | 0.35731 | 1.2156 | 0 | 0 | 0 | 0
2021-12-21 03:45 | 0.62887 | 1.001 | 0.35119 | 1.2038 | 0 | 0 | 0 | 0
2021-12-21 04:00 | 0.63296 | 1.1011 | 0.43286 | 1.3155 | 0 | 0 | 0 | 0
2021-12-21 04:15 | 0.63704 | 1.1023 | 0.35833 | 1.4546 | 0 | 0 | 0 | 0
2021-12-21 04:30 | 0.64112 | 0.94901 | 0.36956 | 0.94345 | 0 | 0 | 0 | 0
2021-12-21 04:45 | 0.64521 | 0.98061 | 0.3226 | 0.83626 | 0 | 0 | 0 | 0
2021-12-21 05:00 | 0.64929 | 0.95005 | 0.36344 | 0.80257 | 0 | 0 | 0 | 0
2021-12-21 05:15 | 0.65337 | 0.94352 | 0.31954 | 0.7543 | 0 | 0 | 0 | 0
2021-12-21 05:30 | 0.65746 | 0.90409 | 0.42469 | 0.79776 | 0 | 0 | 0 | 0
2021-12-21 05:45 | 0.66154 | 0.99354 | 0.72688 | 0.84749 | 0 | 0 | 0 | 0
2021-12-21 06:00 | 0.66562 | 0.94352 | 0.51045 | 0.78915 | 0 | 0 | 0 | 0
2021-12-21 06:15 | 0.66562 | 0.93812 | 0.38182 | 0.7508 | 0 | 0 | 0 | 0
2021-12-21 06:30 | 0.66971 | 0.8987 | 0.42878 | 0.79761 | 0 | 0 | 0 | 0
2021-12-21 06:45 | 0.67379 | 0.8987 | 0.43694 | 0.7998 | 0 | 0 | 0 | 0
2021-12-21 07:00 | 0.67788 | 0.6376 | 0.44103 | 0.37832 | 0 | 0 | 0 | 0
2021-12-21 07:15 | 0.68196 | 0.64897 | 0.42061 | 0.34579 | 0 | 0 | 0 | 0
2021-12-21 07:30 | 0.68604 | 0.67162 | 0.39815 | 0.38648 | 0 | 0 | 0 | 0
2021-12-21 07:45 | 0.69013 | 0.99893 | 0.37161 | 0.63296 | 0.006193 | 0.006433 | 0.001713 | 0.000921
2021-12-21 08:00 | 0.69421 | 1.1794 | 0.35833 | 1.096 | 0.076819 | 0.055709 | 0.019577 | 0.008935
2021-12-21 08:15 | 0.69829 | 1.2512 | 0.47778 | 1.1648 | 0.14745 | 0.10203 | 0.03744 | 0.016948
2021-12-21 08:30 | 0.69829 | 1.3008 | 0.41244 | 1.0541 | 0.21807 | 0.16372 | 0.055304 | 0.024962
2021-12-21 08:45 | 0.70238 | 1.2339 | 0.31852 | 1.1285 | 0.28747 | 0.17712 | 0.076265 | 0.034559
2021-12-21 09:00 | 0.70646 | 1.2167 | 0.39202 | 0.77938 | 0.34409 | 0.17194 | 0.12655 | 0.054943
2021-12-21 09:15 | 0.71054 | 1.265 | 0.42878 | 0.63121 | 0.40071 | 0.12051 | 0.17684 | 0.075328
2021-12-21 09:30 | 0.71463 | 1.1906 | 0.48595 | 0.64462 | 0.45734 | 0.13495 | 0.22713 | 0.095713
2021-12-21 09:45 | 0.60437 | 1.2072 | 0.5472 | 0.96664 | 0.51062 | 0.15929 | 0.27385 | 0.11457
2021-12-21 10:00 | 0.65337 | 1.1786 | 0.44103 | 0.96227 | 0.52891 | 0.18164 | 0.28669 | 0.12485
2021-12-21 10:15 | 0.61662 | 1.251 | 0.46553 | 0.9926 | 0.5472 | 0.18977 | 0.29952 | 0.13513
2021-12-21 10:30 | 0.51862 | 1.383 | 0.94739 | 1.4199 | 0.56549 | 0.19791 | 0.31236 | 0.14542
2021-12-21 10:45 | 0.6207 | 1.3484 | 0.98006 | 1.3569 | 0.58218 | 0.20125 | 0.32139 | 0.15712
2021-12-21 11:00 | 0.6207 | 1.1852 | 0.44919 | 0.95993 | 0.58211 | 0.17697 | 0.29407 | 0.1755
2021-12-21 11:15 | 0.46553 | 1.2549 | 1.858 | 1.3054 | 0.58204 | 0.15779 | 0.26675 | 0.19388
2021-12-21 11:30 | 0.50636 | 1.2899 | 1.6028 | 1.4126 | 0.58197 | 0.1726 | 0.23944 | 0.21226
2021-12-21 11:45 | 0.46144 | 1.2516 | 1.5824 | 1.1519 | 0.58183 | 0.18599 | 0.21678 | 0.22804
2021-12-21 12:00 | 0.35221 | 1.2275 | 2.7666 | 1.2588 | 0.58099 | 0.18793 | 0.23875 | 0.22797
2021-12-21 12:15 | 0.3471 | 1.1863 | 1.0005 | 0.96081 | 0.58016 | 0.18988 | 0.26072 | 0.2279
2021-12-21 12:30 | 0.40223 | 1.1863 | 0.42061 | 0.87739 | 0.57932 | 0.21246 | 0.2827 | 0.22783
2021-12-21 12:45 | 0.3369 | 1.1863 | 0.39202 | 0.86193 | 0.57851 | 0.21444 | 0.29638 | 0.22789
2021-12-21 13:00 | 0.28993 | 1.3116 | 0.46553 | 1.5496 | 0.57789 | 0.19407 | 0.23036 | 0.22513
2021-12-21 13:15 | 1.3272 | 1.4013 | 0.57987 | 1.4826 | 0.57727 | 0.19454 | 0.16434 | 0.22238
2021-12-21 13:30 | 0.72688 | 1.2204 | 0.7963 | 0.97627 | 0.57665 | 0.19096 | 0.098324 | 0.21962
2021-12-21 13:45 | 0.26033 | 1.2291 | 0.42878 | 0.89606 | 0.57368 | 0.18952 | 0.037997 | 0.21622
2021-12-21 14:00 | 0.31239 | 1.2407 | 0.89022 | 0.98575 | 0.54566 | 0.18086 | 0.032643 | 0.2094
2021-12-21 14:15 | 0.36752 | 1.2116 | 1.3782 | 1.0254 | 0.51763 | 0.1722 | 0.027288 | 0.20257
2021-12-21 14:30 | 0.46144 | 1.1858 | 1.1842 | 0.97233 | 0.48961 | 0.16354 | 0.021934 | 0.19575
2021-12-21 14:45 | 0.41244 | 1.2407 | 1.123 | 1.0159 | 0.45747 | 0.15258 | 0.016681 | 0.18559
2021-12-21 15:00 | 0.41244 | 1.1762 | 1.2659 | 0.9996 | 0.38117 | 0.13765 | 0.012411 | 0.15076
2021-12-21 15:15 | 0.46961 | 1.2052 | 4.1879 | 1.1296 | 0.30487 | 0.11955 | 0.008142 | 0.11592
2021-12-21 15:30 | 0.46961 | 1.0545 | 2.1337 | 0.66504 | 0.22856 | 0.082388 | 0.003872 | 0.081088
2021-12-21 15:45 | 1.6539 | 0.99235 | 1.1944 | 0.46538 | 0.15537 | 0.041845 | 0 | 0.048847
2021-12-21 16:00 | 3.7161 | 1.1844 | 3.8182 | 0.82328 | 0.11569 | 0.031213 | 0 | 0.036266
2021-12-21 16:15 | 3.5833 | 1.1685 | 4.1677 | 1.0876 | 0.076006 | 0.021479 | 0 | 0.023684
2021-12-21 16:30 | 3.5936 | 1.1394 | 1.9397 | 1.1045 | 0.036325 | 0.010799 | 0 | 0.011103
2021-12-21 16:45 | 3.5221 | 1.14 | 1.9805 | 1.1161 | 0 | 0 | 0 | 0
2021-12-21 17:00 | 3.5731 | 1.1086 | 2.001 | 1.0924 | 0 | 0 | 0 | 0
2021-12-21 17:15 | 3.7569 | 1.2756 | 0.41653 | 1.0044 | 0 | 0 | 0 | 0
2021-12-21 17:30 | 3.6854 | 1.1129 | 0.20724 | 0.49936 | 0 | 0 | 0 | 0
2021-12-21 17:45 | 1.6028 | 1.2207 | 0.2103 | 0.57491 | 0 | 0 | 0 | 0
2021-12-21 18:00 | 1.7151 | 1.1001 | 0.28483 | 0.54005 | 0 | 0 | 0 | 0
2021-12-21 18:15 | 0.35833 | 1.4793 | 0.37161 | 0.60568 | 0 | 0 | 0 | 0
2021-12-21 18:30 | 0.76363 | 1.3719 | 0.35731 | 0.7613 | 0 | 0 | 0 | 0
2021-12-21 18:45 | 0.43286 | 1.3212 | 0.27973 | 0.75444 | 0 | 0 | 0 | 0
2021-12-21 19:00 | 0.40427 | 1.2443 | 0.26952 | 0.88847 | 0 | 0 | 0 | 0
2021-12-21 19:15 | 0.59212 | 1.3445 | 0.32465 | 1.0833 | 0 | 0 | 0 | 0
2021-12-21 19:30 | 0.77588 | 1.3318 | 2.5114 | 1.0746 | 0 | 0 | 0 | 0
2021-12-21 19:45 | 0.89022 | 1.6415 | 4.7406 | 2.0123 | 0 | 0 | 0 | 0
2021-12-21 20:00 | 0.61254 | 1.1156 | 1.1026 | 1.025 | 0 | 0 | 0 | 0
2021-12-21 20:15 | 0.46144 | 1.1609 | 0.4982 | 0.87885 | 0 | 0 | 0 | 0
2021-12-21 20:30 | 0.49003 | 1.0743 | 0.52678 | 0.93864 | 0 | 0 | 0 | 0
2021-12-21 20:45 | 0.46961 | 1.0474 | 0.52678 | 0.66402 | 0 | 0 | 0 | 0
2021-12-21 21:00 | 0.40223 | 1.1971 | 0.53087 | 0.65673 | 0 | 0 | 0 | 0
2021-12-21 21:15 | 0.40734 | 1.1199 | 0.53495 | 0.58118 | 0 | 0 | 0 | 0
2021-12-21 21:30 | 0.56354 | 1.1857 | 0.53903 | 0.62421 | 0 | 0 | 0 | 0
2021-12-21 21:45 | 0.66971 | 1.1469 | 0.54312 | 0.65921 | 0 | 0 | 0 | 0
2021-12-21 22:00 | 0.39509 | 0.81158 | 0.5472 | 0.53203 | 0 | 0 | 0 | 0
2021-12-21 22:15 | 0.39713 | 0.70158 | 0.55128 | 0.48201 | 0 | 0 | 0 | 0
2021-12-21 22:30 | 0.40019 | 0.69808 | 0.55537 | 0.49586 | 0 | 0 | 0 | 0
2021-12-21 22:45 | 0.37058 | 0.69918 | 0.55945 | 0.47268 | 0 | 0 | 0 | 0
2021-12-21 23:00 | 3.3179 | 1.1286 | 0.55945 | 1.3114 | 0 | 0 | 0 | 0
2021-12-21 23:15 | 3.3894 | 1.2286 | 0.56354 | 1.3566 | 0 | 0 | 0 | 0
2021-12-21 23:30 | 3.3587 | 1.2718 | 0.56762 | 1.3508 | 0 | 0 | 0 | 0
2021-12-21 23:45 | 3.3894 | 1.2967 | 0.5717 | 1.3469 | 0 | 0 | 0 | 0
2021-12-22 | 3.4813 | 1.1915 | 0.57578 | 1.3555 | 0 | 0 | 0 | 0
2021-12-22 00:15 | 3.4506 | 1.1582 | 0.57987 | 1.3485 | 0 | 0 | 0 | 0
2021-12-22 00:30 | 3.4302 | 1.1582 | 0.58395 | 1.3094 | 0 | 0 | 0 | 0
2021-12-22 00:45 | 3.4506 | 1.207 | 0.58804 | 1.3137 | 0 | 0 | 0 | 0
2021-12-22 01:00 | 3.4608 | 1.0697 | 0.59212 | 1.264 | 0 | 0 | 0 | 0
2021-12-22 01:15 | 3.3996 | 1.0476 | 0.5962 | 1.2432 | 0 | 0 | 0 | 0
2021-12-22 01:30 | 3.3894 | 1.113 | 0.5962 | 1.2634 | 0 | 0 | 0 | 0
2021-12-22 01:45 | 3.4915 | 1.113 | 0.60029 | 1.247 | 0 | 0 | 0 | 0
2021-12-22 02:00 | 3.42 | 0.97635 | 0.60437 | 1.2213 | 0 | 0 | 0 | 0
2021-12-22 02:15 | 3.3894 | 1.1432 | 0.60845 | 1.269 | 0 | 0 | 0 | 0
2021-12-22 02:30 | 3.3996 | 1.1035 | 0.61254 | 1.4685 | 0 | 0 | 0 | 0
2021-12-22 02:45 | 3.4506 | 1.1035 | 0.61662 | 1.4869 | 0 | 0 | 0 | 0
2021-12-22 03:00 | 3.4404 | 1.1492 | 0.6207 | 1.3111 | 0 | 0 | 0 | 0
2021-12-22 03:15 | 3.4506 | 1.1416 | 0.62479 | 1.3212 | 0 | 0 | 0 | 0
2021-12-22 03:30 | 3.4915 | 1.0978 | 0.62887 | 1.2665 | 0 | 0 | 0 | 0
2021-12-22 03:45 | 3.4813 | 1.0583 | 0.62887 | 1.2563 | 0 | 0 | 0 | 0
2021-12-22 04:00 | 2.787 | 1.1363 | 0.63296 | 1.3625 | 0 | 0 | 0 | 0
2021-12-22 04:15 | 1.7457 | 1.0658 | 0.63704 | 1.4838 | 0 | 0 | 0 | 0
2021-12-22 04:30 | 0.88205 | 0.89582 | 0.64112 | 0.98137 | 0 | 0 | 0 | 0
2021-12-22 04:45 | 0.90247 | 0.92648 | 0.64521 | 0.88906 | 0 | 0 | 0 | 0
2021-12-22 05:00 | 0.42878 | 0.89591 | 0.64929 | 0.85522 | 0 | 0 | 0 | 0
2021-12-22 05:15 | 0.24399 | 0.89822 | 0.65337 | 0.81293 | 0 | 0 | 0 | 0
2021-12-22 05:30 | 0.31648 | 0.84235 | 0.65746 | 0.84953 | 0 | 0 | 0 | 0
2021-12-22 05:45 | 0.47778 | 0.83356 | 0.66154 | 0.88074 | 0 | 0 | 0 | 0
2021-12-22 06:00 | 0.59212 | 0.88938 | 0.66562 | 0.84501 | 0 | 0 | 0 | 0
2021-12-22 06:15 | 0.22766 | 0.90808 | 0.66562 | 0.8084 | 0 | 0 | 0 | 0
2021-12-22 06:30 | 0.31444 | 0.85226 | 0.66971 | 0.85872 | 0 | 0 | 0 | 0
2021-12-22 06:45 | 0.34506 | 0.86105 | 0.67379 | 0.85157 | 0 | 0 | 0 | 0
2021-12-22 07:00 | 0.42061 | 0.61774 | 0.67788 | 0.42528 | 0 | 0 | 0 | 0
2021-12-22 07:15 | 0.36854 | 0.63752 | 0.68196 | 0.4015 | 0 | 0 | 0 | 0
2021-12-22 07:30 | 0.32158 | 0.65175 | 0.68604 | 0.4403 | 0 | 0 | 0 | 0
2021-12-22 07:45 | 0.28891 | 0.80268 | 0.69013 | 0.64987 | 0.000572 | 0.007002 | 0.006193 | 0.001607
2021-12-22 08:00 | 1.2251 | 1.1239 | 0.69421 | 1.0943 | 0.007777 | 0.047468 | 0.076819 | 0.018341
2021-12-22 08:15 | 0.8208 | 1.2688 | 0.69829 | 1.1071 | 0.014981 | 0.083306 | 0.14745 | 0.035075
2021-12-22 08:30 | 0.72279 | 1.1487 | 0.69829 | 1.0384 | 0.022186 | 0.12589 | 0.21807 | 0.051809
2021-12-22 08:45 | 0.72688 | 1.1335 | 0.70238 | 1.1606 | 0.029712 | 0.17317 | 0.28747 | 0.068915
2021-12-22 09:00 | 0.42469 | 1.0206 | 0.70646 | 0.80797 | 0.040981 | 0.19428 | 0.34409 | 0.088868
2021-12-22 09:15 | 1.0821 | 1.0464 | 0.71054 | 0.66504 | 0.05225 | 0.21323 | 0.40071 | 0.10882
2021-12-22 09:30 | 0.82488 | 1.0897 | 0.71463 | 0.67379 | 0.063519 | 0.23787 | 0.45734 | 0.12877
2021-12-22 09:45 | 0.62887 | 1.1845 | 0.60437 | 0.98706 | 0.073537 | 0.25463 | 0.51062 | 0.14891
2021-12-22 10:00 | 2.6135 | 1.1347 | 0.65337 | 0.99814 | 0.068935 | 0.2714 | 0.52891 | 0.16841
2021-12-22 10:15 | 3.2975 | 1.1238 | 0.61662 | 1.0212 | 0.064333 | 0.27074 | 0.5472 | 0.18792
2021-12-22 10:30 | 2.491 | 1.3656 | 0.51862 | 1.4333 | 0.059731 | 0.27979 | 0.56549 | 0.20743
2021-12-22 10:45 | 0.61662 | 1.3209 | 0.6207 | 1.3733 | 0.056826 | 0.28805 | 0.58218 | 0.22616
2021-12-22 11:00 | 2.787 | 1.1845 | 0.6207 | 0.98035 | 0.073862 | 0.28801 | 0.58211 | 0.23752
2021-12-22 11:15 | 2.2153 | 1.3158 | 0.46553 | 1.3025 | 0.090898 | 0.28798 | 0.58204 | 0.24887
2021-12-22 11:30 | 0.62887 | 1.324 | 0.50636 | 1.4109 | 0.10793 | 0.27685 | 0.58197 | 0.26022
2021-12-22 11:45 | 0.51045 | 1.2532 | 0.46144 | 1.1303 | 0.12251 | 0.27678 | 0.58183 | 0.27089
2021-12-22 12:00 | 0.51045 | 1.3205 | 0.35221 | 1.2344 | 0.10804 | 0.27639 | 0.58099 | 0.2771
2021-12-22 12:15 | 0.51862 | 1.2268 | 0.3471 | 0.96198 | 0.093567 | 0.27599 | 0.58016 | 0.28331
2021-12-22 12:30 | 0.60845 | 1.1243 | 0.40223 | 0.88526 | 0.079096 | 0.27559 | 0.57932 | 0.28953
2021-12-22 12:45 | 0.64112 | 1.1361 | 0.3369 | 0.86368 | 0.065958 | 0.2752 | 0.57851 | 0.29524
2021-12-22 13:00 | 1.0821 | 1.3094 | 0.28993 | 1.544 | 0.06863 | 0.27491 | 0.57789 | 0.29447
2021-12-22 13:15 | 0.48186 | 1.2871 | 1.3272 | 1.541 | 0.071302 | 0.27461 | 0.57727 | 0.29369
2021-12-22 13:30 | 0.60437 | 1.1269 | 0.72688 | 1.0219 | 0.073975 | 0.24623 | 0.57665 | 0.29292
2021-12-22 13:45 | 1.0515 | 1.1441 | 0.26033 | 0.88745 | 0.075449 | 0.20683 | 0.57368 | 0.29103
2021-12-22 14:00 | 1.3986 | 1.2422 | 0.31239 | 0.98283 | 0.06265 | 0.17968 | 0.54566 | 0.28133
2021-12-22 14:15 | 0.4982 | 1.2162 | 0.36752 | 1.0348 | 0.049851 | 0.16683 | 0.51763 | 0.27164
2021-12-22 14:30 | 0.43286 | 1.2162 | 0.46144 | 0.99523 | 0.037053 | 0.15779 | 0.48961 | 0.26195
2021-12-22 14:45 | 0.33281 | 1.2166 | 0.41244 | 1.0229 | 0.025605 | 0.14744 | 0.45747 | 0.24826
2021-12-22 15:00 | 0.33281 | 1.1852 | 0.41244 | 0.99727 | 0.030345 | 0.12147 | 0.38117 | 0.20322
2021-12-22 15:15 | 0.33485 | 1.2174 | 0.46961 | 1.1453 | 0.035084 | 0.094158 | 0.30487 | 0.15818
2021-12-22 15:30 | 0.35323 | 1.0519 | 0.46961 | 0.68502 | 0.039824 | 0.076177 | 0.22856 | 0.11314
2021-12-22 15:45 | 0.45736 | 1.25 | 1.6539 | 0.65381 | 0.043352 | 0.066812 | 0.15537 | 0.071043
2021-12-22 16:00 | 0.33485 | 1.3809 | 3.7161 | 1.3067 | 0.032303 | 0.048813 | 0.11569 | 0.052792
2021-12-22 16:15 | 0.32975 | 1.2559 | 3.5833 | 1.5561 | 0.021254 | 0.023024 | 0.076006 | 0.034542
2021-12-22 16:30 | 0.32669 | 1.2842 | 3.5936 | 1.5642 | 0.010205 | 0.01044 | 0.036325 | 0.016292
2021-12-22 16:45 | 0.36038 | 1.2605 | 3.5221 | 1.5624 | 0 | 0 | 0 | 0
2021-12-22 17:00 | 0.44511 | 1.2172 | 3.5731 | 1.5599 | 0 | 0 | 0 | 0
2021-12-22 17:15 | 0.40121 | 1.1491 | 3.7569 | 1.4987 | 0 | 0 | 0 | 0
2021-12-22 17:30 | 0.33077 | 1.1208 | 3.6854 | 0.98327 | 0 | 0 | 0 | 0
2021-12-22 17:45 | 0.33281 | 1.0191 | 1.6028 | 0.74744 | 0 | 0 | 0 | 0
2021-12-22 18:00 | 0.42061 | 1.131 | 1.7151 | 0.73125 | 0 | 0 | 0 | 0
2021-12-22 18:15 | 0.38794 | 1.0024 | 0.35833 | 0.60583 | 0 | 0 | 0 | 0
2021-12-22 18:30 | 0.45736 | 0.9788 | 0.76363 | 0.81147 | 0 | 0 | 0 | 0
2021-12-22 18:45 | 2.5829 | 0.96974 | 0.43286 | 0.74861 | 0 | 0 | 0 | 0
2021-12-22 19:00 | 3.8998 | 1.046 | 0.40427 | 0.87447 | 0 | 0 | 0 | 0
2021-12-22 19:15 | 3.9304 | 1.1512 | 0.59212 | 1.0757 | 0 | 0 | 0 | 0
2021-12-22 19:30 | 4.053 | 1.1196 | 0.77588 | 1.0921 | 0 | 0 | 0 | 0
2021-12-22 19:45 | 4.1155 | 1.8738 | 0.89022 | 1.8784 | 0 | 0 | 0 | 0
2021-12-22 20:00 | 1.858 | 0.91605 | 0.61254 | 0.94622 | 0 | 0 | 0 | 0
2021-12-22 20:15 | 1.3272 | 0.88974 | 0.46144 | 0.77267 | 0 | 0 | 0 | 0
2021-12-22 20:30 | 0.55537 | 0.88674 | 0.49003 | 0.78988 | 0 | 0 | 0 | 0
2021-12-22 20:45 | 0.93922 | 0.8791 | 0.46961 | 0.62727 | 0 | 0 | 0 | 0
2021-12-22 21:00 | 0.60437 | 1.0278 | 0.40223 | 0.61443 | 0 | 0 | 0 | 0
2021-12-22 21:15 | 0.63704 | 0.7883 | 0.40734 | 0.54312 | 0 | 0 | 0 | 0
2021-12-22 21:30 | 0.58804 | 0.89116 | 0.56354 | 0.58629 | 0 | 0 | 0 | 0
2021-12-22 21:45 | 0.5717 | 0.8259 | 0.66971 | 0.62887 | 0 | 0 | 0 | 0
2021-12-22 22:00 | 0.58395 | 0.60682 | 0.39509 | 0.50972 | 0 | 0 | 0 | 0
2021-12-22 22:15 | 0.61254 | 0.6121 | 0.39713 | 0.46582 | 0 | 0 | 0 | 0
2021-12-22 22:30 | 0.62887 | 0.60682 | 0.40019 | 0.4912 | 0 | 0 | 0 | 0
2021-12-22 22:45 | 0.64112 | 0.62821 | 0.37058 | 0.47297 | 0 | 0 | 0 | 0
2021-12-22 23:00 | 3.4302 | 2.2972 | 3.3179 | 1.7297 | 0 | 0 | 0 | 0
2021-12-22 23:15 | 3.5527 | 2.424 | 3.3894 | 1.7767 | 0 | 0 | 0 | 0
2021-12-22 23:30 | 3.5323 | 2.5431 | 3.3587 | 1.7594 | 0 | 0 | 0 | 0
2021-12-22 23:45 | 3.5833 | 2.5431 | 3.3894 | 1.7581 | 0 | 0 | 0 | 0
2021-12-23 | 3.4813 | 2.0166 | 3.4813 | 1.7869 | 0 | 0 | 0 | 0
2021-12-23 00:15 | 3.4404 | 2.0166 | 3.4506 | 1.7892 | 0 | 0 | 0 | 0
2021-12-23 00:30 | 3.4506 | 1.967 | 3.4302 | 1.7501 | 0 | 0 | 0 | 0
2021-12-23 00:45 | 3.4302 | 2.0559 | 3.4506 | 1.7384 | 0 | 0 | 0 | 0
2021-12-23 01:00 | 3.3996 | 2.0559 | 3.4608 | 1.7018 | 0 | 0 | 0 | 0
2021-12-23 01:15 | 3.4098 | 2.0559 | 3.3996 | 1.6881 | 0 | 0 | 0 | 0
2021-12-23 01:30 | 3.4404 | 2.0559 | 3.3894 | 1.7068 | 0 | 0 | 0 | 0
2021-12-23 01:45 | 3.4506 | 1.9388 | 3.4915 | 1.7059 | 0 | 0 | 0 | 0
2021-12-23 02:00 | 3.3587 | 1.8581 | 3.42 | 1.6687 | 0 | 0 | 0 | 0
2021-12-23 02:15 | 3.3587 | 1.8181 | 3.3894 | 1.6985 | 0 | 0 | 0 | 0
2021-12-23 02:30 | 3.3485 | 1.9002 | 3.3996 | 1.9069 | 0 | 0 | 0 | 0
2021-12-23 02:45 | 3.3894 | 1.9002 | 3.4506 | 1.9304 | 0 | 0 | 0 | 0
2021-12-23 03:00 | 3.4915 | 1.8581 | 3.4404 | 1.7562 | 0 | 0 | 0 | 0
2021-12-23 03:15 | 3.4302 | 1.8181 | 3.4506 | 1.754 | 0 | 0 | 0 | 0
2021-12-23 03:30 | 3.4098 | 1.8018 | 3.4915 | 1.7183 | 0 | 0 | 0 | 0
2021-12-23 03:45 | 3.3996 | 1.7646 | 3.4813 | 1.7109 | 0 | 0 | 0 | 0
2021-12-23 04:00 | 3.4098 | 1.757 | 2.787 | 1.711 | 0 | 0 | 0 | 0
2021-12-23 04:15 | 3.4302 | 1.3362 | 1.7457 | 1.6864 | 0 | 0 | 0 | 0
2021-12-23 04:30 | 3.5323 | 1.2112 | 0.88205 | 1.0591 | 0 | 0 | 0 | 0
2021-12-23 04:45 | 3.4302 | 1.1112 | 0.90247 | 0.97656 | 0 | 0 | 0 | 0
2021-12-23 05:00 | 3.42 | 0.862 | 0.42878 | 0.87476 | 0 | 0 | 0 | 0
2021-12-23 05:15 | 3.4302 | 0.88548 | 0.24399 | 0.78988 | 0 | 0 | 0 | 0
2021-12-23 05:30 | 3.4302 | 0.86665 | 0.31648 | 0.8294 | 0 | 0 | 0 | 0
2021-12-23 05:45 | 3.5629 | 0.86665 | 0.47778 | 0.90539 | 0 | 0 | 0 | 0
2021-12-23 06:00 | 3.8284 | 0.87071 | 0.59212 | 0.88716 | 0 | 0 | 0 | 0
2021-12-23 06:15 | 3.5425 | 0.87619 | 0.22766 | 0.80126 | 0 | 0 | 0 | 0
2021-12-23 06:30 | 3.5221 | 0.80694 | 0.31444 | 0.84938 | 0 | 0 | 0 | 0
2021-12-23 06:45 | 3.4915 | 0.85737 | 0.34506 | 0.83961 | 0 | 0 | 0 | 0
2021-12-23 07:00 | 0.64929 | 0.56246 | 0.42061 | 0.43592 | 0 | 0 | 0 | 0
2021-12-23 07:15 | 0.3471 | 0.54811 | 0.36854 | 0.4069 | 0 | 0 | 0 | 0
2021-12-23 07:30 | 0.32771 | 0.54574 | 0.32158 | 0.42863 | 0 | 0 | 0 | 0
2021-12-23 07:45 | 0.36752 | 0.68727 | 0.28891 | 0.55405 | 0.002499 | 0.005661 | 0.000572 | 0.001663
2021-12-23 08:00 | 3.3077 | 1.2427 | 1.2251 | 1.138 | 0.037576 | 0.036908 | 0.007777 | 0.019238
2021-12-23 08:15 | 3.5629 | 1.1702 | 0.8208 | 1.0843 | 0.072653 | 0.064081 | 0.014981 | 0.036813
2021-12-23 08:30 | 3.8488 | 1.0449 | 0.72279 | 1.0518 | 0.10773 | 0.091505 | 0.022186 | 0.054388
2021-12-23 08:45 | 3.8794 | 1.0502 | 0.72688 | 1.1618 | 0.1413 | 0.11633 | 0.029712 | 0.072168
2021-12-23 09:00 | 3.6242 | 1.0674 | 0.42469 | 0.77063 | 0.15507 | 0.11645 | 0.040981 | 0.091985
2021-12-23 09:15 | 3.5425 | 1.1501 | 1.0821 | 0.71696 | 0.16884 | 0.11378 | 0.05225 | 0.1118
2021-12-23 09:30 | 3.7467 | 0.99769 | 0.82488 | 0.70646 | 0.18262 | 0.13945 | 0.063519 | 0.13162
2021-12-23 09:45 | 3.7161 | 1.021 | 0.62887 | 0.99114 | 0.19911 | 0.15454 | 0.073537 | 0.15152
2021-12-23 10:00 | 2.8993 | 1.0539 | 2.6135 | 1.2799 | 0.25143 | 0.14967 | 0.068935 | 0.1692
2021-12-23 10:15 | 1.2659 | 1.0125 | 3.2975 | 1.389 | 0.30374 | 0.15485 | 0.064333 | 0.18688
2021-12-23 10:30 | 2.8483 | 1.0229 | 2.491 | 1.6824 | 0.35606 | 0.16002 | 0.059731 | 0.20456
2021-12-23 10:45 | 2.5522 | 1.044 | 0.61662 | 1.3581 | 0.40183 | 0.1548 | 0.056826 | 0.22215
2021-12-23 11:00 | 0.99231 | 1.0447 | 2.787 | 1.3015 | 0.36089 | 0.19714 | 0.073862 | 0.23805
2021-12-23 11:15 | 2.3379 | 1.3486 | 2.2153 | 1.5572 | 0.31995 | 0.21297 | 0.090898 | 0.25395
2021-12-23 11:30 | 1.7151 | 1.1925 | 0.62887 | 1.4085 | 0.27902 | 0.2233 | 0.10793 | 0.26985
2021-12-23 11:45 | 3.5527 | 1.2257 | 0.51045 | 1.1402 | 0.23768 | 0.22697 | 0.12251 | 0.2844
2021-12-23 12:00 | 3.614 | 1.2417 | 0.51045 | 1.242 | 0.19096 | 0.21878 | 0.10804 | 0.28834
2021-12-23 12:15 | 3.5936 | 1.021 | 0.51862 | 0.96373 | 0.14423 | 0.21846 | 0.093567 | 0.29228
2021-12-23 12:30 | 3.5629 | 1.0987 | 0.60845 | 0.89401 | 0.097513 | 0.21022 | 0.079096 | 0.29622
2021-12-23 12:45 | 3.4915 | 0.9187 | 0.64112 | 0.88935 | 0.053465 | 0.21533 | 0.065958 | 0.29997
2021-12-23 13:00 | 3.4915 | 1.3438 | 1.0821 | 1.6315 | 0.045196 | 0.22558 | 0.06863 | 0.30022
2021-12-23 13:15 | 3.4404 | 1.3073 | 0.48186 | 1.5451 | 0.036926 | 0.22626 | 0.071302 | 0.30047
2021-12-23 13:30 | 3.4098 | 1.1099 | 0.60437 | 1.0003 | 0.028657 | 0.22602 | 0.073975 | 0.30072
2021-12-23 13:45 | 3.4506 | 1.0277 | 1.0515 | 0.95891 | 0.023237 | 0.21072 | 0.075449 | 0.29958
2021-12-23 14:00 | 3.5017 | 1.0742 | 1.3986 | 1.0945 | 0.056141 | 0.19548 | 0.06265 | 0.28791
2021-12-23 14:15 | 4.0734 | 1.1099 | 0.4982 | 1.04 | 0.089046 | 0.1743 | 0.049851 | 0.27625
2021-12-23 14:30 | 4.5125 | 1.1099 | 0.43286 | 0.99581 | 0.12195 | 0.16486 | 0.037053 | 0.26458
2021-12-23 14:45 | 3.5425 | 1.1208 | 0.33281 | 1.0081 | 0.14996 | 0.15404 | 0.025605 | 0.24923
2021-12-23 15:00 | 2.8075 | 1.0788 | 0.33281 | 0.98239 | 0.11182 | 0.13121 | 0.030345 | 0.20555
2021-12-23 15:15 | 1.8376 | 1.1273 | 0.33485 | 1.1337 | 0.073676 | 0.10387 | 0.035084 | 0.16186
2021-12-23 15:30 | 1.3067 | 1.0163 | 0.35323 | 0.68852 | 0.035531 | 0.079236 | 0.039824 | 0.11818
2021-12-23 15:45 | 1.2149 | 1.1508 | 0.45736 | 0.6754 | 0 | 0.048012 | 0.043352 | 0.077171
2021-12-23 16:00 | 0.82488 | 1.1299 | 0.33485 | 1.3129 | 0 | 0.033967 | 0.032303 | 0.057359
2021-12-23 16:15 | 0.48186 | 1.0908 | 0.32975 | 1.5463 | 0 | 0.025919 | 0.021254 | 0.037547
2021-12-23 16:30 | 0.50228 | 1.088 | 0.32669 | 1.5233 | 0 | 0.01297 | 0.010205 | 0.017735
2021-12-23 16:45 | 2.0112 | 1.0138 | 0.36038 | 1.5392 | 0 | 0 | 0 | 0
2021-12-23 17:00 | 0.69013 | 1.0943 | 0.44511 | 1.557 | 0 | 0 | 0 | 0
2021-12-23 17:15 | 0.70646 | 1.172 | 0.40121 | 1.4959 | 0 | 0 | 0 | 0
2021-12-23 17:30 | 0.76771 | 1.0595 | 0.33077 | 0.94652 | 0 | 0 | 0 | 0
2021-12-23 17:45 | 0.87389 | 1.0513 | 0.33281 | 0.69056 | 0 | 0 | 0 | 0
2021-12-23 18:00 | 0.91881 | 1.0513 | 0.42061 | 0.66475 | 0 | 0 | 0 | 0
2021-12-23 18:15 | 0.98823 | 0.9253 | 0.38794 | 0.54516 | 0 | 0 | 0 | 0
2021-12-23 18:30 | 0.53495 | 1.0203 | 0.45736 | 0.77471 | 0 | 0 | 0 | 0
2021-12-23 18:45 | 0.49003 | 1.1281 | 2.5829 | 1.0213 | 0 | 0 | 0 | 0
2021-12-23 19:00 | 0.66154 | 1.1865 | 3.8998 | 1.2449 | 0 | 0 | 0 | 0
2021-12-23 19:15 | 0.73096 | 1.2353 | 3.9304 | 1.1807 | 0 | 0 | 0 | 0
2021-12-23 19:30 | 0.7473 | 1.219 | 4.053 | 1.5136 | 0 | 0 | 0 | 0
2021-12-23 19:45 | 0.90656 | 1.2593 | 4.1155 | 1.9486 | 0 | 0 | 0 | 0
2021-12-23 20:00 | 1.0209 | 0.96759 | 1.858 | 1.0352 | 0 | 0 | 0 | 0
2021-12-23 20:15 | 1.2455 | 0.87761 | 1.3272 | 0.82226 | 0 | 0 | 0 | 0
2021-12-23 20:30 | 2.0928 | 0.94268 | 0.55537 | 0.71609 | 0 | 0 | 0 | 0
2021-12-23 20:45 | 1.5722 | 0.94975 | 0.93922 | 0.63719 | 0 | 0 | 0 | 0
2021-12-23 21:00 | 1.5518 | 0.9345 | 0.60437 | 0.5981 | 0 | 0 | 0 | 0
2021-12-23 21:15 | 0.78813 | 0.86762 | 0.63704 | 0.56062 | 0 | 0 | 0 | 0
2021-12-23 21:30 | 0.98006 | 0.91553 | 0.58804 | 0.58629 | 0 | 0 | 0 | 0
2021-12-23 21:45 | 1.0046 | 0.78014 | 0.5717 | 0.58512 | 0 | 0 | 0 | 0
2021-12-23 22:00 | 1.0005 | 0.62419 | 0.58395 | 0.51322 | 0 | 0 | 0 | 0
2021-12-23 22:15 | 0.84938 | 0.63625 | 0.61254 | 0.48974 | 0 | 0 | 0 | 0
2021-12-23 22:30 | 0.72279 | 0.61486 | 0.62887 | 0.50345 | 0 | 0 | 0 | 0
2021-12-23 22:45 | 0.71871 | 0.61486 | 0.64112 | 0.50563 | 0 | 0 | 0 | 0
2021-12-23 23:00 | 0.72279 | 1.9315 | 3.4302 | 1.7457 | 0 | 0 | 0 | 0
2021-12-23 23:15 | 0.7963 | 2.2329 | 3.5527 | 1.7912 | 0 | 0 | 0 | 0
2021-12-23 23:30 | 0.89022 | 1.9733 | 3.5323 | 1.7667 | 0 | 0 | 0 | 0
2021-12-23 23:45 | 0.88614 | 1.9058 | 3.5833 | 1.7771 | 0 | 0 | 0 | 0
2021-12-24 | 0.86572 | 2.111 | 3.4813 | 1.7927 | 0 | 0 | 0 | 0
2021-12-24 00:15 | 0.77997 | 2.1326 | 3.4404 | 1.7877 | 0 | 0 | 0 | 0
2021-12-24 00:30 | 0.66971 | 2.1297 | 3.4506 | 1.7443 | 0 | 0 | 0 | 0
2021-12-24 00:45 | 0.64521 | 2.1297 | 3.4302 | 1.7326 | 0 | 0 | 0 | 0
2021-12-24 01:00 | 0.66154 | 2.2004 | 3.3996 | 1.6945 | 0 | 0 | 0 | 0
2021-12-24 01:15 | 0.66154 | 2.2004 | 3.4098 | 1.6925 | 0 | 0 | 0 | 0
2021-12-24 01:30 | 0.58804 | 2.1297 | 3.4404 | 1.7126 | 0 | 0 | 0 | 0
2021-12-24 01:45 | 0.59212 | 2.17 | 3.4506 | 1.7118 | 0 | 0 | 0 | 0
2021-12-24 02:00 | 0.62887 | 2.1097 | 3.3587 | 1.6687 | 0 | 0 | 0 | 0
2021-12-24 02:15 | 0.65337 | 2.1097 | 3.3587 | 1.6824 | 0 | 0 | 0 | 0
2021-12-24 02:30 | 0.58395 | 1.896 | 3.3485 | 1.9069 | 0 | 0 | 0 | 0
2021-12-24 02:45 | 0.58395 | 1.896 | 3.3894 | 1.9347 | 0 | 0 | 0 | 0
2021-12-24 03:00 | 0.70646 | 1.9424 | 3.4915 | 1.7548 | 0 | 0 | 0 | 0
2021-12-24 03:15 | 0.62479 | 1.9424 | 3.4302 | 1.738 | 0 | 0 | 0 | 0
2021-12-24 03:30 | 0.63296 | 1.9778 | 3.4098 | 1.7227 | 0 | 0 | 0 | 0
2021-12-24 03:45 | 0.59212 | 2.0112 | 3.3996 | 1.7167 | 0 | 0 | 0 | 0
2021-12-24 04:00 | 0.68196 | 1.8531 | 3.4098 | 1.711 | 0 | 0 | 0 | 0
2021-12-24 04:15 | 0.59212 | 1.724 | 3.4302 | 1.8833 | 0 | 0 | 0 | 0
2021-12-24 04:30 | 0.59212 | 1.5507 | 3.5323 | 1.4284 | 0 | 0 | 0 | 0
2021-12-24 04:45 | 0.64929 | 1.7104 | 3.4302 | 1.3435 | 0 | 0 | 0 | 0
2021-12-24 05:00 | 0.5962 | 1.6727 | 3.42 | 1.2927 | 0 | 0 | 0 | 0
2021-12-24 05:15 | 0.64929 | 1.4798 | 3.4302 | 1.2417 | 0 | 0 | 0 | 0
2021-12-24 05:30 | 0.77588 | 1.5749 | 3.4302 | 1.2723 | 0 | 0 | 0 | 0
2021-12-24 05:45 | 0.60845 | 1.4907 | 3.5629 | 1.3782 | 0 | 0 | 0 | 0
2021-12-24 06:00 | 0.58395 | 1.5741 | 3.8284 | 1.4008 | 0 | 0 | 0 | 0
2021-12-24 06:15 | 0.58395 | 1.4726 | 3.5425 | 1.2716 | 0 | 0 | 0 | 0
2021-12-24 06:30 | 0.67379 | 1.5001 | 3.5221 | 1.2942 | 0 | 0 | 0 | 0
2021-12-24 06:45 | 0.63704 | 1.4658 | 3.4915 | 1.293 | 0 | 0 | 0 | 0
2021-12-24 07:00 | 0.64112 | 0.87111 | 0.64929 | 0.48653 | 0 | 0 | 0 | 0
2021-12-24 07:15 | 0.63296 | 0.89433 | 0.3471 | 0.41711 | 0 | 0 | 0 | 0
2021-12-24 07:30 | 0.77588 | 0.91035 | 0.32771 | 0.42703 | 0 | 0 | 0 | 0
2021-12-24 07:45 | 0.67788 | 0.77105 | 0.36752 | 0.48522 | 6.6e-05 | 0.003556 | 0.002499 | 0.00189
2021-12-24 08:00 | 0.63296 | 1.4428 | 3.3077 | 1.4428 | 0.001111 | 0.038693 | 0.037576 | 0.02347
2021-12-24 08:15 | 0.60437 | 1.5152 | 3.5629 | 1.4924 | 0.002156 | 0.073861 | 0.072653 | 0.045049
2021-12-24 08:30 | 0.61662 | 1.3555 | 3.8488 | 1.5328 | 0.003201 | 0.12055 | 0.10773 | 0.066629
2021-12-24 08:45 | 0.69421 | 1.5808 | 3.8794 | 1.6302 | 0.00431 | 0.15443 | 0.1413 | 0.08831
2021-12-24 09:00 | 1.6028 | 1.2712 | 3.6242 | 1.1839 | 0.006377 | 0.17623 | 0.15507 | 0.10996
2021-12-24 09:15 | 0.88614 | 1.166 | 3.5425 | 1.1297 | 0.008444 | 0.20132 | 0.16884 | 0.13161
2021-12-24 09:30 | 0.93514 | 1.0161 | 3.7467 | 1.1734 | 0.010512 | 0.21647 | 0.18262 | 0.15326
2021-12-24 09:45 | 0.74321 | 1.0032 | 3.7161 | 1.4421 | 0.012372 | 0.25048 | 0.19911 | 0.17523
2021-12-24 10:00 | 0.55128 | 1.1383 | 2.8993 | 1.6328 | 0.011114 | 0.2671 | 0.25143 | 0.19911
2021-12-24 10:15 | 0.47778 | 1.0032 | 1.2659 | 1.5051 | 0.009857 | 0.27355 | 0.30374 | 0.223
2021-12-24 10:30 | 0.56762 | 1.0024 | 2.8483 | 2.0222 | 0.008599 | 0.28775 | 0.35606 | 0.24689
2021-12-24 10:45 | 0.44103 | 0.9956 | 2.5522 | 1.6492 | 0.008358 | 0.2713 | 0.40183 | 0.26994
2021-12-24 11:00 | 0.44511 | 1.0172 | 0.99231 | 1.3622 | 0.023489 | 0.29126 | 0.36089 | 0.28021
2021-12-24 11:15 | 0.63704 | 1.0675 | 2.3379 | 1.6315 | 0.03862 | 0.29123 | 0.31995 | 0.29049
2021-12-24 11:30 | 0.69829 | 0.93369 | 1.7151 | 1.2656 | 0.053752 | 0.29751 | 0.27902 | 0.30076
2021-12-24 11:45 | 0.68196 | 0.9185 | 3.5527 | 1.5392 | 0.067335 | 0.29619 | 0.23768 | 0.30941
2021-12-24 12:00 | 0.55128 | 0.94386 | 3.614 | 1.6655 | 0.057366 | 0.29577 | 0.19096 | 0.30518
2021-12-24 12:15 | 0.56354 | 0.97718 | 3.5936 | 1.3972 | 0.047397 | 0.27769 | 0.14423 | 0.30095
2021-12-24 12:30 | 0.60845 | 1.0738 | 3.5629 | 1.3544 | 0.037428 | 0.26555 | 0.097513 | 0.29673
2021-12-24 12:45 | 1.0617 | 0.97596 | 3.4915 | 1.3222 | 0.027857 | 0.24295 | 0.053465 | 0.29215
2021-12-24 13:00 | 0.64521 | 0.97596 | 3.4915 | 1.6884 | 0.024377 | 0.25846 | 0.045196 | 0.28549
2021-12-24 13:15 | 0.94331 | 0.99038 | 3.4404 | 1.8557 | 0.020897 | 0.25818 | 0.036926 | 0.27883
2021-12-24 13:30 | 0.98006 | 0.96456 | 3.4098 | 1.4412 | 0.017418 | 0.24711 | 0.028657 | 0.27217
2021-12-24 13:45 | 1.4497 | 1.03 | 3.4506 | 1.4195 | 0.013965 | 0.24584 | 0.023237 | 0.26489
2021-12-24 14:00 | 1.1944 | 0.99322 | 3.5017 | 1.5621 | 0.010925 | 0.22916 | 0.056141 | 0.25516
2021-12-24 14:15 | 0.97598 | 0.94525 | 4.0734 | 1.5895 | 0.007885 | 0.20515 | 0.089046 | 0.24543
2021-12-24 14:30 | 0.54312 | 0.99603 | 4.5125 | 1.6069 | 0.004845 | 0.18577 | 0.12195 | 0.23569
2021-12-24 14:45 | 0.57987 | 0.97868 | 3.5425 | 1.4663 | 0.00196 | 0.19113 | 0.14996 | 0.22296
2021-12-24 15:00 | 0.99639 | 0.95582 | 2.8075 | 1.3406 | 0.001462 | 0.16508 | 0.11182 | 0.18198
2021-12-24 15:15 | 1.3986 | 1.015 | 1.8376 | 1.3629 | 0.000965 | 0.13272 | 0.073676 | 0.141
2021-12-24 15:30 | 1.5518 | 0.85138 | 1.3067 | 0.84297 | 0.000467 | 0.10507 | 0.035531 | 0.10003
2021-12-24 15:45 | 1.2557 | 0.9126 | 1.2149 | 0.81424 | 0 | 0.053609 | 0 | 0.061581
2021-12-24 16:00 | 1.1026 | 1.0229 | 0.82488 | 1.3945 | 0 | 0.039994 | 0 | 0.045793
2021-12-24 16:15 | 0.98823 | 0.97613 | 0.48186 | 1.5712 | 0 | 0.024494 | 0 | 0.030005
2021-12-24 16:30 | 2.4297 | 0.90262 | 0.50228 | 1.5563 | 0 | 0.013561 | 0 | 0.014217
2021-12-24 16:45 | 4.5553 | 1.1365 | 2.0112 | 1.7943 | 0 | 0 | 0 | 0
2021-12-24 17:00 | 3.91 | 1.0111 | 0.69013 | 1.6232 | 0 | 0 | 0 | 0
2021-12-24 17:15 | 3.7059 | 1.2252 | 0.70646 | 1.5534 | 0 | 0 | 0 | 0
2021-12-24 17:30 | 3.7161 | 1.085 | 0.76771 | 0.99887 | 0 | 0 | 0 | 0
2021-12-24 17:45 | 1.5109 | 1.0451 | 0.87389 | 0.77413 | 0 | 0 | 0 | 0
2021-12-24 18:00 | 0.58395 | 1.1819 | 0.91881 | 0.75823 | 0 | 0 | 0 | 0
2021-12-24 18:15 | 0.83713 | 1.0515 | 0.98823 | 0.64914 | 0 | 0 | 0 | 0
2021-12-24 18:30 | 0.69013 | 1.1157 | 0.53495 | 0.80942 | 0 | 0 | 0 | 0
2021-12-24 18:45 | 0.50228 | 1.1258 | 0.49003 | 1.046 | 0 | 0 | 0 | 0
2021-12-24 19:00 | 0.55945 | 1.3973 | 0.66154 | 1.2764 | 0 | 0 | 0 | 0
2021-12-24 19:15 | 0.56762 | 1.125 | 0.73096 | 1.2362 | 0 | 0 | 0 | 0
2021-12-24 19:30 | 0.61662 | 1.4512 | 0.7473 | 1.5731 | 0 | 0 | 0 | 0
2021-12-24 19:45 | 0.69421 | 1.6297 | 0.90656 | 2.0407 | 0 | 0 | 0 | 0
2021-12-24 20:00 | 0.58804 | 1.1427 | 1.0209 | 1.1344 | 0 | 0 | 0 | 0
2021-12-24 20:15 | 0.51045 | 1.0052 | 1.2455 | 0.94214 | 0 | 0 | 0 | 0
2021-12-24 20:30 | 0.53903 | 0.85604 | 2.0928 | 0.96927 | 0 | 0 | 0 | 0
2021-12-24 20:45 | 0.5472 | 0.79825 | 1.5722 | 0.81205 | 0 | 0 | 0 | 0
2021-12-24 21:00 | 0.56762 | 0.81105 | 1.5518 | 0.77967 | 0 | 0 | 0 | 0
2021-12-24 21:15 | 0.58395 | 1.0709 | 0.78813 | 0.62931 | 0 | 0 | 0 | 0
2021-12-24 21:30 | 0.50636 | 1.0709 | 0.98006 | 0.66796 | 0 | 0 | 0 | 0
2021-12-24 21:45 | 0.46553 | 1.0161 | 1.0046 | 0.64054 | 0 | 0 | 0 | 0
2021-12-24 22:00 | 0.54312 | 1.0101 | 1.0005 | 0.56456 | 0 | 0 | 0 | 0
2021-12-24 22:15 | 0.53087 | 1.0579 | 0.84938 | 0.55435 | 0 | 0 | 0 | 0
2021-12-24 22:30 | 0.63296 | 1.0579 | 0.72279 | 0.53903 | 0 | 0 | 0 | 0
2021-12-24 22:45 | 0.57987 | 1.0579 | 0.71871 | 0.53889 | 0 | 0 | 0 | 0
2021-12-24 23:00 | 0.51862 | 1.3319 | 0.72279 | 1.3677 | 0 | 0 | 0 | 0
2021-12-24 23:15 | 0.53495 | 1.2505 | 0.7963 | 1.4106 | 0 | 0 | 0 | 0
2021-12-24 23:30 | 0.55945 | 1.2782 | 0.89022 | 1.401 | 0 | 0 | 0 | 0
2021-12-24 23:45 | 0.60437 | 1.2505 | 0.88614 | 1.4107 | 0 | 0 | 0 | 0
2021-12-25 | 0.51862 | 0.98759 | 0.86572 | 1.4205 | 0 | 0 | 0 | 0
2021-12-25 00:15 | 0.54312 | 1.0369 | 0.77997 | 1.3916 | 0 | 0 | 0 | 0
2021-12-25 00:30 | 0.63296 | 1.0024 | 0.66971 | 1.3499 | 0 | 0 | 0 | 0
2021-12-25 00:45 | 0.49411 | 1.0274 | 0.64521 | 1.3318 | 0 | 0 | 0 | 0
2021-12-25 01:00 | 0.44511 | 1.0609 | 0.66154 | 1.3019 | 0 | 0 | 0 | 0
2021-12-25 01:15 | 0.3859 | 1.0609 | 0.66154 | 1.297 | 0 | 0 | 0 | 0
2021-12-25 01:30 | 0.42878 | 1.0274 | 0.58804 | 1.3081 | 0 | 0 | 0 | 0
2021-12-25 01:45 | 0.31648 | 1.0609 | 0.59212 | 1.318 | 0 | 0 | 0 | 0
2021-12-25 02:00 | 0.28483 | 1.0449 | 0.62887 | 1.2787 | 0 | 0 | 0 | 0
2021-12-25 02:15 | 0.28279 | 1.0537 | 0.65337 | 1.2974 | 0 | 0 | 0 | 0
2021-12-25 02:30 | 0.35119 | 1.003 | 0.58395 | 1.4915 | 0 | 0 | 0 | 0
2021-12-25 02:45 | 0.40427 | 1.003 | 0.58395 | 1.5194 | 0 | 0 | 0 | 0
2021-12-25 03:00 | 0.30218 | 1.0456 | 0.70646 | 1.3686 | 0 | 0 | 0 | 0
2021-12-25 03:15 | 0.28993 | 1.0202 | 0.62479 | 1.3445 | 0 | 0 | 0 | 0
2021-12-25 03:30 | 0.40019 | 1.0097 | 0.63296 | 1.3187 | 0 | 0 | 0 | 0
2021-12-25 03:45 | 0.37875 | 1.0097 | 0.59212 | 1.3025 | 0 | 0 | 0 | 0
2021-12-25 04:00 | 0.3859 | 1.0615 | 0.68196 | 1.3199 | 0 | 0 | 0 | 0
2021-12-25 04:15 | 0.33587 | 1.058 | 0.59212 | 1.4764 | 0 | 0 | 0 | 0
2021-12-25 04:30 | 0.32362 | 0.94189 | 0.59212 | 1.0259 | 0 | 0 | 0 | 0
2021-12-25 04:45 | 0.42469 | 0.90813 | 0.64929 | 0.95206 | 0 | 0 | 0 | 0
2021-12-25 05:00 | 0.41653 | 0.88808 | 0.5962 | 0.87622 | 0 | 0 | 0 | 0
2021-12-25 05:15 | 0.34404 | 0.78039 | 0.64929 | 0.8488 | 0 | 0 | 0 | 0
2021-12-25 05:30 | 0.3859 | 0.83312 | 0.77588 | 0.90189 | 0 | 0 | 0 | 0
2021-12-25 05:45 | 0.33996 | 0.91368 | 0.60845 | 0.97364 | 0 | 0 | 0 | 0
2021-12-25 06:00 | 0.49411 | 0.9479 | 0.58395 | 0.98546 | 0 | 0 | 0 | 0
2021-12-25 06:15 | 0.39202 | 0.85289 | 0.58395 | 0.87374 | 0 | 0 | 0 | 0
2021-12-25 06:30 | 0.39304 | 0.80508 | 0.67379 | 0.90481 | 0 | 0 | 0 | 0
2021-12-25 06:45 | 0.3471 | 0.83516 | 0.63704 | 0.8911 | 0 | 0 | 0 | 0
2021-12-25 07:00 | 0.44511 | 0.62791 | 0.64112 | 0.50636 | 0 | 0 | 0 | 0
2021-12-25 07:15 | 0.41244 | 0.62248 | 0.63296 | 0.46786 | 0 | 0 | 0 | 0
2021-12-25 07:30 | 0.39917 | 0.65387 | 0.77588 | 0.48857 | 0 | 0 | 0 | 0
2021-12-25 07:45 | 0.34404 | 0.75625 | 0.67788 | 0.51847 | 1.7e-05 | 0.003593 | 6.6e-05 | 0.00183
2021-12-25 08:00 | 0.31648 | 1.2931 | 0.63296 | 1.0709 | 0.00033 | 0.025792 | 0.001111 | 0.022978
2021-12-25 08:15 | 0.38386 | 1.163 | 0.60437 | 0.99975 | 0.000642 | 0.053636 | 0.002156 | 0.044126
2021-12-25 08:30 | 0.34608 | 1.2076 | 0.61662 | 1.0871 | 0.000955 | 0.090407 | 0.003201 | 0.065274
2021-12-25 08:45 | 0.29096 | 1.2513 | 0.69421 | 1.2117 | 0.003955 | 0.10389 | 0.00431 | 0.08645
2021-12-25 09:00 | 0.3665 | 1.2903 | 1.6028 | 1.1796 | 0.053628 | 0.12253 | 0.006377 | 0.10712
2021-12-25 09:15 | 0.42061 | 1.2608 | 0.88614 | 1.1495 | 0.1033 | 0.14593 | 0.008444 | 0.12779
2021-12-25 09:30 | 0.52678 | 1.3631 | 0.93514 | 1.2324 | 0.15297 | 0.14721 | 0.010512 | 0.14846
2021-12-25 09:45 | 0.50228 | 1.7275 | 0.74321 | 1.4853 | 0.19904 | 0.16436 | 0.012372 | 0.16933
2021-12-25 10:00 | 0.5717 | 1.8393 | 0.55128 | 1.6212 | 0.18208 | 0.16525 | 0.011114 | 0.19102
2021-12-25 10:15 | 0.5717 | 1.4543 | 0.47778 | 1.5086 | 0.16512 | 0.17097 | 0.009857 | 0.2127
2021-12-25 10:30 | 0.4982 | 1.9689 | 0.56762 | 2.0362 | 0.14816 | 0.17135 | 0.008599 | 0.23439
2021-12-25 10:45 | 0.38386 | 1.8393 | 0.44103 | 1.6399 | 0.1314 | 0.17467 | 0.008358 | 0.25426
2021-12-25 11:00 | 0.42878 | 1.4397 | 0.44511 | 1.3394 | 0.11811 | 0.14166 | 0.023489 | 0.25527
2021-12-25 11:15 | 0.36752 | 1.8802 | 0.63704 | 1.6467 | 0.10483 | 0.15049 | 0.03862 | 0.25627
2021-12-25 11:30 | 0.49411 | 1.4653 | 0.69829 | 1.3181 | 0.091544 | 0.15047 | 0.053752 | 0.25727
2021-12-25 11:45 | 0.42469 | 1.7596 | 0.68196 | 1.5967 | 0.078722 | 0.15044 | 0.067335 | 0.25768
2021-12-25 12:00 | 0.36344 | 1.8773 | 0.55128 | 1.6967 | 0.074088 | 0.15022 | 0.057366 | 0.25113
2021-12-25 12:15 | 0.39202 | 1.6413 | 0.56354 | 1.4281 | 0.069453 | 0.15258 | 0.047397 | 0.24459
2021-12-25 12:30 | 0.39509 | 1.6672 | 0.60845 | 1.3749 | 0.064819 | 0.15091 | 0.037428 | 0.23804
2021-12-25 12:45 | 1.3476 | 1.6528 | 1.0617 | 1.4182 | 0.06023 | 0.16941 | 0.027857 | 0.23086
2021-12-25 13:00 | 3.5936 | 1.8493 | 0.64521 | 1.7271 | 0.056455 | 0.16318 | 0.024377 | 0.21991
2021-12-25 13:15 | 3.5527 | 1.8254 | 0.94331 | 1.917 | 0.05268 | 0.163 | 0.020897 | 0.20896
2021-12-25 13:30 | 3.6038 | 1.4858 | 0.98006 | 1.5278 | 0.048906 | 0.15669 | 0.017418 | 0.19801
2021-12-25 13:45 | 3.6956 | 1.6797 | 1.4497 | 1.563 | 0.045013 | 0.15187 | 0.013965 | 0.18733
2021-12-25 14:00 | 3.6548 | 1.8082 | 1.1944 | 1.6792 | 0.039001 | 0.15736 | 0.010925 | 0.18073
2021-12-25 14:15 | 1.0924 | 1.7804 | 0.97598 | 1.6763 | 0.032989 | 0.15247 | 0.007885 | 0.17414
2021-12-25 14:30 | 0.45328 | 1.7832 | 0.54312 | 1.6262 | 0.026977 | 0.14903 | 0.004845 | 0.16754
2021-12-25 14:45 | 0.36038 | 1.6558 | 0.57987 | 1.4838 | 0.021016 | 0.1317 | 0.00196 | 0.15894
2021-12-25 15:00 | 1.613 | 1.5426 | 0.99639 | 1.4293 | 0.015982 | 0.1125 | 0.001462 | 0.12976
2021-12-25 15:15 | 2.1337 | 1.4916 | 1.3986 | 1.5098 | 0.010947 | 0.090767 | 0.000965 | 0.10058
2021-12-25 15:30 | 0.44919 | 1.0644 | 1.5518 | 0.99989 | 0.005912 | 0.070865 | 0.000467 | 0.071394
2021-12-25 15:45 | 0.43694 | 1.1714 | 1.2557 | 0.92945 | 0.001125 | 0.058347 | 0 | 0.043884
2021-12-25 16:00 | 0.46553 | 1.2885 | 1.1026 | 1.4993 | 0.00084 | 0.04486 | 0 | 0.032654
2021-12-25 16:15 | 0.43286 | 1.474 | 0.98823 | 1.6605 | 0.000555 | 0.029608 | 0 | 0.021424
2021-12-25 16:30 | 0.78813 | 1.7243 | 2.4297 | 1.8452 | 0.00027 | 0.015071 | 0 | 0.010194
2021-12-25 16:45 | 3.1137 | 1.8978 | 4.5553 | 2.3564 | 0 | 0 | 0 | 0
2021-12-25 17:00 | 1.0311 | 1.7411 | 3.91 | 2.1083 | 0 | 0 | 0 | 0
2021-12-25 17:15 | 0.29708 | 1.7773 | 3.7059 | 1.8611 | 0 | 0 | 0 | 0
2021-12-25 17:30 | 0.30627 | 1.3875 | 3.7161 | 1.3991 | 0 | 0 | 0 | 0
2021-12-25 17:45 | 0.46553 | 1.03 | 1.5109 | 0.76246 | 0 | 0 | 0 | 0
2021-12-25 18:00 | 0.92289 | 1.0037 | 0.58395 | 0.71156 | 0 | 0 | 0 | 0
2021-12-25 18:15 | 0.89839 | 1.1248 | 0.83713 | 0.62814 | 0 | 0 | 0 | 0
2021-12-25 18:30 | 1.1842 | 1.1658 | 0.69013 | 0.81234 | 0 | 0 | 0 | 0
2021-12-25 18:45 | 1.1026 | 1.2821 | 0.50228 | 1.039 | 0 | 0 | 0 | 0
2021-12-25 19:00 | 0.99639 | 1.3518 | 0.55945 | 1.2642 | 0 | 0 | 0 | 0
2021-12-25 19:15 | 0.99231 | 1.2992 | 0.56762 | 1.2449 | 0 | 0 | 0 | 0
2021-12-25 19:30 | 0.92697 | 1.3721 | 0.61662 | 1.4861 | 0 | 0 | 0 | 0
2021-12-25 19:45 | 0.95147 | 1.6458 | 0.69421 | 1.8672 | 0 | 0 | 0 | 0
2021-12-25 20:00 | 2.1235 | 1.1266 | 0.58804 | 1.0375 | 0 | 0 | 0 | 0
2021-12-25 20:15 | 1.7866 | 1.0098 | 0.51045 | 0.91589 | 0 | 0 | 0 | 0
2021-12-25 20:30 | 1.3782 | 1.1195 | 0.53903 | 0.97102 | 0 | 0 | 0 | 0
2021-12-25 20:45 | 0.8698 | 0.98018 | 0.5472 | 0.7998 | 0 | 0 | 0 | 0
2021-12-25 21:00 | 0.63704 | 1.1434 | 0.56762 | 0.77559 | 0 | 0 | 0 | 0
2021-12-25 21:15 | 0.68604 | 1.0994 | 0.58395 | 0.62581 | 0 | 0 | 0 | 0
2021-12-25 21:30 | 0.57987 | 1.1191 | 0.50636 | 0.65746 | 0 | 0 | 0 | 0
2021-12-25 21:45 | 0.52678 | 0.81163 | 0.46553 | 0.63646 | 0 | 0 | 0 | 0
2021-12-25 22:00 | 0.61662 | 0.80777 | 0.54312 | 0.57097 | 0 | 0 | 0 | 0
2021-12-25 22:15 | 0.66562 | 0.67537 | 0.53087 | 0.54326 | 0 | 0 | 0 | 0
2021-12-25 22:30 | 0.62479 | 0.67537 | 0.63296 | 0.54487 | 0 | 0 | 0 | 0
2021-12-25 22:45 | 0.59212 | 0.67537 | 0.57987 | 0.5383 | 0 | 0 | 0 | 0
2021-12-25 23:00 | 0.55945 | 1.0965 | 0.51862 | 1.377 | 0 | 0 | 0 | 0
2021-12-25 23:15 | 0.51453 | 1.063 | 0.53495 | 1.4339 | 0 | 0 | 0 | 0
2021-12-25 23:30 | 0.5227 | 1.0907 | 0.55945 | 1.4284 | 0 | 0 | 0 | 0
2021-12-25 23:45 | 0.39611 | 1.083 | 0.60437 | 1.443 | 0 | 0 | 0 | 0
2021-12-26 | 0.35323 | 1.0741 | 0.51862 | 1.4304 | 0 | 0 | 0 | 0
2021-12-26 00:15 | 0.34098 | 1.0051 | 0.54312 | 1.3998 | 0 | 0 | 0 | 0
2021-12-26 00:30 | 0.37263 | 0.95841 | 0.63296 | 1.3768 | 0 | 0 | 0 | 0
2021-12-26 00:45 | 0.44103 | 1.1044 | 0.49411 | 1.3534 | 0 | 0 | 0 | 0
2021-12-26 01:00 | 0.31648 | 1.0834 | 0.44511 | 1.3162 | 0 | 0 | 0 | 0
2021-12-26 01:15 | 0.24502 | 1.0834 | 0.3859 | 1.3022 | 0 | 0 | 0 | 0
2021-12-26 01:30 | 0.25727 | 1.0922 | 0.42878 | 1.3184 | 0 | 0 | 0 | 0
2021-12-26 01:45 | 0.30014 | 1.1524 | 0.31648 | 1.3186 | 0 | 0 | 0 | 0
2021-12-26 02:00 | 0.34404 | 1.0494 | 0.28483 | 1.2742 | 0 | 0 | 0 | 0
2021-12-26 02:15 | 0.26543 | 1.0494 | 0.28279 | 1.2789 | 0 | 0 | 0 | 0
2021-12-26 02:30 | 0.28789 | 1.2816 | 0.35119 | 1.4885 | 0 | 0 | 0 | 0
2021-12-26 02:45 | 0.26237 | 1.3051 | 0.40427 | 1.5243 | 0 | 0 | 0 | 0
2021-12-26 03:00 | 0.37671 | 1.1469 | 0.30218 | 1.3619 | 0 | 0 | 0 | 0
2021-12-26 03:15 | 0.28585 | 0.99721 | 0.28993 | 1.327 | 0 | 0 | 0 | 0
2021-12-26 03:30 | 0.25931 | 1.1273 | 0.40019 | 1.3315 | 0 | 0 | 0 | 0
2021-12-26 03:45 | 0.29504 | 1.1184 | 0.37875 | 1.3126 | 0 | 0 | 0 | 0
2021-12-26 04:00 | 0.36548 | 1.3324 | 0.3859 | 1.3242 | 0 | 0 | 0 | 0
2021-12-26 04:15 | 0.342 | 1.5839 | 0.33587 | 1.4648 | 0 | 0 | 0 | 0
2021-12-26 04:30 | 0.26339 | 1.1527 | 0.32362 | 1.0137 | 0 | 0 | 0 | 0
2021-12-26 04:45 | 0.28381 | 0.83916 | 0.42469 | 0.96139 | 0 | 0 | 0 | 0
2021-12-26 05:00 | 0.33281 | 0.81911 | 0.41653 | 0.89299 | 0 | 0 | 0 | 0
2021-12-26 05:15 | 0.25114 | 0.82718 | 0.34404 | 0.85522 | 0 | 0 | 0 | 0
2021-12-26 05:30 | 0.26135 | 0.82718 | 0.3859 | 0.89751 | 0 | 0 | 0 | 0
2021-12-26 05:45 | 0.24502 | 0.98931 | 0.33996 | 0.97583 | 0 | 0 | 0 | 0
2021-12-26 06:00 | 0.41653 | 0.96402 | 0.49411 | 1.0111 | 0 | 0 | 0 | 0
2021-12-26 06:15 | 0.33077 | 0.91237 | 0.39202 | 0.87374 | 0 | 0 | 0 | 0
2021-12-26 06:30 | 0.25625 | 0.89465 | 0.39304 | 0.89853 | 0 | 0 | 0 | 0
2021-12-26 06:45 | 0.26237 | 0.89465 | 0.3471 | 0.89533 | 0 | 0 | 0 | 0
2021-12-26 07:00 | 0.2981 | 0.64534 | 0.44511 | 0.51978 | 0 | 0 | 0 | 0
2021-12-26 07:15 | 0.37569 | 0.64281 | 0.41244 | 0.46436 | 0 | 0 | 0 | 0
2021-12-26 07:30 | 0.35323 | 0.71231 | 0.39917 | 0.47034 | 0 | 0 | 0 | 0
2021-12-26 07:45 | 0.29912 | 0.78411 | 0.34404 | 0.43753 | 3.3e-05 | 0.003861 | 1.7e-05 | 0.001684
2021-12-26 08:00 | 0.27054 | 1.1097 | 0.31648 | 0.98137 | 0.000751 | 0.052174 | 0.00033 | 0.021554
2021-12-26 08:15 | 0.26339 | 1.1283 | 0.38386 | 0.98342 | 0.001468 | 0.099805 | 0.000642 | 0.041424
2021-12-26 08:30 | 0.33383 | 1.21 | 0.34608 | 1.0467 | 0.002186 | 0.14241 | 0.000955 | 0.061295
2021-12-26 08:45 | 0.37875 | 1.1947 | 0.29096 | 1.1196 | 0.00294 | 0.18069 | 0.003955 | 0.081544
2021-12-26 09:00 | 0.39917 | 1.2623 | 0.3665 | 1.1211 | 0.00445 | 0.2263 | 0.053628 | 0.10769
2021-12-26 09:15 | 0.32158 | 1.2536 | 0.42061 | 1.118 | 0.00596 | 0.24618 | 0.1033 | 0.13385
2021-12-26 09:30 | 0.33792 | 1.2862 | 0.52678 | 1.118 | 0.007469 | 0.28478 | 0.15297 | 0.16
2021-12-26 09:45 | 0.33894 | 1.2375 | 0.50228 | 1.0349 | 0.009093 | 0.31796 | 0.19904 | 0.18489
2021-12-26 10:00 | 0.49411 | 1.3025 | 0.5717 | 1.1749 | 0.013078 | 0.32935 | 0.18208 | 0.19403
2021-12-26 10:15 | 1.9091 | 1.3554 | 0.5717 | 1.0609 | 0.017062 | 0.34484 | 0.16512 | 0.20318
2021-12-26 10:30 | 1.0821 | 1.4698 | 0.4982 | 1.5678 | 0.021047 | 0.34875 | 0.14816 | 0.21232
2021-12-26 10:45 | 0.56762 | 1.3108 | 0.38386 | 1.1638 | 0.024731 | 0.34591 | 0.1314 | 0.22013
2021-12-26 11:00 | 1.2761 | 1.191 | 0.42878 | 0.88585 | 0.022116 | 0.35134 | 0.11811 | 0.21312
2021-12-26 11:15 | 1.1434 | 1.2519 | 0.36752 | 1.1815 | 0.019501 | 0.3554 | 0.10483 | 0.20611
2021-12-26 11:30 | 0.89431 | 1.214 | 0.49411 | 0.86951 | 0.016887 | 0.38742 | 0.091544 | 0.1991
2021-12-26 11:45 | 0.52678 | 1.3478 | 0.42469 | 1.125 | 0.014612 | 0.38843 | 0.078722 | 0.19216
2021-12-26 12:00 | 0.61662 | 1.307 | 0.36344 | 1.2207 | 0.019516 | 0.41454 | 0.074088 | 0.18414
2021-12-26 12:15 | 0.60437 | 1.2152 | 0.39202 | 0.97073 | 0.024421 | 0.37324 | 0.069453 | 0.17613
2021-12-26 12:30 | 3.5017 | 1.1979 | 0.39509 | 0.9121 | 0.029325 | 0.34085 | 0.064819 | 0.16811
2021-12-26 12:45 | 3.6344 | 1.2607 | 1.3476 | 1.0959 | 0.034015 | 0.33155 | 0.06023 | 0.15954
2021-12-26 13:00 | 3.5119 | 1.3519 | 3.5936 | 1.7139 | 0.034128 | 0.32283 | 0.056455 | 0.14786
2021-12-26 13:15 | 3.5221 | 1.7022 | 3.5527 | 1.8965 | 0.03424 | 0.32248 | 0.05268 | 0.13617
2021-12-26 13:30 | 3.6548 | 1.2623 | 3.6038 | 1.5293 | 0.034353 | 0.32214 | 0.048906 | 0.12449
2021-12-26 13:45 | 3.6854 | 1.2825 | 3.6956 | 1.5601 | 0.034424 | 0.33058 | 0.045013 | 0.11348
2021-12-26 14:00 | 3.6344 | 1.2945 | 3.6548 | 1.6515 | 0.033609 | 0.32883 | 0.039001 | 0.10969
2021-12-26 14:15 | 3.5527 | 1.3953 | 1.0924 | 1.3088 | 0.032794 | 0.31649 | 0.032989 | 0.10591
2021-12-26 14:30 | 3.5119 | 1.3795 | 0.45328 | 1.1644 | 0.031979 | 0.32368 | 0.026977 | 0.10212
2021-12-26 14:45 | 3.4813 | 1.1991 | 0.36038 | 0.99421 | 0.030855 | 0.30243 | 0.021016 | 0.097312
2021-12-26 15:00 | 3.4404 | 1.2705 | 1.613 | 1.1347 | 0.023056 | 0.24029 | 0.015982 | 0.079929
2021-12-26 15:15 | 3.4506 | 1.4344 | 2.1337 | 1.5812 | 0.015257 | 0.18813 | 0.010947 | 0.062545
2021-12-26 15:30 | 3.5629 | 1.153 | 0.44919 | 1.0046 | 0.007457 | 0.11649 | 0.005912 | 0.045161
2021-12-26 15:45 | 3.42 | 1.1601 | 0.43694 | 0.94068 | 0 | 0.080168 | 0.001125 | 0.02855
2021-12-26 16:00 | 3.2771 | 1.2732 | 0.46553 | 1.5243 | 0 | 0.063032 | 0.00084 | 0.021262
2021-12-26 16:15 | 3.1852 | 1.3036 | 0.43286 | 1.4963 | 0 | 0.042675 | 0.000555 | 0.013974
2021-12-26 16:30 | 3.2158 | 1.3023 | 0.78813 | 1.4444 | 0 | 0.014902 | 0.00027 | 0.006686
2021-12-26 16:45 | 3.2771 | 1.3428 | 3.1137 | 2.2776 | 0 | 0 | 0 | 0
2021-12-26 17:00 | 3.3281 | 1.3053 | 1.0311 | 1.732 | 0 | 0 | 0 | 0
2021-12-26 17:15 | 3.2567 | 1.2936 | 0.29708 | 1.3785 | 0 | 0 | 0 | 0
2021-12-26 17:30 | 3.2975 | 1.3184 | 0.30627 | 1.3471 | 0 | 0 | 0 | 0
2021-12-26 17:45 | 3.3281 | 1.0232 | 0.46553 | 0.77078 | 0 | 0 | 0 | 0
2021-12-26 18:00 | 3.4404 | 1.0476 | 0.92289 | 0.77515 | 0 | 0 | 0 | 0
2021-12-26 18:15 | 3.3894 | 1.1562 | 0.89839 | 0.67948 | 0 | 0 | 0 | 0
2021-12-26 18:30 | 3.3485 | 1.03 | 1.1842 | 0.87593 | 0 | 0 | 0 | 0
2021-12-26 18:45 | 3.2975 | 1.247 | 1.1026 | 1.0909 | 0 | 0 | 0 | 0
2021-12-26 19:00 | 3.3077 | 1.3065 | 0.99639 | 1.291 | 0 | 0 | 0 | 0
2021-12-26 19:15 | 3.3179 | 1.3065 | 0.99231 | 1.2764 | 0 | 0 | 0 | 0
2021-12-26 19:30 | 3.4608 | 1.4019 | 0.92697 | 1.4855 | 0 | 0 | 0 | 0
2021-12-26 19:45 | 3.4915 | 1.5096 | 0.95147 | 1.8649 | 0 | 0 | 0 | 0
2021-12-26 20:00 | 0.2736 | 1.0914 | 2.1235 | 1.1498 | 0 | 0 | 0 | 0
2021-12-26 20:15 | 0.2981 | 1.0747 | 1.7866 | 1.0049 | 0 | 0 | 0 | 0
2021-12-26 20:30 | 0.21133 | 1.0747 | 1.3782 | 0.96956 | 0 | 0 | 0 | 0
2021-12-26 20:45 | 0.25522 | 0.9643 | 0.8698 | 0.83072 | 0 | 0 | 0 | 0
2021-12-26 21:00 | 0.33792 | 1.0974 | 0.63704 | 0.76801 | 0 | 0 | 0 | 0
2021-12-26 21:15 | 0.33485 | 1.0018 | 0.68604 | 0.61823 | 0 | 0 | 0 | 0
2021-12-26 21:30 | 0.31444 | 1.0215 | 0.57987 | 0.64637 | 0 | 0 | 0 | 0
2021-12-26 21:45 | 0.26339 | 0.76984 | 0.52678 | 0.63004 | 0 | 0 | 0 | 0
2021-12-26 22:00 | 0.26543 | 0.75251 | 0.61662 | 0.58789 | 0 | 0 | 0 | 0
2021-12-26 22:15 | 0.32873 | 0.7282 | 0.66562 | 0.57651 | 0 | 0 | 0 | 0
2021-12-26 22:30 | 0.35527 | 0.7282 | 0.62479 | 0.5717 | 0 | 0 | 0 | 0
2021-12-26 22:45 | 0.27258 | 0.68318 | 0.59212 | 0.56105 | 0 | 0 | 0 | 0
2021-12-26 23:00 | 3.2056 | 1.0971 | 0.55945 | 1.38 | 0 | 0 | 0 | 0
2021-12-26 23:15 | 3.4302 | 1.2277 | 0.51453 | 1.4252 | 0 | 0 | 0 | 0
2021-12-26 23:30 | 3.4098 | 1.1661 | 0.5227 | 1.4272 | 0 | 0 | 0 | 0
2021-12-26 23:45 | 3.3792 | 1.186 | 0.39611 | 1.4307 | 0 | 0 | 0 | 0
2021-12-27 | 3.3792 | 1.1736 | 0.35323 | 1.4115 | 0 | 0 | 0 | 0
2021-12-27 00:15 | 3.4813 | 1.1736 | 0.34098 | 1.375 | 0 | 0 | 0 | 0
2021-12-27 00:30 | 3.5017 | 1.1343 | 0.37263 | 1.3711 | 0 | 0 | 0 | 0
2021-12-27 00:45 | 3.4506 | 1.1343 | 0.44103 | 1.3558 | 0 | 0 | 0 | 0
2021-12-27 01:00 | 3.4302 | 1.2479 | 0.31648 | 1.3143 | 0 | 0 | 0 | 0
2021-12-27 01:15 | 3.369 | 1.0837 | 0.24502 | 1.2885 | 0 | 0 | 0 | 0
2021-12-27 01:30 | 3.4915 | 1.0837 | 0.25727 | 1.2983 | 0 | 0 | 0 | 0
2021-12-27 01:45 | 3.4813 | 0.91721 | 0.30014 | 1.3132 | 0 | 0 | 0 | 0
2021-12-27 02:00 | 3.4302 | 0.98198 | 0.34404 | 1.282 | 0 | 0 | 0 | 0
2021-12-27 02:15 | 3.3996 | 0.98198 | 0.26543 | 1.2736 | 0 | 0 | 0 | 0
2021-12-27 02:30 | 3.3996 | 0.9965 | 0.28789 | 1.2729 | 0 | 0 | 0 | 0
2021-12-27 02:45 | 3.4608 | 1.0169 | 0.26237 | 1.2906 | 0 | 0 | 0 | 0
2021-12-27 03:00 | 3.5731 | 0.91721 | 0.37671 | 1.3375 | 0 | 0 | 0 | 0
2021-12-27 03:15 | 3.5017 | 0.96406 | 0.28585 | 1.2914 | 0 | 0 | 0 | 0
2021-12-27 03:30 | 3.4302 | 1.0169 | 0.25931 | 1.3114 | 0 | 0 | 0 | 0
2021-12-27 03:45 | 3.42 | 1.0169 | 0.29504 | 1.3038 | 0 | 0 | 0 | 0
2021-12-27 04:00 | 3.471 | 1.032 | 0.36548 | 1.2423 | 0 | 0 | 0 | 0
2021-12-27 04:15 | 3.5017 | 0.94469 | 0.342 | 1.063 | 0 | 0 | 0 | 0
2021-12-27 04:30 | 3.369 | 0.88888 | 0.26339 | 0.94345 | 0 | 0 | 0 | 0
2021-12-27 04:45 | 2.2256 | 0.87217 | 0.28381 | 0.95118 | 0 | 0 | 0 | 0
2021-12-27 05:00 | 1.6539 | 0.83276 | 0.33281 | 0.88672 | 0 | 0 | 0 | 0
2021-12-27 05:15 | 1.3374 | 0.9185 | 0.25114 | 0.84166 | 0 | 0 | 0 | 0
2021-12-27 05:30 | 0.89839 | 0.85798 | 0.26135 | 0.89314 | 0 | 0 | 0 | 0
2021-12-27 05:45 | 0.56762 | 0.95891 | 0.24502 | 0.94608 | 0 | 0 | 0 | 0
2021-12-27 06:00 | 0.55128 | 1.1382 | 0.41653 | 1.013 | 0 | 0 | 0 | 0
2021-12-27 06:15 | 0.28381 | 0.93129 | 0.33077 | 0.87491 | 0 | 0 | 0 | 0
2021-12-27 06:30 | 0.3175 | 0.87078 | 0.25625 | 0.89401 | 0 | 0 | 0 | 0
2021-12-27 06:45 | 0.26543 | 0.87078 | 0.26237 | 0.88482 | 0 | 0 | 0 | 0
2021-12-27 07:00 | 0.2787 | 0.6475 | 0.2981 | 0.51045 | 0 | 0 | 0 | 0
2021-12-27 07:15 | 0.31035 | 0.74286 | 0.37569 | 0.46276 | 0 | 0 | 0 | 0
2021-12-27 07:30 | 0.40836 | 0.91934 | 0.35323 | 0.46597 | 0 | 0 | 0 | 0
2021-12-27 07:45 | 0.26645 | 0.96616 | 0.29912 | 0.43417 | 0.000139 | 0.002256 | 3.3e-05 | 0.001585
2021-12-27 08:00 | 1.2455 | 1.3756 | 0.27054 | 0.97218 | 0.003751 | 0.019448 | 0.000751 | 0.020563
2021-12-27 08:15 | 0.65337 | 1.4502 | 0.26339 | 0.97306 | 0.007363 | 0.058125 | 0.001468 | 0.039541
2021-12-27 08:30 | 0.40836 | 1.5718 | 0.33383 | 0.99698 | 0.010975 | 0.096496 | 0.002186 | 0.058519
2021-12-27 08:45 | 0.33587 | 1.4678 | 0.37875 | 0.99873 | 0.01561 | 0.12013 | 0.00294 | 0.077993
2021-12-27 09:00 | 0.34302 | 1.6221 | 0.39917 | 1.0737 | 0.046133 | 0.16364 | 0.00445 | 0.10445
2021-12-27 09:15 | 0.22868 | 1.5404 | 0.32158 | 1.056 | 0.076655 | 0.20895 | 0.00596 | 0.13091
2021-12-27 09:30 | 0.27054 | 1.5188 | 0.33792 | 1.0817 | 0.10718 | 0.22866 | 0.007469 | 0.15737
2021-12-27 09:45 | 0.26543 | 1.4166 | 0.33894 | 1.0116 | 0.13622 | 0.25049 | 0.009093 | 0.18252
2021-12-27 10:00 | 0.20724 | 1.5404 | 0.49411 | 1.1749 | 0.12737 | 0.25946 | 0.013078 | 0.19175
2021-12-27 10:15 | 0.36344 | 1.5402 | 1.9091 | 1.2292 | 0.11851 | 0.26843 | 0.017062 | 0.20098
2021-12-27 10:30 | 0.25625 | 1.2471 | 1.0821 | 1.279 | 0.10966 | 0.28456 | 0.021047 | 0.21021
2021-12-27 10:45 | 0.27973 | 1.2253 | 0.56762 | 0.8803 | 0.10167 | 0.31334 | 0.024731 | 0.2181
2021-12-27 11:00 | 0.26339 | 1.5037 | 1.2761 | 0.99989 | 0.11593 | 0.28509 | 0.022116 | 0.21066
2021-12-27 11:15 | 0.25829 | 1.3765 | 1.1434 | 1.2892 | 0.1302 | 0.27032 | 0.019501 | 0.20323
2021-12-27 11:30 | 0.30218 | 1.2925 | 0.89431 | 0.93427 | 0.14446 | 0.27433 | 0.016887 | 0.19579
2021-12-27 11:45 | 0.27666 | 1.3437 | 0.52678 | 1.1058 | 0.15749 | 0.2739 | 0.014612 | 0.18849
2021-12-27 12:00 | 0.27768 | 1.4556 | 0.61662 | 1.2535 | 0.13869 | 0.27351 | 0.019516 | 0.18139
2021-12-27 12:15 | 0.31648 | 1.307 | 0.60437 | 1.0028 | 0.11989 | 0.26331 | 0.024421 | 0.17428
2021-12-27 12:30 | 0.2981 | 1.4887 | 3.5017 | 1.3571 | 0.10109 | 0.25519 | 0.029325 | 0.16717
2021-12-27 12:45 | 0.58804 | 1.6883 | 3.6344 | 1.5579 | 0.082468 | 0.25483 | 0.034015 | 0.15949
2021-12-27 13:00 | 0.42878 | 1.5337 | 3.5119 | 1.8685 | 0.068502 | 0.23359 | 0.034128 | 0.14815
2021-12-27 13:15 | 0.2685 | 1.5737 | 3.5221 | 1.9782 | 0.054536 | 0.23333 | 0.03424 | 0.13681
2021-12-27 13:30 | 0.2787 | 1.6438 | 3.6548 | 1.968 | 0.040569 | 0.24858 | 0.034353 | 0.12547
2021-12-27 13:45 | 0.37977 | 1.5475 | 3.6854 | 2.0031 | 0.027276 | 0.26828 | 0.034424 | 0.11482
2021-12-27 14:00 | 0.33077 | 1.4291 | 3.6344 | 2.0838 | 0.031848 | 0.2655 | 0.033609 | 0.11152
2021-12-27 14:15 | 0.34608 | 1.415 | 3.5527 | 1.7055 | 0.03642 | 0.25187 | 0.032794 | 0.10821
2021-12-27 14:30 | 0.29504 | 1.4727 | 3.5119 | 1.5856 | 0.040992 | 0.22959 | 0.031979 | 0.10491
2021-12-27 14:45 | 0.25012 | 1.2629 | 3.4813 | 1.4046 | 0.045012 | 0.21452 | 0.030855 | 0.10051
2021-12-27 15:00 | 0.2787 | 1.3587 | 3.4404 | 1.5526 | 0.034233 | 0.18212 | 0.023056 | 0.082321
2021-12-27 15:15 | 0.39815 | 1.4246 | 3.4506 | 1.9733 | 0.023454 | 0.1542 | 0.015257 | 0.064134
2021-12-27 15:30 | 0.26748 | 1.3414 | 3.5629 | 1.4039 | 0.012675 | 0.11492 | 0.007457 | 0.045947
2021-12-27 15:45 | 0.26543 | 1.4058 | 3.42 | 1.3762 | 0.00226 | 0.055561 | 0 | 0.02855
2021-12-27 16:00 | 0.41244 | 1.4347 | 3.2771 | 1.9342 | 0.00169 | 0.030908 | 0 | 0.021262
2021-12-27 16:15 | 0.21133 | 1.4399 | 3.1852 | 1.8813 | 0.00112 | 0.013397 | 0 | 0.013974
2021-12-27 16:30 | 0.20418 | 1.346 | 3.2158 | 1.828 | 0.00055 | 0.003094 | 0 | 0.006686
2021-12-27 16:45 | 0.30831 | 1.4598 | 3.2771 | 2.6886 | 0 | 0 | 0 | 0
2021-12-27 17:00 | 0.29402 | 1.4129 | 3.3281 | 2.1398 | 0 | 0 | 0 | 0
2021-12-27 17:15 | 0.2736 | 1.0349 | 3.2567 | 1.7915 | 0 | 0 | 0 | 0
2021-12-27 17:30 | 0.33383 | 1.2394 | 3.2975 | 1.7587 | 0 | 0 | 0 | 0
2021-12-27 17:45 | 0.30014 | 1.3059 | 3.3281 | 1.1892 | 0 | 0 | 0 | 0
2021-12-27 18:00 | 0.26033 | 1.3462 | 3.4404 | 1.1838 | 0 | 0 | 0 | 0
2021-12-27 18:15 | 0.24604 | 1.2732 | 3.3894 | 1.033 | 0 | 0 | 0 | 0
2021-12-27 18:30 | 0.32567 | 1.3429 | 3.3485 | 1.048 | 0 | 0 | 0 | 0
2021-12-27 18:45 | 0.3859 | 1.384 | 3.2975 | 1.2411 | 0 | 0 | 0 | 0
2021-12-27 19:00 | 0.28993 | 1.2298 | 3.3077 | 1.4427 | 0 | 0 | 0 | 0
2021-12-27 19:15 | 0.25318 | 1.2298 | 3.3179 | 1.4937 | 0 | 0 | 0 | 0
2021-12-27 19:30 | 0.25522 | 1.5349 | 3.4608 | 1.8703 | 0 | 0 | 0 | 0
2021-12-27 19:45 | 0.27564 | 1.8734 | 3.4915 | 2.2557 | 0 | 0 | 0 | 0
2021-12-27 20:00 | 0.40836 | 1.1279 | 0.2736 | 1.0827 | 0 | 0 | 0 | 0
2021-12-27 20:15 | 0.34404 | 0.83517 | 0.2981 | 0.87535 | 0 | 0 | 0 | 0
2021-12-27 20:30 | 0.28075 | 0.83517 | 0.21133 | 0.82766 | 0 | 0 | 0 | 0
2021-12-27 20:45 | 0.25931 | 0.83517 | 0.25522 | 0.74 | 0 | 0 | 0 | 0
2021-12-27 21:00 | 0.25829 | 0.81953 | 0.33792 | 0.66169 | 0 | 0 | 0 | 0
2021-12-27 21:15 | 0.27973 | 0.8637 | 0.33485 | 0.56747 | 0 | 0 | 0 | 0
2021-12-27 21:30 | 0.33485 | 0.88267 | 0.31444 | 0.58162 | 0 | 0 | 0 | 0
2021-12-27 21:45 | 0.26645 | 0.77811 | 0.26339 | 0.57783 | 0 | 0 | 0 | 0
2021-12-27 22:00 | 0.28687 | 0.77811 | 0.26543 | 0.56456 | 0 | 0 | 0 | 0
2021-12-27 22:15 | 0.29402 | 0.69295 | 0.32873 | 0.56222 | 0 | 0 | 0 | 0
2021-12-27 22:30 | 0.29504 | 0.69295 | 0.35527 | 0.56003 | 0 | 0 | 0 | 0
2021-12-27 22:45 | 0.30423 | 0.62769 | 0.27258 | 0.53349 | 0 | 0 | 0 | 0
2021-12-27 23:00 | 1.2659 | 1.3341 | 3.2056 | 1.7591 | 0 | 0 | 0 | 0
2021-12-27 23:15 | 0.67788 | 1.3502 | 3.4302 | 1.8259 | 0 | 0 | 0 | 0
2021-12-27 23:30 | 0.4982 | 1.3502 | 3.4098 | 1.8344 | 0 | 0 | 0 | 0
2021-12-27 23:45 | 0.32158 | 1.3502 | 3.3792 | 1.83 | 0 | 0 | 0 | 0
2021-12-28 | 0.27156 | 1.2372 | 3.3792 | 1.8079 | 0 | 0 | 0 | 0
2021-12-28 00:15 | 0.28993 | 1.2372 | 3.4813 | 1.8023 | 0 | 0 | 0 | 0
2021-12-28 00:30 | 0.27156 | 1.3074 | 3.5017 | 1.806 | 0 | 0 | 0 | 0
2021-12-28 00:45 | 0.42469 | 1.3074 | 3.4506 | 1.7857 | 0 | 0 | 0 | 0
2021-12-28 01:00 | 0.22256 | 1.143 | 3.4302 | 1.758 | 0 | 0 | 0 | 0
2021-12-28 01:15 | 0.24297 | 1.143 | 3.369 | 1.7239 | 0 | 0 | 0 | 0
2021-12-28 01:30 | 0.26441 | 1.143 | 3.4915 | 1.7416 | 0 | 0 | 0 | 0
2021-12-28 01:45 | 0.33996 | 1.143 | 3.4813 | 1.7475 | 0 | 0 | 0 | 0
2021-12-28 02:00 | 0.24604 | 1.1757 | 3.4302 | 1.7244 | 0 | 0 | 0 | 0
2021-12-28 02:15 | 0.29402 | 1.143 | 3.3996 | 1.7083 | 0 | 0 | 0 | 0
2021-12-28 02:30 | 0.21949 | 1.1791 | 3.3996 | 1.7119 | 0 | 0 | 0 | 0
2021-12-28 02:45 | 0.24604 | 1.1791 | 3.4608 | 1.7383 | 0 | 0 | 0 | 0
2021-12-28 03:00 | 0.3471 | 1.3075 | 3.5731 | 1.7873 | 0 | 0 | 0 | 0
2021-12-28 03:15 | 0.30831 | 1.2021 | 3.5017 | 1.744 | 0 | 0 | 0 | 0
2021-12-28 03:30 | 0.28075 | 1.2021 | 3.4302 | 1.7504 | 0 | 0 | 0 | 0
2021-12-28 03:45 | 0.25931 | 1.2021 | 3.42 | 1.7422 | 0 | 0 | 0 | 0
2021-12-28 04:00 | 0.27258 | 1.2617 | 3.471 | 1.6763 | 0 | 0 | 0 | 0
2021-12-28 04:15 | 0.29198 | 1.2142 | 3.5017 | 1.5121 | 0 | 0 | 0 | 0
2021-12-28 04:30 | 0.31341 | 1.2009 | 3.369 | 1.3719 | 0 | 0 | 0 | 0
2021-12-28 04:45 | 0.25318 | 1.1581 | 2.2256 | 1.223 | 0 | 0 | 0 | 0
2021-12-28 05:00 | 0.27156 | 1.1803 | 1.6539 | 1.0711 | 0 | 0 | 0 | 0
2021-12-28 05:15 | 0.38079 | 1.0469 | 1.3374 | 0.98706 | 0 | 0 | 0 | 0
2021-12-28 05:30 | 0.35527 | 1.0499 | 0.89839 | 0.96081 | 0 | 0 | 0 | 0
2021-12-28 05:45 | 0.24093 | 1.0628 | 0.56762 | 0.92333 | 0 | 0 | 0 | 0
2021-12-28 06:00 | 0.28483 | 1.2232 | 0.55128 | 1.0189 | 0 | 0 | 0 | 0
2021-12-28 06:15 | 0.23685 | 1.0698 | 0.28381 | 0.86091 | 0 | 0 | 0 | 0
2021-12-28 06:30 | 0.27156 | 1.0135 | 0.3175 | 0.87812 | 0 | 0 | 0 | 0
2021-12-28 06:45 | 0.36548 | 1.0362 | 0.26543 | 0.86032 | 0 | 0 | 0 | 0
2021-12-28 07:00 | 0.25931 | 0.7143 | 0.2787 | 0.48726 | 0 | 0 | 0 | 0
2021-12-28 07:15 | 0.27666 | 0.76663 | 0.31035 | 0.44701 | 0 | 0 | 0 | 0
2021-12-28 07:30 | 0.23889 | 0.7034 | 0.40836 | 0.46742 | 0 | 0 | 0 | 0
2021-12-28 07:45 | 0.35221 | 0.75023 | 0.26645 | 0.41915 | 0.000279 | 0.002743 | 0.000139 | 0.00136
2021-12-28 08:00 | 0.26033 | 1.1488 | 1.2455 | 1.0989 | 0.009543 | 0.025168 | 0.003751 | 0.018302
2021-12-28 08:15 | 0.24502 | 1.151 | 0.65337 | 0.99814 | 0.018808 | 0.056095 | 0.007363 | 0.035244
2021-12-28 08:30 | 0.25522 | 1.2199 | 0.40836 | 0.99639 | 0.028072 | 0.08152 | 0.010975 | 0.052186
2021-12-28 08:45 | 0.1858 | 1.2264 | 0.33587 | 1.0012 | 0.037675 | 0.10244 | 0.01561 | 0.069328
2021-12-28 09:00 | 0.38386 | 1.1814 | 0.34302 | 1.0667 | 0.058316 | 0.12383 | 0.046133 | 0.092962
2021-12-28 09:15 | 0.45736 | 1.1037 | 0.22868 | 1.0275 | 0.078957 | 0.14462 | 0.076655 | 0.1166
2021-12-28 09:30 | 0.37467 | 1.1718 | 0.27054 | 1.0509 | 0.099597 | 0.15816 | 0.10718 | 0.14023
2021-12-28 09:45 | 0.34098 | 1.14 | 0.26543 | 0.97131 | 0.11945 | 0.17462 | 0.13622 | 0.16286
2021-12-28 10:00 | 0.391 | 1.1578 | 0.20724 | 1.1415 | 0.11331 | 0.18087 | 0.12737 | 0.16899
2021-12-28 10:15 | 0.35731 | 1.2035 | 0.36344 | 1.2146 | 0.10717 | 0.18618 | 0.11851 | 0.17512
2021-12-28 10:30 | 0.39304 | 1.2156 | 0.25625 | 1.1803 | 0.10103 | 0.1924 | 0.10966 | 0.18125
2021-12-28 10:45 | 0.2736 | 1.0845 | 0.27973 | 0.78026 | 0.094776 | 0.19808 | 0.10167 | 0.18671
2021-12-28 11:00 | 0.22256 | 1.1562 | 0.26339 | 0.97335 | 0.084661 | 0.19806 | 0.11593 | 0.18522
2021-12-28 11:15 | 0.23481 | 1.1849 | 0.25829 | 1.0607 | 0.074547 | 0.18905 | 0.1302 | 0.18372
2021-12-28 11:30 | 0.36344 | 1.1503 | 0.30218 | 0.74846 | 0.064433 | 0.18903 | 0.14446 | 0.18222
2021-12-28 11:45 | 0.28789 | 1.1319 | 0.27666 | 0.91924 | 0.05442 | 0.18524 | 0.15749 | 0.18002
2021-12-28 12:00 | 0.24706 | 1.1295 | 0.27768 | 0.89795 | 0.047821 | 0.17988 | 0.13869 | 0.16709
2021-12-28 12:15 | 0.28381 | 1.1295 | 0.31648 | 0.9051 | 0.041221 | 0.17862 | 0.11989 | 0.15416
2021-12-28 12:30 | 0.32873 | 1.3064 | 0.2981 | 1.3396 | 0.034622 | 0.18242 | 0.10109 | 0.14123
2021-12-28 12:45 | 0.53087 | 1.3176 | 0.58804 | 1.5859 | 0.028924 | 0.18219 | 0.082468 | 0.12893
2021-12-28 13:00 | 0.60437 | 1.3915 | 0.42878 | 1.8633 | 0.054044 | 0.18107 | 0.068502 | 0.12502
2021-12-28 13:15 | 0.28687 | 1.5759 | 0.2685 | 1.9337 | 0.079165 | 0.17656 | 0.054536 | 0.12112
2021-12-28 13:30 | 0.26339 | 1.5387 | 0.2787 | 1.8941 | 0.10429 | 0.19084 | 0.040569 | 0.11722
2021-12-28 13:45 | 0.29096 | 1.3157 | 0.37977 | 1.9961 | 0.12781 | 0.18986 | 0.027276 | 0.11329
2021-12-28 14:00 | 0.33383 | 1.3614 | 0.33077 | 2.0039 | 0.096241 | 0.18059 | 0.031848 | 0.11141
2021-12-28 14:15 | 0.39611 | 1.3297 | 0.34608 | 1.558 | 0.064669 | 0.17131 | 0.03642 | 0.10952
2021-12-28 14:30 | 0.3175 | 1.3932 | 0.29504 | 1.4586 | 0.033096 | 0.16202 | 0.040992 | 0.10763
2021-12-28 14:45 | 0.21337 | 1.3138 | 0.25012 | 1.2799 | 0.004232 | 0.16259 | 0.045012 | 0.10455
2021-12-28 15:00 | 0.22256 | 1.2421 | 0.2787 | 1.4116 | 0.070259 | 0.134 | 0.034233 | 0.085438
2021-12-28 15:15 | 0.39611 | 1.2536 | 0.39815 | 1.4319 | 0.13628 | 0.11331 | 0.023454 | 0.066321
2021-12-28 15:30 | 0.32975 | 1.1719 | 0.26748 | 1.1373 | 0.20231 | 0.089887 | 0.012675 | 0.047204
2021-12-28 15:45 | 0.27666 | 1.2708 | 0.26543 | 1.2435 | 0.2647 | 0.038894 | 0.00226 | 0.028872
2021-12-28 16:00 | 0.22051 | 1.5194 | 0.41244 | 1.4476 | 0.19808 | 0.024952 | 0.00169 | 0.021503
2021-12-28 16:15 | 0.26135 | 1.4269 | 0.21133 | 1.3161 | 0.13145 | 0.020537 | 0.00112 | 0.014134
2021-12-28 16:30 | 0.37263 | 1.6428 | 0.20418 | 1.5801 | 0.064824 | 0.010179 | 0.00055 | 0.006764
2021-12-28 16:45 | 0.30627 | 2.2381 | 0.30831 | 2.4497 | 0 | 0 | 0 | 0
2021-12-28 17:00 | 0.29096 | 2.0475 | 0.29402 | 1.896 | 0 | 0 | 0 | 0
2021-12-28 17:15 | 0.42061 | 2.0788 | 0.2736 | 1.7711 | 0 | 0 | 0 | 0
2021-12-28 17:30 | 0.58395 | 2.0788 | 0.33383 | 1.7768 | 0 | 0 | 0 | 0
2021-12-28 17:45 | 0.57987 | 1.2624 | 0.30014 | 1.202 | 0 | 0 | 0 | 0
2021-12-28 18:00 | 0.71054 | 1.2672 | 0.26033 | 1.1803 | 0 | 0 | 0 | 0
2021-12-28 18:15 | 0.77997 | 1.2116 | 0.24604 | 1.0151 | 0 | 0 | 0 | 0
2021-12-28 18:30 | 0.68604 | 1.2252 | 0.32567 | 1.0435 | 0 | 0 | 0 | 0
2021-12-28 18:45 | 0.58804 | 1.3364 | 0.3859 | 1.2563 | 0 | 0 | 0 | 0
2021-12-28 19:00 | 0.7473 | 1.2266 | 0.28993 | 1.4456 | 0 | 0 | 0 | 0
2021-12-28 19:15 | 0.86572 | 1.2359 | 0.25318 | 1.4835 | 0 | 0 | 0 | 0
2021-12-28 19:30 | 0.88614 | 1.4225 | 0.25522 | 1.548 | 0 | 0 | 0 | 0
2021-12-28 19:45 | 0.96781 | 1.5202 | 0.27564 | 1.6179 | 0 | 0 | 0 | 0
2021-12-28 20:00 | 1.3884 | 0.92666 | 0.40836 | 0.98356 | 0 | 0 | 0 | 0
2021-12-28 20:15 | 1.7662 | 0.84401 | 0.34404 | 0.85332 | 0 | 0 | 0 | 0
2021-12-28 20:30 | 1.5926 | 0.85359 | 0.28075 | 0.79251 | 0 | 0 | 0 | 0
2021-12-28 20:45 | 0.8453 | 0.85359 | 0.25931 | 0.70179 | 0 | 0 | 0 | 0
2021-12-28 21:00 | 0.73913 | 0.86172 | 0.25829 | 0.62275 | 0 | 0 | 0 | 0
2021-12-28 21:15 | 0.59212 | 0.75636 | 0.27973 | 0.53101 | 0 | 0 | 0 | 0
2021-12-28 21:30 | 0.48186 | 0.68172 | 0.33485 | 0.55245 | 0 | 0 | 0 | 0
2021-12-28 21:45 | 0.50228 | 0.72627 | 0.26645 | 0.5383 | 0 | 0 | 0 | 0
2021-12-28 22:00 | 0.45736 | 0.68912 | 0.28687 | 0.52737 | 0 | 0 | 0 | 0
2021-12-28 22:15 | 0.43286 | 0.68912 | 0.29402 | 0.52547 | 0 | 0 | 0 | 0
2021-12-28 22:30 | 0.59212 | 0.72675 | 0.29504 | 0.52285 | 0 | 0 | 0 | 0
2021-12-28 22:45 | 0.5717 | 0.71087 | 0.30423 | 0.49703 | 0 | 0 | 0 | 0
2021-12-28 23:00 | 0.58395 | 2.2317 | 1.2659 | 1.8601 | 0 | 0 | 0 | 0
2021-12-28 23:15 | 0.49003 | 2.3131 | 0.67788 | 1.8423 | 0 | 0 | 0 | 0
2021-12-28 23:30 | 0.5227 | 2.3131 | 0.4982 | 1.8245 | 0 | 0 | 0 | 0
2021-12-28 23:45 | 0.53087 | 2.2094 | 0.32158 | 1.7943 | 0 | 0 | 0 | 0
2021-12-29 | 0.5472 | 1.467 | 0.27156 | 1.7644 | 0 | 0 | 0 | 0
2021-12-29 00:15 | 0.44511 | 1.2787 | 0.28993 | 1.7609 | 0 | 0 | 0 | 0
2021-12-29 00:30 | 0.36752 | 1.273 | 0.27156 | 1.7613 | 0 | 0 | 0 | 0
2021-12-29 00:45 | 0.46961 | 1.467 | 0.42469 | 1.7624 | 0 | 0 | 0 | 0
2021-12-29 01:00 | 0.46553 | 1.2343 | 0.22256 | 1.7052 | 0 | 0 | 0 | 0
2021-12-29 01:15 | 0.39407 | 1.2174 | 0.24297 | 1.6734 | 0 | 0 | 0 | 0
2021-12-29 01:30 | 0.29708 | 1.3143 | 0.26441 | 1.6943 | 0 | 0 | 0 | 0
2021-12-29 01:45 | 0.28585 | 1.4442 | 0.33996 | 1.7103 | 0 | 0 | 0 | 0
2021-12-29 02:00 | 0.31954 | 1.4283 | 0.24604 | 1.6732 | 0 | 0 | 0 | 0
2021-12-29 02:15 | 0.32056 | 1.464 | 0.29402 | 1.6633 | 0 | 0 | 0 | 0
2021-12-29 02:30 | 0.32465 | 1.4196 | 0.21949 | 1.6557 | 0 | 0 | 0 | 0
2021-12-29 02:45 | 0.35425 | 1.464 | 0.24604 | 1.6854 | 0 | 0 | 0 | 0
2021-12-29 03:00 | 0.42878 | 1.7136 | 0.3471 | 1.7482 | 0 | 0 | 0 | 0
2021-12-29 03:15 | 0.46144 | 1.5609 | 0.30831 | 1.6988 | 0 | 0 | 0 | 0
2021-12-29 03:30 | 0.70238 | 1.784 | 0.28075 | 1.7007 | 0 | 0 | 0 | 0
2021-12-29 03:45 | 0.47778 | 1.9363 | 0.25931 | 1.6894 | 0 | 0 | 0 | 0
2021-12-29 04:00 | 0.29402 | 1.8931 | 0.27258 | 1.6248 | 0 | 0 | 0 | 0
2021-12-29 04:15 | 0.32362 | 1.188 | 0.29198 | 1.4628 | 0 | 0 | 0 | 0
2021-12-29 04:30 | 0.34915 | 1.1155 | 0.31341 | 1.3251 | 0 | 0 | 0 | 0
2021-12-29 04:45 | 0.2981 | 0.85151 | 0.25318 | 1.167 | 0 | 0 | 0 | 0
2021-12-29 05:00 | 0.36548 | 0.65672 | 0.27156 | 1.0171 | 0 | 0 | 0 | 0
2021-12-29 05:15 | 0.44511 | 0.53218 | 0.38079 | 0.94812 | 0 | 0 | 0 | 0
2021-12-29 05:30 | 0.46553 | 0.53218 | 0.35527 | 0.91764 | 0 | 0 | 0 | 0
2021-12-29 05:45 | 0.41653 | 0.70183 | 0.24093 | 0.86324 | 0 | 0 | 0 | 0
2021-12-29 06:00 | 0.31239 | 0.71751 | 0.28483 | 0.96445 | 0 | 0 | 0 | 0
2021-12-29 06:15 | 0.30729 | 0.59346 | 0.23685 | 0.79965 | 0 | 0 | 0 | 0
2021-12-29 06:30 | 0.42469 | 0.63593 | 0.27156 | 0.82124 | 0 | 0 | 0 | 0
2021-12-29 06:45 | 0.42878 | 0.63593 | 0.36548 | 0.81628 | 0 | 0 | 0 | 0
2021-12-29 07:00 | 0.33996 | 0.66627 | 0.25931 | 0.42746 | 0 | 0 | 0 | 0
2021-12-29 07:15 | 0.32567 | 0.52598 | 0.27666 | 0.38911 | 0 | 0 | 0 | 0
2021-12-29 07:30 | 0.40427 | 0.52049 | 0.23889 | 0.40355 | 0 | 0 | 0 | 0
2021-12-29 07:45 | 0.43694 | 0.55534 | 0.35221 | 0.37088 | 2e-05 | 0.003848 | 0.000279 | 0.000515
2021-12-29 08:00 | 0.33894 | 1.1763 | 0.26033 | 1.0369 | 0.000932 | 0.05878 | 0.009543 | 0.008691
2021-12-29 08:15 | 0.33077 | 1.4041 | 0.24502 | 0.93339 | 0.001845 | 0.11282 | 0.018808 | 0.016867
2021-12-29 08:30 | 0.42878 | 1.3722 | 0.25522 | 0.9331 | 0.002757 | 0.16183 | 0.028072 | 0.025043
2021-12-29 08:45 | 0.45328 | 1.2628 | 0.1858 | 0.92741 | 0.003723 | 0.21042 | 0.037675 | 0.033643
2021-12-29 09:00 | 0.41244 | 1.1584 | 0.38386 | 1.0206 | 0.007113 | 0.25293 | 0.058316 | 0.052136
2021-12-29 09:15 | 0.68604 | 1.3287 | 0.45736 | 0.99129 | 0.010503 | 0.27687 | 0.078957 | 0.07063
2021-12-29 09:30 | 0.85755 | 1.2662 | 0.37467 | 1.0024 | 0.013892 | 0.30675 | 0.099597 | 0.089124
2021-12-29 09:45 | 0.75138 | 1.1754 | 0.34098 | 0.93368 | 0.017652 | 0.34249 | 0.11945 | 0.10697
2021-12-29 10:00 | 0.5962 | 1.4778 | 0.391 | 1.104 | 0.038452 | 0.3624 | 0.11331 | 0.10962
2021-12-29 10:15 | 0.58395 | 1.658 | 0.35731 | 1.1775 | 0.059253 | 0.37494 | 0.10717 | 0.11226
2021-12-29 10:30 | 2.2562 | 1.391 | 0.39304 | 1.1624 | 0.080054 | 0.38747 | 0.10103 | 0.1149
2021-12-29 10:45 | 2.6135 | 1.2009 | 0.2736 | 0.73067 | 0.10001 | 0.40578 | 0.094776 | 0.11708
2021-12-29 11:00 | 2.0724 | 1.3506 | 0.22256 | 0.91647 | 0.080412 | 0.39645 | 0.084661 | 0.11415
2021-12-29 11:15 | 1.1536 | 1.3853 | 0.23481 | 1.0278 | 0.060814 | 0.39881 | 0.074547 | 0.11122
2021-12-29 11:30 | 3.3077 | 1.3316 | 0.36344 | 0.72805 | 0.041216 | 0.39348 | 0.064433 | 0.10829
2021-12-29 11:45 | 1.1434 | 1.1886 | 0.28789 | 0.89445 | 0.022116 | 0.37624 | 0.05442 | 0.10468
2021-12-29 12:00 | 1.4293 | 1.2003 | 0.24706 | 0.88293 | 0.026791 | 0.37571 | 0.047821 | 0.090925
2021-12-29 12:15 | 3.0831 | 1.2196 | 0.28381 | 0.89606 | 0.031465 | 0.37517 | 0.041221 | 0.077169
2021-12-29 12:30 | 1.3476 | 0.77856 | 0.32873 | 1.3291 | 0.03614 | 0.3904 | 0.034622 | 0.063413
2021-12-29 12:45 | 0.69421 | 0.959 | 0.53087 | 1.6136 | 0.040744 | 0.38579 | 0.028924 | 0.050417
2021-12-29 13:00 | 0.5962 | 1.3628 | 0.60437 | 1.9082 | 0.041921 | 0.38538 | 0.054044 | 0.05019
2021-12-29 13:15 | 0.53087 | 0.86367 | 0.28687 | 1.7851 | 0.043099 | 0.37514 | 0.079165 | 0.049964
2021-12-29 13:30 | 0.58804 | 0.87332 | 0.26339 | 1.8278 | 0.044276 | 0.40338 | 0.10429 | 0.049737
2021-12-29 13:45 | 0.91472 | 1.413 | 0.29096 | 2.0005 | 0.045285 | 0.35773 | 0.12781 | 0.049597
2021-12-29 14:00 | 1.5824 | 1.3737 | 0.33383 | 2.0069 | 0.037983 | 0.38168 | 0.096241 | 0.047202
2021-12-29 14:15 | 0.66971 | 0.78816 | 0.39611 | 1.5621 | 0.030681 | 0.35741 | 0.064669 | 0.044808
2021-12-29 14:30 | 0.5717 | 0.7574 | 0.3175 | 1.438 | 0.023379 | 0.33806 | 0.033096 | 0.042413
2021-12-29 14:45 | 0.46144 | 0.72112 | 0.21337 | 1.2515 | 0.016146 | 0.32019 | 0.004232 | 0.039806
2021-12-29 15:00 | 2.0112 | 0.66472 | 0.22256 | 1.3845 | 0.012374 | 0.26906 | 0.070259 | 0.041022
2021-12-29 15:15 | 1.9703 | 0.70555 | 0.39611 | 1.4214 | 0.008602 | 0.19468 | 0.13628 | 0.042238
2021-12-29 15:30 | 2.0214 | 1.061 | 0.32975 | 1.1173 | 0.00483 | 0.1497 | 0.20231 | 0.043454
2021-12-29 15:45 | 1.9601 | 1.1854 | 0.27666 | 1.0467 | 0.001125 | 0.17686 | 0.2647 | 0.044492
2021-12-29 16:00 | 1.3067 | 0.84333 | 0.22051 | 0.94827 | 0.000842 | 0.13234 | 0.19808 | 0.033273
2021-12-29 16:15 | 0.42061 | 0.70781 | 0.26135 | 0.84151 | 0.00056 | 0.090419 | 0.13145 | 0.022054
2021-12-29 16:30 | 0.34302 | 0.7202 | 0.37263 | 1.1199 | 0.000277 | 0.043034 | 0.064824 | 0.010836
2021-12-29 16:45 | 0.37161 | 0.876 | 0.30627 | 1.9903 | 0 | 0 | 0 | 0
2021-12-29 17:00 | 0.49003 | 0.78901 | 0.29096 | 1.4271 | 0 | 0 | 0 | 0
2021-12-29 17:15 | 0.51862 | 0.86716 | 0.42061 | 1.2945 | 0 | 0 | 0 | 0
2021-12-29 17:30 | 0.51862 | 0.81583 | 0.58395 | 1.3337 | 0 | 0 | 0 | 0
2021-12-29 17:45 | 0.55537 | 0.89699 | 0.57987 | 1.0559 | 0 | 0 | 0 | 0
2021-12-29 18:00 | 0.69421 | 0.96372 | 0.71054 | 1.0368 | 0 | 0 | 0 | 0
2021-12-29 18:15 | 0.69421 | 0.92074 | 0.77997 | 1.0753 | 0 | 0 | 0 | 0
2021-12-29 18:30 | 0.8208 | 1.0008 | 0.68604 | 1.0324 | 0 | 0 | 0 | 0
2021-12-29 18:45 | 0.86572 | 1.3156 | 0.58804 | 1.2785 | 0 | 0 | 0 | 0
2021-12-29 19:00 | 0.76771 | 1.375 | 0.7473 | 1.4946 | 0 | 0 | 0 | 0
2021-12-29 19:15 | 0.92289 | 1.375 | 0.86572 | 1.5226 | 0 | 0 | 0 | 0
2021-12-29 19:30 | 1.0821 | 1.3992 | 0.88614 | 1.5637 | 0 | 0 | 0 | 0
2021-12-29 19:45 | 2.3481 | 1.7072 | 0.96781 | 1.6289 | 0 | 0 | 0 | 0
2021-12-29 20:00 | 1.8989 | 1.107 | 1.3884 | 1.0944 | 0 | 0 | 0 | 0
2021-12-29 20:15 | 1.6334 | 1.0979 | 1.7662 | 1.0397 | 0 | 0 | 0 | 0
2021-12-29 20:30 | 1.4803 | 0.88976 | 1.5926 | 0.95002 | 0 | 0 | 0 | 0
2021-12-29 20:45 | 0.91064 | 0.98008 | 0.8453 | 0.75546 | 0 | 0 | 0 | 0
2021-12-29 21:00 | 0.88205 | 0.81014 | 0.73913 | 0.67087 | 0 | 0 | 0 | 0
2021-12-29 21:15 | 0.87797 | 0.74965 | 0.59212 | 0.55741 | 0 | 0 | 0 | 0
2021-12-29 21:30 | 0.79222 | 0.70666 | 0.48186 | 0.54078 | 0 | 0 | 0 | 0
2021-12-29 21:45 | 0.62479 | 0.69834 | 0.50228 | 0.51439 | 0 | 0 | 0 | 0
2021-12-29 22:00 | 0.66154 | 0.70666 | 0.45736 | 0.53626 | 0 | 0 | 0 | 0
2021-12-29 22:15 | 0.72688 | 0.70666 | 0.43286 | 0.53057 | 0 | 0 | 0 | 0
2021-12-29 22:30 | 0.78813 | 0.68819 | 0.59212 | 0.55026 | 0 | 0 | 0 | 0
2021-12-29 22:45 | 0.73096 | 0.69741 | 0.5717 | 0.52576 | 0 | 0 | 0 | 0
2021-12-29 23:00 | 3.91 | 1.654 | 0.58395 | 1.4695 | 0 | 0 | 0 | 0
2021-12-29 23:15 | 3.9815 | 1.7211 | 0.49003 | 1.4281 | 0 | 0 | 0 | 0
2021-12-29 23:30 | 3.7161 | 1.7225 | 0.5227 | 1.4193 | 0 | 0 | 0 | 0
2021-12-29 23:45 | 3.6854 | 1.5818 | 0.53087 | 1.3859 | 0 | 0 | 0 | 0
2021-12-30 | 3.665 | 1.7663 | 0.5472 | 1.3452 | 0 | 0 | 0 | 0
2021-12-30 00:15 | 3.6854 | 1.7328 | 0.44511 | 1.3315 | 0 | 0 | 0 | 0
2021-12-30 00:30 | 3.7161 | 1.7663 | 0.36752 | 1.3238 | 0 | 0 | 0 | 0
2021-12-30 00:45 | 3.6752 | 1.863 | 0.46961 | 1.3365 | 0 | 0 | 0 | 0
2021-12-30 01:00 | 3.5629 | 1.7663 | 0.46553 | 1.2773 | 0 | 0 | 0 | 0
2021-12-30 01:15 | 3.4915 | 1.8412 | 0.39407 | 1.244 | 0 | 0 | 0 | 0
2021-12-30 01:30 | 3.4915 | 1.7169 | 0.29708 | 1.2525 | 0 | 0 | 0 | 0
2021-12-30 01:45 | 3.5323 | 1.7685 | 0.28585 | 1.2523 | 0 | 0 | 0 | 0
2021-12-30 02:00 | 3.471 | 1.5705 | 0.31954 | 1.2303 | 0 | 0 | 0 | 0
2021-12-30 02:15 | 2.103 | 1.5624 | 0.32056 | 1.2249 | 0 | 0 | 0 | 0
2021-12-30 02:30 | 1.3884 | 1.5624 | 0.32465 | 1.2165 | 0 | 0 | 0 | 0
2021-12-30 02:45 | 0.96373 | 1.5587 | 0.35425 | 1.243 | 0 | 0 | 0 | 0
2021-12-30 03:00 | 0.61662 | 1.7228 | 0.42878 | 1.318 | 0 | 0 | 0 | 0
2021-12-30 03:15 | 0.32465 | 1.6203 | 0.46144 | 1.2717 | 0 | 0 | 0 | 0
2021-12-30 03:30 | 0.30423 | 1.608 | 0.70238 | 1.3022 | 0 | 0 | 0 | 0
2021-12-30 03:45 | 0.41653 | 1.643 | 0.47778 | 1.2604 | 0 | 0 | 0 | 0
2021-12-30 04:00 | 0.36548 | 1.6538 | 0.29402 | 1.2687 | 0 | 0 | 0 | 0
2021-12-30 04:15 | 0.30218 | 1.6789 | 0.32362 | 1.2596 | 0 | 0 | 0 | 0
2021-12-30 04:30 | 0.29198 | 1.6789 | 0.34915 | 1.249 | 0 | 0 | 0 | 0
2021-12-30 04:45 | 0.42878 | 1.4219 | 0.2981 | 1.0807 | 0 | 0 | 0 | 0
2021-12-30 05:00 | 0.33077 | 1.3792 | 0.36548 | 1.0081 | 0 | 0 | 0 | 0
2021-12-30 05:15 | 0.29606 | 1.4082 | 0.44511 | 0.97685 | 0 | 0 | 0 | 0
2021-12-30 05:30 | 0.3369 | 1.3908 | 0.46553 | 0.93893 | 0 | 0 | 0 | 0
2021-12-30 05:45 | 0.37569 | 1.4388 | 0.41653 | 0.85449 | 0 | 0 | 0 | 0
2021-12-30 06:00 | 0.31035 | 1.3929 | 0.31239 | 0.92449 | 0 | 0 | 0 | 0
2021-12-30 06:15 | 0.33179 | 1.391 | 0.30729 | 0.81103 | 0 | 0 | 0 | 0
2021-12-30 06:30 | 0.41244 | 1.3733 | 0.42469 | 0.83699 | 0 | 0 | 0 | 0
2021-12-30 06:45 | 0.30525 | 1.3733 | 0.42878 | 0.82824 | 0 | 0 | 0 | 0
2021-12-30 07:00 | 0.33894 | 0.59003 | 0.33996 | 0.41594 | 0 | 0 | 0 | 0
2021-12-30 07:15 | 0.36752 | 0.57536 | 0.32567 | 0.38298 | 0 | 0 | 0 | 0
2021-12-30 07:30 | 0.40019 | 0.63952 | 0.40427 | 0.41536 | 0 | 0 | 0 | 0
2021-12-30 07:45 | 0.3369 | 0.65832 | 0.43694 | 0.39202 | 8.9e-05 | 0.002261 | 2e-05 | 0.000436
2021-12-30 08:00 | 1.0617 | 1.1236 | 0.33894 | 0.91035 | 0.006568 | 0.030808 | 0.000932 | 0.007713
2021-12-30 08:15 | 0.76363 | 1.4112 | 0.33077 | 0.86339 | 0.013048 | 0.063883 | 0.001845 | 0.014991
2021-12-30 08:30 | 0.38079 | 1.4088 | 0.42878 | 0.8911 | 0.019527 | 0.090721 | 0.002757 | 0.022268
2021-12-30 08:45 | 0.36038 | 1.4017 | 0.45328 | 0.88833 | 0.026344 | 0.12291 | 0.003723 | 0.02993
2021-12-30 09:00 | 0.96781 | 1.4214 | 0.41244 | 1.0189 | 0.058107 | 0.16759 | 0.007113 | 0.047298
2021-12-30 09:15 | 0.46553 | 1.3326 | 0.68604 | 0.9347 | 0.089869 | 0.19964 | 0.010503 | 0.064666
2021-12-30 09:30 | 0.62479 | 1.3499 | 0.85755 | 1.007 | 0.12163 | 0.22936 | 0.013892 | 0.082034
2021-12-30 09:45 | 1.2659 | 1.3397 | 0.75138 | 0.95118 | 0.15266 | 0.23165 | 0.017652 | 0.098991
2021-12-30 10:00 | 1.419 | 1.0649 | 0.5962 | 0.81584 | 0.1277 | 0.23497 | 0.038452 | 0.10526
2021-12-30 10:15 | 1.0209 | 1.0416 | 0.58395 | 0.78988 | 0.10274 | 0.27448 | 0.059253 | 0.11153
2021-12-30 10:30 | 0.63704 | 1.3243 | 2.2562 | 1.1288 | 0.077782 | 0.26176 | 0.080054 | 0.1178
2021-12-30 10:45 | 2.4501 | 1.0423 | 2.6135 | 1.0159 | 0.053072 | 0.28081 | 0.10001 | 0.12325
2021-12-30 11:00 | 3.1648 | 1.0429 | 2.0724 | 0.81438 | 0.047733 | 0.26816 | 0.080412 | 0.11509
2021-12-30 11:15 | 0.88205 | 1.0429 | 1.1536 | 0.87608 | 0.042393 | 0.27803 | 0.060814 | 0.10692
2021-12-30 11:30 | 0.88205 | 1.1309 | 3.3077 | 1.1107 | 0.037054 | 0.28949 | 0.041216 | 0.098758
2021-12-30 11:45 | 0.91064 | 1.1806 | 1.1434 | 0.98487 | 0.031966 | 0.28356 | 0.022116 | 0.090339
2021-12-30 12:00 | 0.69421 | 1.2275 | 1.4293 | 1.0142 | 0.04705 | 0.28316 | 0.026791 | 0.079319
2021-12-30 12:15 | 0.6207 | 1.4335 | 3.0831 | 1.2624 | 0.062133 | 0.28083 | 0.031465 | 0.068298
2021-12-30 12:30 | 0.72688 | 1.3501 | 1.3476 | 1.4347 | 0.077217 | 0.27048 | 0.03614 | 0.057277
2021-12-30 12:45 | 0.62887 | 1.5968 | 0.69421 | 1.6212 | 0.0929 | 0.26022 | 0.040744 | 0.046815
2021-12-30 13:00 | 0.58395 | 1.5945 | 0.5962 | 1.8388 | 0.15799 | 0.26294 | 0.041921 | 0.046375
2021-12-30 13:15 | 0.7963 | 1.4587 | 0.53087 | 1.7921 | 0.22308 | 0.30539 | 0.043099 | 0.045935
2021-12-30 13:30 | 0.64521 | 1.4828 | 0.58804 | 1.8255 | 0.28817 | 0.30686 | 0.044276 | 0.045495
2021-12-30 13:45 | 0.64929 | 1.44 | 0.91472 | 1.981 | 0.35174 | 0.2984 | 0.045285 | 0.045287
2021-12-30 14:00 | 0.6207 | 1.4914 | 1.5824 | 2.0332 | 0.28656 | 0.28494 | 0.037983 | 0.043678
2021-12-30 14:15 | 0.57578 | 1.3891 | 0.66971 | 1.5866 | 0.22138 | 0.25987 | 0.030681 | 0.042069
2021-12-30 14:30 | 0.31444 | 1.1105 | 0.5717 | 1.4579 | 0.1562 | 0.2175 | 0.023379 | 0.04046
2021-12-30 14:45 | 0.28585 | 1.2023 | 0.46144 | 1.2698 | 0.091503 | 0.19515 | 0.016146 | 0.038455
2021-12-30 15:00 | 0.28381 | 1.2993 | 2.0112 | 1.6242 | 0.06876 | 0.20166 | 0.012374 | 0.038455
2021-12-30 15:15 | 0.28177 | 1.3831 | 1.9703 | 1.655 | 0.046017 | 0.15433 | 0.008602 | 0.038455
2021-12-30 15:30 | 0.28789 | 1.0719 | 2.0214 | 1.3556 | 0.023274 | 0.10842 | 0.00483 | 0.038455
2021-12-30 15:45 | 0.28483 | 0.9709 | 1.9601 | 1.2614 | 0.000778 | 0.13273 | 0.001125 | 0.038459
2021-12-30 16:00 | 0.41244 | 0.89771 | 1.3067 | 1.0871 | 0.000583 | 0.095646 | 0.000842 | 0.028779
2021-12-30 16:15 | 0.39611 | 1.059 | 0.42061 | 0.85449 | 0.000388 | 0.06445 | 0.00056 | 0.019098
2021-12-30 16:30 | 0.62887 | 1.1711 | 0.34302 | 1.1223 | 0.000193 | 0.032016 | 0.000277 | 0.009417
2021-12-30 16:45 | 0.52678 | 1.3104 | 0.37161 | 1.9919 | 0 | 0 | 0 | 0
2021-12-30 17:00 | 0.31035 | 1.0973 | 0.49003 | 1.4335 | 0 | 0 | 0 | 0
2021-12-30 17:15 | 0.31035 | 1.2981 | 0.51862 | 1.3113 | 0 | 0 | 0 | 0
2021-12-30 17:30 | 0.31444 | 1.3337 | 0.51862 | 1.3606 | 0 | 0 | 0 | 0
2021-12-30 17:45 | 0.29708 | 1.2207 | 0.55537 | 1.0877 | 0 | 0 | 0 | 0
2021-12-30 18:00 | 0.53495 | 1.2175 | 0.69421 | 1.0759 | 0 | 0 | 0 | 0
2021-12-30 18:15 | 0.51862 | 1.2185 | 0.69421 | 1.119 | 0 | 0 | 0 | 0
2021-12-30 18:30 | 0.49003 | 1.1521 | 0.8208 | 1.0843 | 0 | 0 | 0 | 0
2021-12-30 18:45 | 0.55537 | 1.1154 | 0.86572 | 1.0331 | 0 | 0 | 0 | 0
2021-12-30 19:00 | 1.0127 | 1.3222 | 0.76771 | 1.0471 | 0 | 0 | 0 | 0
2021-12-30 19:15 | 2.246 | 1.2202 | 0.92289 | 1.0929 | 0 | 0 | 0 | 0
2021-12-30 19:30 | 2.5931 | 1.2396 | 1.0821 | 1.1393 | 0 | 0 | 0 | 0
2021-12-30 19:45 | 2.5727 | 1.332 | 2.3481 | 1.3765 | 0 | 0 | 0 | 0
2021-12-30 20:00 | 2.3481 | 1.0985 | 1.8989 | 1.1002 | 0 | 0 | 0 | 0
2021-12-30 20:15 | 1.0924 | 1.0985 | 1.6334 | 1.0835 | 0 | 0 | 0 | 0
2021-12-30 20:30 | 1.807 | 1.1299 | 1.4803 | 1.0821 | 0 | 0 | 0 | 0
2021-12-30 20:45 | 1.858 | 0.97017 | 0.91064 | 0.75138 | 0 | 0 | 0 | 0
2021-12-30 21:00 | 0.58395 | 0.95454 | 0.88205 | 0.71054 | 0 | 0 | 0 | 0
2021-12-30 21:15 | 0.55945 | 0.89265 | 0.87797 | 0.59183 | 0 | 0 | 0 | 0
2021-12-30 21:30 | 2.2766 | 0.90898 | 0.79222 | 0.56995 | 0 | 0 | 0 | 0
2021-12-30 21:45 | 2.491 | 0.72599 | 0.62479 | 0.52197 | 0 | 0 | 0 | 0
2021-12-30 22:00 | 2.4706 | 0.74221 | 0.66154 | 0.54735 | 0 | 0 | 0 | 0
2021-12-30 22:15 | 1.368 | 0.71343 | 0.72688 | 0.54691 | 0 | 0 | 0 | 0
2021-12-30 22:30 | 2.8075 | 0.85509 | 0.78813 | 0.57301 | 0 | 0 | 0 | 0
2021-12-30 22:45 | 1.419 | 0.69538 | 0.73096 | 0.5386 | 0 | 0 | 0 | 0
2021-12-30 23:00 | 0.45736 | 1.3751 | 3.91 | 1.5381 | 0 | 0 | 0 | 0
2021-12-30 23:15 | 0.43286 | 1.3112 | 3.9815 | 1.4893 | 0 | 0 | 0 | 0
2021-12-30 23:30 | 0.33894 | 1.2951 | 3.7161 | 1.4456 | 0 | 0 | 0 | 0
2021-12-30 23:45 | 0.33485 | 1.3151 | 3.6854 | 1.4005 | 0 | 0 | 0 | 0
2021-12-31 | 0.31341 | 1.3761 | 3.665 | 1.3715 | 0 | 0 | 0 | 0
2021-12-31 00:15 | 0.30423 | 1.3965 | 3.6854 | 1.3665 | 0 | 0 | 0 | 0
2021-12-31 00:30 | 0.33179 | 1.4062 | 3.7161 | 1.3617 | 0 | 0 | 0 | 0
2021-12-31 00:45 | 0.39509 | 1.3965 | 3.6752 | 1.3715 | 0 | 0 | 0 | 0
2021-12-31 01:00 | 0.38998 | 1.3488 | 3.5629 | 1.3006 | 0 | 0 | 0 | 0
2021-12-31 01:15 | 0.27973 | 1.2934 | 3.4915 | 1.2557 | 0 | 0 | 0 | 0
2021-12-31 01:30 | 0.28279 | 1.1767 | 3.4915 | 1.2598 | 0 | 0 | 0 | 0
2021-12-31 01:45 | 0.30933 | 1.1767 | 3.5323 | 1.264 | 0 | 0 | 0 | 0
2021-12-31 02:00 | 0.28687 | 1.1626 | 3.471 | 1.2464 | 0 | 0 | 0 | 0
2021-12-31 02:15 | 0.41244 | 1.1165 | 2.103 | 1.0455 | 0 | 0 | 0 | 0
2021-12-31 02:30 | 0.31035 | 1.0038 | 1.3884 | 0.93645 | 0 | 0 | 0 | 0
2021-12-31 02:45 | 0.32465 | 0.95987 | 0.96373 | 0.89649 | 0 | 0 | 0 | 0
2021-12-31 03:00 | 0.32158 | 1.0396 | 0.61662 | 0.90729 | 0 | 0 | 0 | 0
2021-12-31 03:15 | 0.35017 | 0.95129 | 0.32465 | 0.82809 | 0 | 0 | 0 | 0
2021-12-31 03:30 | 0.28789 | 0.90641 | 0.30423 | 0.85857 | 0 | 0 | 0 | 0
2021-12-31 03:45 | 0.31137 | 0.91601 | 0.41653 | 0.83422 | 0 | 0 | 0 | 0
2021-12-31 04:00 | 0.31444 | 0.95921 | 0.36548 | 0.83378 | 0 | 0 | 0 | 0
2021-12-31 04:15 | 0.39202 | 0.90159 | 0.30218 | 0.81278 | 0 | 0 | 0 | 0
2021-12-31 04:30 | 0.3226 | 0.91931 | 0.29198 | 0.78609 | 0 | 0 | 0 | 0
2021-12-31 04:45 | 0.28687 | 0.95579 | 0.42878 | 0.65192 | 0 | 0 | 0 | 0
2021-12-31 05:00 | 0.32362 | 0.85308 | 0.33077 | 0.56674 | 0 | 0 | 0 | 0
2021-12-31 05:15 | 0.39509 | 0.75352 | 0.29606 | 0.52912 | 0 | 0 | 0 | 0
2021-12-31 05:30 | 0.34404 | 0.70285 | 0.3369 | 0.49703 | 0 | 0 | 0 | 0
2021-12-31 05:45 | 0.28381 | 0.6207 | 0.37569 | 0.39917 | 0 | 0 | 0 | 0
2021-12-31 06:00 | 0.29606 | 0.67945 | 0.31035 | 0.42192 | 0 | 0 | 0 | 0
2021-12-31 06:15 | 0.33792 | 0.6394 | 0.33179 | 0.35235 | 0 | 0 | 0 | 0
2021-12-31 06:30 | 0.38182 | 0.69369 | 0.41244 | 0.39275 | 0 | 0 | 0 | 0
2021-12-31 06:45 | 0.30729 | 0.63744 | 0.30525 | 0.37306 | 0 | 0 | 0 | 0
2021-12-31 07:00 | 0.30321 | 0.64341 | 0.33894 | 0.37161 | 0 | 0 | 0 | 0
2021-12-31 07:15 | 0.38386 | 0.62765 | 0.36752 | 0.3859 | 0 | 0 | 0 | 0
2021-12-31 07:30 | 0.34098 | 0.67427 | 0.40019 | 0.42571 | 0 | 0 | 0 | 0
2021-12-31 07:45 | 0.31035 | 0.73219 | 0.3369 | 0.38765 | 6.6e-05 | 0.000707 | 8.9e-05 | 9.2e-05
2021-12-31 08:00 | 0.41653 | 0.97764 | 1.0617 | 0.58949 | 0.012047 | 0.031466 | 0.006568 | 0.003284
2021-12-31 08:15 | 0.42469 | 1.0135 | 0.76363 | 0.46349 | 0.024029 | 0.060395 | 0.013048 | 0.006476
2021-12-31 08:30 | 0.38794 | 0.88921 | 0.38079 | 0.39567 | 0.03601 | 0.10064 | 0.019527 | 0.009667
2021-12-31 08:45 | 0.30831 | 0.95222 | 0.36038 | 0.38561 | 0.047955 | 0.10948 | 0.026344 | 0.013508
2021-12-31 09:00 | 0.28177 | 1.2956 | 0.96781 | 0.63937 | 0.052727 | 0.12549 | 0.058107 | 0.033446
2021-12-31 09:15 | 0.96781 | 1.1113 | 0.46553 | 0.49513 | 0.057499 | 0.1332 | 0.089869 | 0.053384
2021-12-31 09:30 | 0.61662 | 1.1762 | 0.62479 | 0.56105 | 0.062271 | 0.17116 | 0.12163 | 0.073322
2021-12-31 09:45 | 0.62479 | 1.1474 | 1.2659 | 0.60116 | 0.067094 | 0.19791 | 0.15266 | 0.092354
2021-12-31 10:00 | 0.65746 | 1.1662 | 1.419 | 0.60437 | 0.08258 | 0.20168 | 0.1277 | 0.087585
2021-12-31 10:15 | 0.91064 | 1.1944 | 1.0209 | 0.75488 | 0.098067 | 0.18039 | 0.10274 | 0.082816
2021-12-31 10:30 | 0.77588 | 1.1666 | 0.63704 | 0.81293 | 0.11355 | 0.20886 | 0.077782 | 0.078048
2021-12-31 10:45 | 2.0316 | 1.1692 | 2.4501 | 1.0014 | 0.12926 | 0.2018 | 0.053072 | 0.073431
2021-12-31 11:00 | 0.87797 | 1.2274 | 3.1648 | 1.1247 | 0.19501 | 0.1874 | 0.047733 | 0.070351
2021-12-31 11:15 | 0.75138 | 1.1621 | 0.88205 | 0.6681 | 0.26076 | 0.17133 | 0.042393 | 0.067271
2021-12-31 11:30 | 0.62887 | 1.1702 | 0.88205 | 0.99173 | 0.32651 | 0.18075 | 0.037054 | 0.064192
2021-12-31 11:45 | 1.7151 | 1.1595 | 0.91064 | 0.60743 | 0.39211 | 0.17661 | 0.031966 | 0.060952
2021-12-31 12:00 | 1.5722 | 1.1263 | 0.69421 | 0.59708 | 0.42251 | 0.17201 | 0.04705 | 0.058761
2021-12-31 12:15 | 1.6334 | 1.1368 | 0.6207 | 0.83772 | 0.45291 | 0.17583 | 0.062133 | 0.056569
2021-12-31 12:30 | 1.1128 | 1.1831 | 0.72688 | 1.0295 | 0.48331 | 0.19288 | 0.077217 | 0.054378
2021-12-31 12:45 | 0.36752 | 1.3553 | 0.62887 | 1.2122 | 0.51358 | 0.19261 | 0.0929 | 0.052448
2021-12-31 13:00 | 0.26543 | 1.4536 | 0.58395 | 1.4234 | 0.51016 | 0.21287 | 0.15799 | 0.062488
2021-12-31 13:15 | 0.41653 | 1.5072 | 0.7963 | 1.4144 | 0.50675 | 0.22156 | 0.22308 | 0.072528
2021-12-31 13:30 | 0.52678 | 1.4794 | 0.64521 | 1.4306 | 0.50334 | 0.24649 | 0.28817 | 0.082568
2021-12-31 13:45 | 0.51453 | 1.5397 | 0.64929 | 1.5808 | 0.4999 | 0.24775 | 0.35174 | 0.092217
2021-12-31 14:00 | 0.51862 | 1.5364 | 0.6207 | 1.6216 | 0.48978 | 0.22837 | 0.28656 | 0.076595
2021-12-31 14:15 | 0.50636 | 1.302 | 0.57578 | 1.087 | 0.47966 | 0.18603 | 0.22138 | 0.060974
2021-12-31 14:30 | 0.48186 | 1.1431 | 0.31444 | 0.85814 | 0.46953 | 0.18064 | 0.1562 | 0.045353
2021-12-31 14:45 | 0.44511 | 1.143 | 0.28585 | 0.80461 | 0.45922 | 0.15258 | 0.091503 | 0.030104
2021-12-31 15:00 | 0.44511 | 1.3072 | 0.28381 | 1.2637 | 0.38776 | 0.12444 | 0.06876 | 0.032304
2021-12-31 15:15 | 0.57987 | 1.4325 | 0.28177 | 1.4328 | 0.31631 | 0.10473 | 0.046017 | 0.034504
2021-12-31 15:30 | 0.90656 | 1.2923 | 0.28789 | 1.2101 | 0.24485 | 0.091944 | 0.023274 | 0.036704
2021-12-31 15:45 | 0.70646 | 1.2753 | 0.28483 | 1.1285 | 0.17347 | 0.089678 | 0.000778 | 0.03857
2021-12-31 16:00 | 0.68604 | 1.2675 | 0.41244 | 1.0282 | 0.13008 | 0.064175 | 0.000583 | 0.028862
2021-12-31 16:15 | 1.2149 | 1.1757 | 0.39611 | 0.84224 | 0.086684 | 0.04315 | 0.000388 | 0.019153
2021-12-31 16:30 | 1.5313 | 1.2825 | 0.62887 | 1.1403 | 0.04329 | 0.019652 | 0.000193 | 0.009445
2021-12-31 16:45 | 1.1128 | 1.9909 | 0.52678 | 1.7799 | 0 | 0 | 0 | 0
2021-12-31 17:00 | 0.87797 | 1.697 | 0.31035 | 1.3792 | 0 | 0 | 0 | 0
2021-12-31 17:15 | 1.1332 | 1.6035 | 0.31035 | 1.2547 | 0 | 0 | 0 | 0
2021-12-31 17:30 | 0.84938 | 1.6542 | 0.31444 | 1.2958 | 0 | 0 | 0 | 0
2021-12-31 17:45 | 0.77997 | 1.2218 | 0.29708 | 1.0053 | 0 | 0 | 0 | 0
2021-12-31 18:00 | 2.6339 | 1.131 | 0.53495 | 1.021 | 0 | 0 | 0 | 0
2021-12-31 18:15 | 5.2897 | 1.2838 | 0.51862 | 1.052 | 0 | 0 | 0 | 0
2021-12-31 18:30 | 4.3438 | 1.2685 | 0.49003 | 1.0779 | 0 | 0 | 0 | 0
2021-12-31 18:45 | 4.3564 | 1.1417 | 0.55537 | 1.0425 | 0 | 0 | 0 | 0
2021-12-31 19:00 | 4.2741 | 1.1711 | 1.0127 | 1.0973 | 0 | 0 | 0 | 0
2021-12-31 19:15 | 4.1831 | 1.2341 | 2.246 | 1.3094 | 0 | 0 | 0 | 0
2021-12-31 19:30 | 4.5172 | 1.2341 | 2.5931 | 1.403 | 0 | 0 | 0 | 0
2021-12-31 19:45 | 5.8155 | 1.612 | 2.5727 | 1.6145 | 0 | 0 | 0 | 0
2021-12-31 20:00 | 2.8483 | 1.2599 | 2.3481 | 1.2898 | 0 | 0 | 0 | 0
2021-12-31 20:15 | 2.8483 | 0.97671 | 1.0924 | 1.0616 | 0 | 0 | 0 | 0
2021-12-31 20:30 | 2.2562 | 0.94786 | 1.807 | 1.0413 | 0 | 0 | 0 | 0
2021-12-31 20:45 | 2.1541 | 0.86066 | 1.858 | 0.79222 | 0 | 0 | 0 | 0
2021-12-31 21:00 | 1.2149 | 0.80979 | 0.58395 | 0.57229 | 0 | 0 | 0 | 0
2021-12-31 21:15 | 1.0311 | 0.76444 | 0.55945 | 0.55916 | 0 | 0 | 0 | 0
2021-12-31 21:30 | 0.98006 | 0.86936 | 2.2766 | 0.75517 | 0 | 0 | 0 | 0
2021-12-31 21:45 | 0.80038 | 0.92789 | 2.491 | 0.73432 | 0 | 0 | 0 | 0
2021-12-31 22:00 | 1.1026 | 0.95987 | 2.4706 | 0.75736 | 0 | 0 | 0 | 0
2021-12-31 22:15 | 1.317 | 0.83177 | 1.368 | 0.621 | 0 | 0 | 0 | 0
2021-12-31 22:30 | 0.88614 | 0.97862 | 2.8075 | 0.87082 | 0 | 0 | 0 | 0
2021-12-31 22:45 | 0.89022 | 0.83177 | 1.419 | 0.63864 | 0 | 0 | 0 | 0
2021-12-31 23:00 | 3.8079 | 1.2394 | 0.45736 | 1.5001 | 0 | 0 | 0 | 0
2021-12-31 23:15 | 3.8794 | 1.2394 | 0.43286 | 1.4374 | 0 | 0 | 0 | 0
2021-12-31 23:30 | 3.614 | 1.2255 | 0.33894 | 1.3668 | 0 | 0 | 0 | 0
2021-12-31 23:45 | 3.6854 | 1.2185 | 0.33485 | 1.3218 | 0 | 0 | 0 | 0